## fPM_min
Key | primary_fuel | fPM_Min_lb_per_MWh_Rank | Reason_for_Removal as top ranked unit for fPM new source floor | ORIS Code | Plant Name | boiler_id | configuration_id | Unit Type | boiler_type | MWe_capacity | max_heat_input | compound | EF_1mg | Final_EF_Units | From | Report_id (Part II) | Count of Runs | Count of Methods | Submittal_ID (ERT) | MaxOfEF_Changed | Submitted_EF (lb/MMBtu) | AvgOf1mg | MaxOf1mg_corrected | AvgOf2mg | MaxOf2mg_corrected | Config_heat_rate_MMBtu/MWh | lb/MWh (1mg = 1 x MDL) | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
10566_Boil 2 | coal | 1 | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Chambers Cogeneration LP | Boil 2 | Boil 2 | Conventional Boiler | Wall firing - front firing | 142.5 | 1387 | Filterable Particulate | 0.00023004 | lb/MMBtu | ERT |  | 3 | 3 | 1365 |  | 0.00015281 | 0.00023004 | corrected | 0.00043013 | corrected | 9.7333 | 0.002239 | NOx control | Selective Catalytic Reduction | 1994-03-01 | SO2 control | Dry FGD - Spray Dryer | 1994-03-01 | PM control | Fabric Filter, reverse air | 1994-03-01
50976_AABO1 | coal | 2 | Indiantown Unit 1's ERT submittal includes a test where the facility entered grams as milligrams. This error was apparent because the tare weights of the filters as reported was 1000 times lower than the tare weights in other test reports. When the erronous "milligram" entries were corrected to "milligrams" Indian Town was not one of the top performers. It is also worth noting here that there was a second test reported for Indian Town under Part II with a very low emission rate (0.0004 lbs fPM/MMBtu). Per EPA guidance we estimated the volume of flue gas sampled to meet the minimum sample volume specified in the method (0.8 scm). Based on an estimated sample volume of one standard cubic meter we calcuated a detection limit for fPM on a lb fPM/MMBtu basis. The minimum detection limit for Indian Town based on this method (on a lb/MMBtu) was approximately 0.0007 lbs fPM/MMBtu. This value removed Indiantown from contention as the best performing EGU. | 50976 | INDIANTOWN COGENERATION L.P. | AABO1 | 001 | Conventional Boiler | Wall firing - opposed firing | 361 | 3422 | Filterable Particulate | 0.0002424 | lb/MMBtu | ERT |  | 3 | 3 | 1336 |  | 3.2218e-06 | 0.0002424 | corrected | 0.00048481 | corrected | 9.4792 | 0.0022978 | NOx control | Selective Catalytic Reduction | 1995-12-01 | SO2 control | Dry FGD - Spray Dryer | 1995-12-01 | PM control | Fabric Filter, pulse | 1995-12-01
2554_1 | coal | 3 | The air pollution control technology in services at Dunkirk Unit 1 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 2554 | Dunkirk Generating Plant | 1 | 1 | Conventional Boiler | Tangential firing | 85 | 922.2 | Filterable Particulate | 0.00029899 | lb/MMBtu | ERT |  | 6 | 6 | 535 |  | 0.00024426 | 0.00029899 | corrected | 0.00047944 | corrected | 10.8494 | 0.0032438 | NOx control | Selective Noncatalytic Reduction |  | Other control | Dry sorbent injection |  | PM control | Fabric Filter, unspecified | 2009-12-01
10566_Boil 1 | coal | 4 | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Chambers Cogeneration LP | Boil 1 | Boil 1 | Conventional Boiler | Wall firing - front firing | 142.5 | 1387 | Filterable Particulate | 0.0005161 | lb/MMBtu | ERT |  | 3 | 3 | 1128 |  | 0.0005161 | 0.0005161 |  | 0.00054725 | corrected | 9.7333 | 0.0050234 | NOx control | Selective Catalytic Reduction | 1994-03-01 | SO2 control | Dry FGD - Spray Dryer | 1994-03-01 | PM control | Fabric Filter, reverse air | 1994-03-01
492_5 | coal | 5 | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | Martin Drake | 5 | Unit 5 - Coal | Conventional Boiler | Wall firing - front firing | 55 | 570 | Filterable Particulate | 0.00049068 | lb/MMBtu | ERT |  | 3 | 3 | 1189 |  | 0.00046881 | 0.00049068 | corrected | 0.00056361 | corrected | 10.3636 | 0.0050853 | PM control | Fabric Filter, reverse air | 1998-05-01
8223_3 | coal | 6 | New MACT Floor Unit | 8223 | Springerville | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 450 | 4200 | Filterable Particulate | 0.00058211 | lb/MMBtu | ERT |  | 6 | 6 | 1133 |  | 0.00058211 | 0.00058211 |  | 0.00058549 | corrected | 9.3333 | 0.0054331 | NOx control | Selective Catalytic Reduction | 2006-08-01 | SO2 control | Dry FGD - Spray Dryer | 2006-08-01 | PM control | Fabric Filter, pulse | 2006-08-01
2277_2 | coal | 7 |  | 2277 | Sheldon Station | 2 | U2 | Conventional Boiler | Cyclone firing | 141 | 1514 | Filterable Particulate | 0.00051535 | lb/MMBtu | ERT |  | 6 | 6 | 1833 |  | 0.00051535 | 0.00051535 |  | 0.00058217 | corrected | 10.7376 | 0.0055336 | PM control | Fabric Filter, pulse | 2000-02-01
10043_B01 | coal | 8 |  | 10043 | Logan Generating Plant | B01 | Unit1 | Conventional Boiler | Wall firing - opposed firing | 241.7 | 2116 | Filterable Particulate | 0.00065396 | lb/MMBtu | ERT |  | 3 | 3 | 1266 |  | 0.00065396 | 0.00065396 |  | 0.00072754 | corrected | 8.7547 | 0.0057252 | NOx control | Selective Catalytic Reduction | 1994-09-01 | SO2 control | Dry FGD - Spray Dryer | 1994-09-01 | PM control | Fabric Filter, reverse air | 1994-09-01
1626_1 | coal | 9 |  | 1626 | Salem Harbor | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 81.419 | 981 | Filterable Particulate | 0.00049037 | lb/MMBtu | ERT |  | 3 | 3 | 2161 |  | 0.00049037 | 0.00049037 |  | 0.00058818 | corrected | 12.0488 | 0.0059084 | NOx control | Selective Noncatalytic Reduction | 1993-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-07-01
8223_4 | coal | 10 |  | 8223 | Springerville | 4 | 4 | Conventional Boiler | Wall firing - opposed firing | 450 | 4200 | Filterable Particulate | 0.00075428 | lb/MMBtu | ERT |  | 6 | 6 | 1129 |  | 0.00075428 | 0.00075428 |  | 0.00076179 | corrected | 9.3333 | 0.00704 | NOx control | Selective Catalytic Reduction | 2009-12-01 | SO2 control | Dry FGD - Spray Dryer | 2009-12-01 | PM control | Fabric Filter, pulse | 2009-12-01
52071_5A | coal | 11 |  | 52071 | Sandow Station | 5A | 5A | Fluidized bed firing | Fluidized bed firing | 2960 | 282.35 | Filterable Particulate | 0.0006734 | lb/MMBtu | ERT |  | 6 | 6 | 834 |  | 0.0006734 | 0.0006734 |  | 0.00068925 | corrected | 10.4834 | 0.0070596
2408_E2 | coal | 12 |  | 2408 | PSEG Mercer Generating Station | E2 | MERU2E2PT2OS1-Coal | Conventional Boiler | Wall firing - unspecified | 343 | 3100 | Filterable Particulate | 0.00078255 | lb/MMBtu | ERT |  | 6 | 6 | 1585 |  | 0.00076396 | 0.00078255 | corrected | 0.00089685 | corrected | 9.0379 | 0.0070726 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1991-08-01 | NOx control | Selective Catalytic Reduction | 2004-06-01 | Other control | Activated carbon injection | 2007-01-01 | PM control | Fabric Filter, pulse | 2008-12-01
2554_4 | coal | 13 |  | 2554 | Dunkirk Generating Plant | 4 | 4 | Conventional Boiler | Tangential firing | 195 | 1836 | Filterable Particulate | 0.00076382 | lb/MMBtu | ERT |  | 6 | 6 | 536 |  | 0.00074222 | 0.00076382 | corrected | 0.00082471 | corrected | 9.4154 | 0.0071917 | NOx control | Selective Noncatalytic Reduction |  | Other control | Dry sorbent injection |  | PM control | Fabric Filter, unspecified | 2009-05-01
2408_E1 | coal | 14 |  | 2408 | PSEG Mercer Generating Station | E1 | MERU1E1PT1OS1-Coal | Conventional Boiler | Wall firing - unspecified | 343 | 3100 | Filterable Particulate | 0.0008561 | lb/MMBtu | ERT |  | 6 | 6 | 1602 |  | 0.00079261 | 0.0008561 | corrected | 0.00097124 | corrected | 9.0379 | 0.0077374 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1994-05-01 | NOx control | Selective Catalytic Reduction | 2004-06-01 | Other control | Activated carbon injection | 2007-01-01 | PM control | Fabric Filter, pulse | 2008-12-01
6077_2 | coal | 15 |  | 6077 | Gerald Gentleman | 2 | U2 | Conventional Boiler | Wall firing - opposed firing | 750 | 7538 | Filterable Particulate | 0.00080743 | lb/MMBtu | ERT |  | 6 | 6 | 1835 |  | 0.00080743 | 0.00080743 |  | 0.00090904 | corrected | 10.0507 | 0.0081152 | PM control | Fabric Filter, reverse air | 2001-05-01
568_BHB3 | coal | 16 |  | 568 | Bridgeport Station | BHB3 | BHSEMU3OS2-Coal | Conventional Boiler | Tangential firing | 403 | 4100 | Filterable Particulate | 0.00079892 | lb/MMBtu | ERT |  | 6 | 6 | 1618 |  | 0.00079892 | 0.00079892 |  | 0.00079892 |  | 10.1737 | 0.008128 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-08-01 | Other control | Activated carbon injection | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-01-01
6041_3 | coal | 17 |  | 6041 | H L Spurlock Station | 3 | Unit 03 | Fluidized bed firing | Fluidized bed firing | 300 | 2500 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | Acid Gas Emissions Test (1/9/07) | 2 | 2 |  |  | 0.001 | 0.001 |  | 0.0016412 | Corrected | 8.3333 | 0.0083333 | NOx control | Selective Noncatalytic Reduction | 2005-03-01 | SO2 control | Dry FGD - Unspecified | 2005-03-01 | PM control | Fabric Filter, pulse | 2005-03-01
963_34 | coal | 18 |  | 963 | Dallman | 34 | 34 | Conventional Boiler | Wall firing - opposed firing | 229.4 | 1924.9 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | Dallman 34 Test 2 | 1 | 1 |  |  |  | 0.001 |  | 0.0016572 | Corrected | 8.391 | 0.008391 | NOx control | Selective Catalytic Reduction | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01 | SO2 control | Wet FGD - Packed Type | 2009-05-01 | Other control | Wet electrostatic precipitator | 2009-05-01
492_6 | coal | 19 |  | 492 | Martin Drake | 6 | Unit 6 - Coal | Conventional Boiler | Wall firing - front firing | 85 | 930 | Filterable Particulate | 0.00077373 | lb/MMBtu | Part II | Airtech 2693A-D-A | 3 | 3 |  |  | 0.00063867 | 0.00077373 | Corrected | 0.0015313 | Corrected | 10.9412 | 0.0084655 | PM control | Fabric Filter, reverse air | 1978-09-01
3788_3 | coal | 20 |  | 3788 | Potomac River | 3 | 3 | Conventional Boiler | Tangential firing | 961 | 108 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | C3 PM STK TronaOn 1206 | 1 | 1 |  |  |  | 0.001 |  | 0.0016359 | Corrected | 8.8981 | 0.0088981
8219_1 | coal | 21 |  | 8219 | Ray D Nixon | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 225 | 2095 | Filterable Particulate | 0.00096371 | lb/MMBtu | Part II | APT CSU5384 N | 3 | 3 |  |  | 0.00079333 | 0.00096371 | Corrected | 0.001789 | Corrected | 9.3111 | 0.0089732 | PM control | Fabric Filter, reverse air | 1980-04-01
10769_Config 1 | coal | 22 |  | 10769 | Rio Bravo Poso | C-E CONTRACT 24687 | Config 1 | Fluidized bed firing | Fluidized bed firing | 407.93 | 36 | Filterable Particulate | 0.00080762 | lb/MMBtu | Part II | 2006 R015281 | 1 | 1 |  |  |  | 0.00080762 | Corrected | 0.0016152 | Corrected | 11.3314 | 0.0091515
6761_101 | coal | 23 |  | 6761 | Rawhide | 101 | Rawhide101 | Conventional Boiler | Tangential firing | 305 | 2800 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | Dec 2005 PM Compliance Test | 1 | 1 |  |  |  | 0.001 |  | 0.0016572 | Corrected | 9.1803 | 0.0091803 | SO2 control | Dry FGD - Spray Dryer | 1984-04-01 | PM control | Fabric Filter, reverse air | 1984-04-01
6761_101 | coal | 24 |  | 6761 | Rawhide | 101 | Rawhide101 | Conventional Boiler | Tangential firing | 305 | 2800 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | Feb 2006 PM, HCL, and HF Testing | 1 | 1 |  |  |  | 0.001 |  | 0.0016572 | Corrected | 9.1803 | 0.0091803 | SO2 control | Dry FGD - Spray Dryer | 1984-04-01 | PM control | Fabric Filter, reverse air | 1984-04-01
1743_SC2-Config | coal | 25 |  | 1743 | St Clair Power Plant | 2 | SC2-Config | Conventional Boiler | Wall firing - front firing | 1750 | 163 | Filterable Particulate | 0.0008564 | lb/MMBtu | Part II | 2009Sep_2b | 2 | 0 |  |  | 0.0005 | 0.0008564 | Corrected | 0.0017128 | Corrected | 10.7362 | 0.0091945
492_7 | coal | 26 |  | 492 | Martin Drake | 7 | Unit 7 - Coal | Conventional Boiler | Wall firing - front firing | 141 | 1475 | Filterable Particulate | 0.0009115 | lb/MMBtu | Part II | APT CSU5384 D | 2 | 2 |  |  | 0.000485 | 0.0009115 | Corrected | 0.001823 | Corrected | 10.461 | 0.0095352 | PM control | Fabric Filter, reverse air | 1993-11-01
55479_3 | coal | 27 |  | 55479 | Wygen 1 | 3 | WYG1Cfg | Conventional Boiler | Wall firing - front firing | 91 | 1053 | Filterable Particulate | 0.00082645 | lb/MMBtu | ERT |  | 4 | 4 | 1488 |  | 0.00082645 | 0.00082645 |  | 0.00082645 |  | 11.5714 | 0.0095632 | NOx control | Selective Catalytic Reduction | 2003-04-01 | SO2 control | Dry FGD - Spray Dryer | 2003-04-01 | PM control | Fabric Filter, pulse | 2003-04-01
897_Unit 2 | coal | 28 |  | 897 | Vermilion | Unit 2 | 002 | Conventional Boiler | Tangential firing | 110 | 1076 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 8 | 1 | 0 |  |  |  | 0.001 |  | 0.0017128 | Corrected | 9.7818 | 0.0097818 | PM control | Electrostatic precipitator, unspecified | 1974-01-01 | Other control | Activated carbon injection | 2007-05-01 | PM control | Fabric Filter, unspecified | 2007-05-01
10673_BLR A | coal | 29 |  | 10673 | AES Hawaii | BLR A | 001 | Fluidized bed firing | Fluidized bed firing | 101.5 | 1021.4 | Filterable Particulate | 0.0009892 | lb/MMBtu | ERT |  | 6 | 6 | 779 |  | 0.0009892 | 0.0009892 |  | 0.0009892 |  | 10.0631 | 0.0099544 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
2277_1 | coal | 30 |  | 2277 | Sheldon Station | 1 | U1 | Conventional Boiler | Cyclone firing | 128 | 1374 | Filterable Particulate | 0.0009369 | lb/MMBtu | ERT |  | 6 | 6 | 1832 |  | 0.0009369 | 0.0009369 |  | 0.00096368 | corrected | 10.7344 | 0.010057 | PM control | Fabric Filter, pulse | 1999-12-01
52071_5B | coal | 31 |  | 52071 | Sandow Station | 5B | 5B | Fluidized bed firing | Fluidized bed firing | 2960 | 282.35 | Filterable Particulate | 0.00098701 | lb/MMBtu | ERT |  | 6 | 6 | 830 |  | 0.00098701 | 0.00098701 |  | 0.0010008 | corrected | 10.4834 | 0.010347
891_Boiler 9 | coal | 32 |  | 891 | Havana | Boiler 9 | Boiler 9 | Conventional Boiler | Wall firing - unspecified | 481 | 5030 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 5 | 1 | 0 |  |  |  | 0.001 |  | 0.0018229 | Corrected | 10.4574 | 0.010457 | PM control | Electrostatic precipitator, hot side, unspecified | 1978-04-01 | NOx control | Selective Catalytic Reduction | 2003-08-01 | Other control | Activated carbon injection | 2009-07-01 | SO2 control | Dry FGD - Spray Dryer |  | PM control | Fabric Filter, unspecified | 2009-06-01
6180_1 | coal | 33 |  | 6180 | Oak Grove | 1 | OG1 | Conventional Boiler | Conventional Boiler | 817 | 8970 | Filterable Particulate | 0.0010178 | lb/MMBtu | Part II | 1-Compliance Test Report | 3 | 3 |  |  | 0.0009 | 0.0010178 | Corrected | 0.0016551 | Corrected | 10.9792 | 0.011175
470_2 | coal | 34 |  | 470 | Comanche | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 365 | 3482 | Filterable Particulate | 0.0012059 | lb/MMBtu | ERT |  | 3 | 3 | 1449 |  | 0.0012059 | 0.0012059 |  | 0.0012059 |  | 9.5397 | 0.011504 | Other control | Activated carbon injection |  | SO2 control | Dry FGD - Spray Dryer | 2008-07-01 | PM control | Fabric Filter, reverse air | 1991-12-01
897_Unit 1 | coal | 35 |  | 897 | Vermilion | Unit 1 | 001 | Conventional Boiler | Tangential firing | 72 | 831 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 8 | 1 | 0 |  |  |  | 0.001 |  | 0.0017128 | Corrected | 11.5417 | 0.011542 | PM control | Electrostatic precipitator, unspecified | 1973-06-01 | Other control | Activated carbon injection | 2007-05-01 | PM control | Fabric Filter, unspecified | 2007-05-01
7504_2 | coal | 36 |  | 7504 | Neil Simpson II | 2 | NS2Cfg | Conventional Boiler | Wall firing - front firing | 88 | 1100 | Filterable Particulate | 0.00092616 | lb/MMBtu | ERT |  | 6 | 6 | 1382 |  | 0.00092616 | 0.00092616 |  | 0.00093214 | corrected | 12.5 | 0.011577
6077_1 | coal | 37 |  | 6077 | Gerald Gentleman | 1 | U1 | Conventional Boiler | Wall firing - opposed firing | 715 | 7538 | Filterable Particulate | 0.0011321 | lb/MMBtu | ERT |  | 6 | 6 | 2170 |  | 0.0011321 | 0.0011321 |  | 0.0012072 | corrected | 10.5427 | 0.011935 | PM control | Fabric Filter, reverse air | 2000-12-01
3845_BD22 | coal | 38 |  | 3845 | TransAlta Centralia Generation | BD22 | BW22CONFIG | Conventional Boiler | Tangential firing | 567 | 7743 | Filterable Particulate | 0.00088166 | lb/MMBtu | Part II | 2006 Compliance Unit 2 | 3 | 0 |  |  | 0.00073333 | 0.00088166 | Corrected | 0.00165 | Corrected | 13.6561 | 0.01204 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1971-12-01 | SO2 control | Wet FGD - Spray Type | 2001-10-01
2079_5A | coal | 39 |  | 2079 | Hawthorn | 5A | 5A | Conventional Boiler | Wall firing - opposed firing | 594 | 6600 | Filterable Particulate | 0.0011025 | lb/MMBtu | ERT |  | 6 | 6 | 1398 |  | 0.0011025 | 0.0011025 |  | 0.0011025 |  | 11.1111 | 0.01225 | NOx control | Selective Catalytic Reduction | 2001-05-01 | SO2 control | Dry FGD - Spray Dryer | 2001-05-01 | PM control | Fabric Filter, pulse | 2001-05-01
1626_3 | coal | 40 |  | 1626 | Salem Harbor | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 151.751 | 1783 | Filterable Particulate | 0.0010546 | lb/MMBtu | Part II | 2008Unit3PM | 1 | 0 |  |  |  | 0.0010546 | Corrected | 0.0021092 | Corrected | 11.7495 | 0.012391
50888_BLR1 | coal | 41 |  | 50888 | Northampton Generating Company, L.P. | BLR1 | GEN1 | Fluidized bed firing | Fluidized bed firing | 121 | 1146 | Filterable Particulate | 0.00135 | lb/MMBtu | Part II | AWC/PC/PPR April 2006 | 3 | 0 |  |  | 0.00135 | 0.00135 |  | 0.0017128 | Corrected | 9.4711 | 0.012786 | NOx control | Selective Noncatalytic Reduction | 1995-08-01 | PM control | Fabric Filter, pulse | 1995-08-01
4041_7 | coal | 42 |  | 4041 | South Oak Creek | 7 | OCPP-B7 | Conventional Boiler | Tangential firing | 320 | 2856 | Filterable Particulate | 0.0015333 | lb/MMBtu | ERT |  | 6 | 6 | 1021 |  | 0.0015333 | 0.0015333 |  | 0.0015333 |  | 8.925 | 0.013684 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1992-07-01
10673_BLR B | coal | 43 |  | 10673 | AES Hawaii | BLR B | 002 | Fluidized bed firing | Fluidized bed firing | 101.5 | 944.2 | Filterable Particulate | 0.0014764 | lb/MMBtu | ERT |  | 6 | 6 | 77922 |  | 0.0014764 | 0.0014764 |  | 0.0014764 |  | 9.3025 | 0.013734 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
2451_Unit 3 | coal | 44 |  | 2451 | San Juan | Unit 3 | Unit 3 | Conventional Boiler | Wall firing - opposed firing | 544 | 5758 | Filterable Particulate | 0.0013557 | lb/MMBtu | ERT |  | 3 | 3 | 23152 |  | 0.0013557 | 0.0013557 |  | 0.0013557 |  | 10.5846 | 0.014349 | Other control | Activated carbon injection | 2008-04-01 | PM control | Fabric Filter, pulse | 2008-03-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
1082_3 | coal | 45 |  | 1082 | Walter Scott Jr. Energy Center | 3 | 3 | Conventional Boiler | Wall firing - unspecified | 765 | 7700 | Filterable Particulate | 0.0014273 | lb/MMBtu | Part II | 6/2009 PM | 1 | 0 |  |  |  | 0.0014273 |  | 0.0018036 | Corrected | 10.0654 | 0.014366 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01
3845_BD21 | coal | 46 |  | 3845 | TransAlta Centralia Generation | BD21 | BW21CONFIG | Conventional Boiler | Tangential firing | 603 | 7743 | Filterable Particulate | 0.0011428 | lb/MMBtu | Part II | 2006 Compliance Unit 1 | 3 | 0 |  |  | 0.001 | 0.0011428 | Corrected | 0.0016724 | Corrected | 12.8408 | 0.014675 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-01-01 | SO2 control | Wet FGD - Spray Type | 2002-06-01
7210_COP1 | coal | 47 |  | 7210 | Cope | COP1 | COP001 | Conventional Boiler | Tangential firing | 441 | 4059.1 | Filterable Particulate | 0.0016 | lb/MMBtu | Part II | PM-10/09 | 1 | 0 |  |  |  | 0.0016 |  | 0.001836 | Corrected | 9.2043 | 0.014727 | NOx control | Selective Catalytic Reduction | 2009-01-01 | SO2 control | Dry FGD - Spray Dryer | 1993-04-01 | PM control | Fabric Filter, unspecified | 1993-04-01
3944_2 | coal | 48 |  | 3944 | Harrison Power Station | 2 | Boiler2 | Conventional Boiler | Wall firing - unspecified | 692 | 6042 | Filterable Particulate | 0.0018667 | lb/MMBtu | Part II | 4 | 3 | 0 |  |  | 0.0018667 | 0.0018667 |  | 0.0022066 | Corrected | 8.7312 | 0.016298
6002_4 | coal | 49 |  | 6002 | James H. Miller Jr. | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 723 | 6976.5291 | Filterable Particulate | 0.0017209 | lb/MMBtu | ERT |  | 3 | 3 | 203612 |  | 0.0017209 | 0.0017209 |  | 0.0017209 |  | 9.6494 | 0.016606 | NOx control | Selective Catalytic Reduction | 2003-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-03-01 | SO2 control | Wet FGD - Spray Type
1554_2 | coal | 50 |  | 1554 | Herbert A. Wagner | 2 | 002 | Conventional Boiler | Wall firing - unspecified | 145 | 1488 | Filterable Particulate | 0.0016609 | lb/MMBtu | ERT |  | 3 | 3 | 2195 |  | 0.0016609 | 0.0016609 |  | 0.0016609 |  | 10.2621 | 0.017045
1710_Unit 2 | coal | 51 |  | 1710 | Consumers Energy - J.H. Campbell | Unit 2 | JHC2-Conf | Conventional Boiler | Wall firing - front firing | 374 | 3392 | Filterable Particulate | 0.0019333 | lb/MMBtu | Part II | JHC12-PM 2008 Compliance Testing | 3 | 3 |  |  | 0.0019333 | 0.0019333 |  | 0.0019732 | Corrected | 9.0695 | 0.017534 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-12-01
3287_MCM1 | coal | 52 |  | 3287 | McMeekin | MCM1 | MCM001 | Conventional Boiler | Tangential firing | 135 | 1143.5 | Filterable Particulate | 0.0021 | lb/MMBtu | Part II | PM-01/07-MCM1 | 1 | 0 |  |  |  | 0.0021 |  | 0.0021 |  | 8.4704 | 0.017788 | PM control | Fabric Filter, unspecified | 1993-04-01
87_1 | coal | 53 |  | 87 | Escalante | 1 | 1 | Conventional Boiler | Tangential firing | 260 | 2366 | Filterable Particulate | 0.0019708 | lb/MMBtu | Part II | 2007 PM Test | 3 | 3 |  |  | 0.0019708 | 0.0019708 |  | 0.0020105 | Corrected | 9.1 | 0.017935 | PM control | Fabric Filter, reverse air | 1984-01-01 | SO2 control | Wet FGD - Spray Type | 1984-01-01
1710_Unit 1 | coal | 54 |  | 1710 | Consumers Energy - J.H. Campbell | Unit 1 | JHC1-Conf | Conventional Boiler | Tangential firing | 274 | 2561 | Filterable Particulate | 0.0019333 | lb/MMBtu | Part II | JHC12-PM 2008 Compliance Testing | 3 | 3 |  |  | 0.0019333 | 0.0019333 |  | 0.0019732 | Corrected | 9.3467 | 0.01807 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2001-07-01
6181_2 | coal | 55 |  | 6181 | J T Deely | 2 | 2 | Conventional Boiler | Tangential firing | 450 | 4251 | Filterable Particulate | 0.0019178 | lb/MMBtu | ERT |  | 6 | 6 | 452145 |  | 0.0019178 | 0.0019178 |  | 0.0019178 |  | 9.4467 | 0.018116 | PM control | Fabric Filter, reverse air | 2006-04-01
6181_1 | coal | 56 |  | 6181 | J T Deely | 1 | 1 | Conventional Boiler | Tangential firing | 450 | 4251 | Filterable Particulate | 0.0019178 | lb/MMBtu | ERT |  | 6 | 6 | 452145 |  | 0.0019178 | 0.0019178 |  | 0.0019178 |  | 9.4467 | 0.018116 | PM control | Fabric Filter, reverse air | 2007-05-01
4078_4 | coal | 57 |  | 4078 | Weston | 4 | W4 | Conventional Boiler | Wall firing - opposed firing | 574.5 | 5173.07 | Filterable Particulate | 0.0021071 | lb/MMBtu | ERT |  | 6 | 6 | 1611 |  | 0.0021071 | 0.0021071 |  | 0.0021071 |  | 9.0045 | 0.018973 | NOx control | Selective Catalytic Reduction | 2008-07-01 | Other control | Activated carbon injection | 2008-07-01 | SO2 control | Dry FGD - Spray Dryer | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-07-01
26_3 | coal | 58 |  | 26 | E. C. Gaston | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 270 | 2462.7795 | Filterable Particulate | 0.0021 | lb/MMBtu | Part II | Unit 3 PM Emissions Test (April 15, 2005) | 3 | 0 |  |  | 0.0021 | 0.0021 |  | 0.0023566 | Corrected | 9.1214 | 0.019155
2712_2 | coal | 59 |  | 2712 | Roxboro Steam Electric Plant | 2 | Rox_Cfg_2c | Conventional Boiler | Tangential firing | 703 | 6893 | Filterable Particulate | 0.0019832 | lb/MMBtu | ERT |  | 6 | 6 | 985 |  | 0.0019832 | 0.0019832 |  | 0.0019832 |  | 9.8051 | 0.019446 | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-05-01 | SO2 control | Wet FGD - Spray/Tray Type | 2007-04-20
6041_4 | coal | 60 |  | 6041 | H L Spurlock Station | 4 | Unit 04 | Fluidized bed firing | Fluidized bed firing | 300 | 2800 | Filterable Particulate | 0.0021333 | lb/MMBtu | Part II | Compliance_PM_05/27/09 | 3 | 3 |  |  | 0.0021333 | 0.0021333 |  | 0.0021333 |  | 9.3333 | 0.019911 | NOx control | Selective Noncatalytic Reduction | 2009-04-01 | SO2 control | Dry FGD - Unspecified | 2009-04-01 | PM control | Fabric Filter, pulse | 2009-04-01
3287_MCM2 | coal | 61 |  | 3287 | McMeekin | MCM2 | MCM002 | Conventional Boiler | Tangential firing | 132 | 1101.3 | Filterable Particulate | 0.0024 | lb/MMBtu | Part II | PM-01/06-MCM2 | 1 | 0 |  |  |  | 0.0024 |  | 0.0024 |  | 8.3432 | 0.020024 | PM control | Fabric Filter, unspecified | 1992-11-01
2324_1 | coal | 62 |  | 2324 | Reid Gardner | 1 | 1 | Conventional Boiler | Wall firing - front firing | 111 | 1215 | Filterable Particulate | 0.0019244 | lb/MMBtu | ERT |  | 3 | 3 | 1972 |  | 0.0019244 | 0.0019244 |  | 0.0019244 |  | 10.9459 | 0.021065 | PM control | Fabric Filter, pulse | 2008-12-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
2706_1 | coal | 63 |  | 2706 | Asheville Steam Electric Plant | 1 | Ash_Cfg_1d | Conventional Boiler | Wall firing - front firing | 207 | 1914 | Filterable Particulate | 0.0022867 | lb/MMBtu | Part II | Ash_Blr_1_Test_8p | 9 | 9 |  |  | 0.0022867 | 0.0022867 |  | 0.002324 | Corrected | 9.2464 | 0.021143 | NOx control | Selective Catalytic Reduction | 2007-06-14 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2005-11-17 | SO2 control | Wet FGD - Spray/Tray Type | 2005-11-17
130_1 | coal | 64 |  | 130 | Cross | 1 | C1 | Conventional Boiler | Wall firing - opposed firing | 610 | 6502 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | C1PM2008 | 1 | 1 |  |  |  | 0.002 |  | 0.002 |  | 10.659 | 0.021318 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-05-01 | SO2 control | Wet FGD - Spray Type | 1995-05-01
207_PPBoiler1 | coal | 65 |  | 207 | St Johns River Power Park | PPBoiler1 | PPUnit1Configuration | Conventional Boiler | Wall firing - opposed firing | 660 | 6144 | Filterable Particulate | 0.0023333 | lb/MMBtu | Part II | S1_2009_PM | 3 | 3 |  |  | 0.0023333 | 0.0023333 |  | 0.0026301 | Corrected | 9.3091 | 0.021721
54238_N64516 | coal | 66 |  | 54238 | Port of Stockton District Energy Facility | N64516 | 1 | Fluidized bed firing | Fluidized bed firing | 25 | 285 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 2006 Unit A | 3 | 0 |  |  | 0.002 | 0.002 |  | 0.002 |  | 11.4 | 0.0228
54238_N64514 | coal | 67 |  | 54238 | Port of Stockton District Energy Facility | N64514 | 1 | Fluidized bed firing | Fluidized bed firing | 25 | 285 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 2006 Unit A | 3 | 0 |  |  | 0.002 | 0.002 |  | 0.002 |  | 11.4 | 0.0228
1733_4 | coal | 68 |  | 1733 | Monroe Power Plant | 4 | MN4-Config | Conventional Boiler | Wall firing - opposed firing | 815 | 7140 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | PM2009_Sep_4b | 3 | 0 |  |  | 0.0026667 | 0.0026667 |  | 0.0026667 |  | 8.7607 | 0.023362
1379_10 | coal | 69 |  | 1379 | Shawnee | 10 | 10 | Fluidized bed firing | Fluidized bed firing | 175 | 1800 | Filterable Particulate | 0.0023333 | lb/MMBtu | Part II | SHF10 - 2006 | 3 | 3 |  |  | 0.0023333 | 0.0023333 |  | 0.0024077 | Corrected | 10.2857 | 0.024
8223_2 | coal | 70 |  | 8223 | Springerville | 2 | 2 | Conventional Boiler | Tangential firing | 430 | 3830 | Filterable Particulate | 0.0027 | lb/MMBtu | Part II | U2 PERF 06JUN05 | 1 | 1 |  |  |  | 0.0027 |  | 0.0027 |  | 8.907 | 0.024049 | SO2 control | Dry FGD - Spray Dryer | 1990-06-01 | PM control | Fabric Filter, reverse air | 1990-06-01
4041_8 | coal | 71 |  | 4041 | South Oak Creek | 8 | OCPP-B8 | Conventional Boiler | Tangential firing | 336 | 3009 | Filterable Particulate | 0.0027333 | lb/MMBtu | Part II | OCPP-PM-B8-6.2005 | 3 | 3 |  |  | 0.0027333 | 0.0027333 |  | 0.0027333 |  | 8.9554 | 0.024478 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-07-01
645_4 | coal | 72 |  | 645 | Big Bend | 4 | BB04_SCR_iso | Conventional Boiler | Tangential firing | 465 | 4330 | Filterable Particulate | 0.0026473 | lb/MMBtu | Part II | BB#4_ECOTHERM | 1 | 0 |  |  |  | 0.0026473 |  | 0.0026473 |  | 9.3118 | 0.024651
4078_3 | coal | 73 |  | 4078 | Weston | 3 | W3 | Conventional Boiler | Tangential firing | 365.6 | 3423.48 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | W3 PM 2009 | 3 | 3 |  |  | 0.0026667 | 0.0026667 |  | 0.0026667 |  | 9.364 | 0.024971 | PM control | Fabric Filter, pulse | 2001-05-01 | Other control | Activated carbon injection
3138_3 | coal | 74 |  | 3138 | New Castle Plant | 3 | NC3-2 | Conventional Boiler | Wall firing - front firing | 98 | 1025 | Filterable Particulate | 0.0024 | lb/MMBtu | Part II | NC-50 | 4 | 4 |  |  | 0.0024 | 0.0024 |  | 0.0024547 | Corrected | 10.4592 | 0.025102 | NOx control | Selective Noncatalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
108_SGU1 | coal | 75 |  | 108 | HOLCOMB | SGU1 | SGU1 | Conventional Boiler | Wall firing - opposed firing | 387 | 3389 | Filterable Particulate | 0.0028667 | lb/MMBtu | Part II | 2009-10150 | 3 | 3 |  |  | 0.0028667 | 0.0028667 |  | 0.0028667 |  | 8.7571 | 0.025104
2706_2 | coal | 76 |  | 2706 | Asheville Steam Electric Plant | 2 | Ash_Cfg_2 | Conventional Boiler | Wall firing - front firing | 204 | 1902 | Filterable Particulate | 0.0027 | lb/MMBtu | Part II | Ash_Blr_2_Test_7t | 3 | 3 |  |  | 0.0027 | 0.0027 |  | 0.0027 |  | 9.3235 | 0.025174 | NOx control | Selective Catalytic Reduction | 2006-06-14 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Spray/Tray Type | 2006-05-15
1626_2 | coal | 77 |  | 1626 | Salem Harbor | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 78.763 | 1014 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 2005Unit2PM | 1 | 0 |  |  |  | 0.002 |  | 0.0020143 | Corrected | 12.8741 | 0.025748
8226_1 | coal | 78 |  | 8226 | Cheswick Power Plant | 1 | CH2 | Conventional Boiler | Tangential firing | 612 | 6000 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | CH-23B | 3 | 3 |  |  | 0.0026667 | 0.0026667 |  | 0.0029778 | Corrected | 9.8039 | 0.026144
50_6 | coal | 79 |  | 50 | Widows Creek | 6 | 6 | Conventional Boiler | Wall firing - front firing | 140.6 | 1589 | Filterable Particulate | 0.0023333 | lb/MMBtu | Part II | WCF6 - 2007 | 3 | 3 |  |  | 0.0023333 | 0.0023333 |  | 0.0026209 | Corrected | 11.3016 | 0.02637
8224_1 | coal | 80 |  | 8224 | North Valmy | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 243.5 | 2560 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | U1_2006_COMPLIANCE | 3 | 3 |  |  | 0.0025333 | 0.0025333 |  | 0.0025333 |  | 10.5133 | 0.026634 | PM control | Fabric Filter, reverse air | 1981-12-01
8223_1 | coal | 81 |  | 8223 | Springerville | 1 | 1 | Conventional Boiler | Tangential firing | 427 | 3830 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | U1 PERF 06JUN01 (PM RETEST) | 1 | 1 |  |  |  | 0.003 |  | 0.003 |  | 8.9696 | 0.026909 | SO2 control | Dry FGD - Spray Dryer | 1985-06-01 | PM control | Fabric Filter, reverse air | 1985-06-01
1082_4 | coal | 82 |  | 1082 | Walter Scott Jr. Energy Center | 4 | 4 | Conventional Boiler | Wall firing - unspecified | 850 | 7675 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 5/2007 PM | 1 | 0 |  |  |  | 0.003 |  | 0.003 |  | 9.0294 | 0.027088 | NOx control | Selective Catalytic Reduction | 2007-02-01 | Other control | Activated carbon injection | 2007-02-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-02-01 | PM control | Fabric Filter, pulse | 2007-02-01
2712_1 | coal | 83 |  | 2712 | Roxboro Steam Electric Plant | 1 | Rox_Cfg_1b | Conventional Boiler | Wall firing - opposed firing | 385 | 3755 | Filterable Particulate | 0.0028093 | lb/MMBtu | ERT |  | 6 | 6 | 983 |  | 0.0028093 | 0.0028093 |  | 0.0028093 |  | 9.7532 | 0.027399 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01 | SO2 control | Wet FGD - Spray/Tray Type | 2008-12-01
1740_3 | coal | 84 |  | 1740 | River Rouge Power Plant | 3 | RR3-Config | Conventional Boiler | Wall firing - front firing | 293 | 2679 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 2009Dec_3 | 2 | 0 |  |  | 0.003 | 0.003 |  | 0.003 |  | 9.1433 | 0.02743
981_3 | coal | 85 |  | 981 | State Line | 3 | Unit 3 | Conventional Boiler | Tangential firing | 216 | 2380 | Filterable Particulate | 0.0025 | lb/MMBtu | Part II | Unit3_2007 | 1 | 0 |  |  |  | 0.0025 |  | 0.0025 |  | 11.0185 | 0.027546 | PM control | Fabric Filter, pulse | 1999-01-01
3280_CAN3 | coal | 86 |  | 3280 | Canadys Steam | CAN3 | CAN003 | Conventional Boiler | Wall firing - unspecified | 185 | 1824.5 | Filterable Particulate | 0.0028 | lb/MMBtu | Part II | PM-02/06-CAN3 | 1 | 0 |  |  |  | 0.0028 |  | 0.0028 |  | 9.8622 | 0.027614 | PM control | Fabric Filter, unspecified | 1998-07-01 | [13 empty] | 0
10002_1 | coal | 87 |  | 10002 | ACE Cogeneration Company | 1 | Config 1 | Fluidized bed firing | Fluidized bed firing | 117 | 1052 | Filterable Particulate | 0.0031 | lb/MMBtu | Part II | 06212005 | 1 | 1 |  |  |  | 0.0031 |  | 0.0031 |  | 8.9915 | 0.027874
1743_3 | coal | 88 |  | 1743 | St Clair Power Plant | 3 | SC3-Config | Conventional Boiler | Wall firing - front firing | 174 | 1765 | Filterable Particulate | 0.00275 | lb/MMBtu | Part II | 2009Sep_3 | 4 | 0 |  |  | 0.00275 | 0.00275 |  | 0.00275 |  | 10.1437 | 0.027895
113_3 | coal | 89 |  | 113 | Cholla | 3 | 003 | Conventional Boiler | Tangential firing | 305 | 2929 | Filterable Particulate | 0.002924 | lb/MMBtu | ERT |  | 3 | 3 | 1647 |  | 0.002924 | 0.002924 |  | 0.002924 |  | 9.6033 | 0.02808 | PM control | Fabric Filter, unspecified | 2009-01-01 | SO2 control | Wet FGD - Unspecified | 2009-01-01
4042_3 | coal | 90 |  | 4042 | Valley | 3 | VAPP-B3 | Conventional Boiler | Wall firing - front firing | 72 | 868 | Filterable Particulate | 0.0023648 | lb/MMBtu | ERT |  | 6 | 6 | 735 |  | 0.0023648 | 0.0023648 |  | 0.0023648 |  | 12.0556 | 0.028509 | PM control | Fabric Filter, pulse | 1995-06-01
564_1 | coal | 91 |  | 564 | Stanton Energy Center | 1 | 1 coal | Conventional Boiler | Wall firing - opposed firing | 468 | 4286 | Filterable Particulate | 0.0031333 | lb/MMBtu | Part II | Unit 1 PM 2009 | 3 | 3 |  |  | 0.0031333 | 0.0031333 |  | 0.0031333 |  | 9.1581 | 0.028695
7213_2 | coal | 92 |  | 7213 | Clover | 2 | Unit 2 | Conventional Boiler | Tangential firing | 434 | 5041 | Filterable Particulate | 0.0025465 | lb/MMBtu | ERT |  | 3 | 3 | 1535 |  | 0.0025465 | 0.0025465 |  | 0.0025465 |  | 11.6152 | 0.029578 | NOx control | Selective Noncatalytic Reduction | 2003-03-01 | PM control | Fabric Filter, reverse air | 2003-05-01 | SO2 control | Wet FGD - Spray Type | 2003-05-01
8_10 | coal | 93 |  | 8 | Gorgas | 10 | Unit 10 | Conventional Boiler | Tangential firing | 720 | 6523.794 | Filterable Particulate | 0.0032663 | lb/MMBtu | Part II | UNITS 8-10 FGD PERFORMANCE TESTING | 6 | 6 |  |  | 0.0032663 | 0.0032663 |  | 0.0032663 |  | 9.0608 | 0.029595 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-10-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
7097_BLR1 | coal | 94 |  | 7097 | J K Spruce | BLR1 | 1 | Conventional Boiler | Tangential firing | 580 | 6361 | Filterable Particulate | 0.0027209 | lb/MMBtu | ERT |  | 6 | 6 | 1515 |  | 0.0027209 | 0.0027209 |  | 0.0027209 |  | 10.9672 | 0.02984 | PM control | Fabric Filter, reverse air | 1992-07-01 | SO2 control | Wet FGD - Spray Type | 1992-12-01
8_8 | coal | 95 |  | 8 | Gorgas | 8 | Unit 8 | Conventional Boiler | Tangential firing | 175 | 1600.8973 | Filterable Particulate | 0.0032663 | lb/MMBtu | Part II | UNITS 8-10 FGD PERFORMANCE TESTING | 6 | 6 |  |  | 0.0032663 | 0.0032663 |  | 0.0032663 |  | 9.148 | 0.02988 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
4042_4 | coal | 96 |  | 4042 | Valley | 4 | VAPP-B4 | Conventional Boiler | Wall firing - front firing | 72 | 868 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | VAPP-PM-B1B2B3B4-8.2005 | 3 | 3 |  |  | 0.0025333 | 0.0025333 |  | 0.0025333 |  | 12.0556 | 0.030541 | PM control | Fabric Filter, pulse | 1995-06-01
1743_6 | coal | 97 |  | 1743 | St Clair Power Plant | 6 | SC6-Config | Conventional Boiler | Tangential firing | 331 | 3045 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | PM2007_Oct6 | 3 | 0 |  |  | 0.0033333 | 0.0033333 |  | 0.0033333 |  | 9.1994 | 0.030665
8_9 | coal | 98 |  | 8 | Gorgas | 9 | Unit 9 | Conventional Boiler | Tangential firing | 185 | 1738.6247 | Filterable Particulate | 0.0032663 | lb/MMBtu | Part II | UNITS 8-10 FGD PERFORMANCE TESTING | 6 | 6 |  |  | 0.0032663 | 0.0032663 |  | 0.0032663 |  | 9.398 | 0.030696 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
3403_4 | coal | 99 |  | 3403 | Gallatin | 4 | 4 | Conventional Boiler | Tangential firing | 327.6 | 3032 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | GAF3-4 - 2006 | 3 | 3 |  |  | 0.0033333 | 0.0033333 |  | 0.0033333 |  | 9.2552 | 0.030851
3403_3 | coal | 100 |  | 3403 | Gallatin | 3 | 3 | Conventional Boiler | Tangential firing | 327.6 | 3032 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | GAF3-4 - 2006 | 3 | 3 |  |  | 0.0033333 | 0.0033333 |  | 0.0033333 |  | 9.2552 | 0.030851
2107_2 | coal | 101 |  | 2107 | Sioux | 2 | 002 | Conventional Boiler | Cyclone firing | 524 | 4920 | Filterable Particulate | 0.0033472 | lb/MMBtu | ERT |  | 3 | 3 | 1915 |  | 0.0033472 | 0.0033472 |  | 0.0033472 |  | 9.3893 | 0.031428 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1997-12-01 | SO2 control | Wet FGD - Unspecified
56224_BLR100 | coal | 102 |  | 56224 | TS Power Plant | BLR100 | TSPower | Conventional Boiler | Wall firing - opposed firing | 242 | 2112 | Filterable Particulate | 0.0036333 | lb/MMBtu | Part II | TRC 04/2008 | 3 | 3 |  |  | 0.0036333 | 0.0036333 |  | 0.0036333 |  | 8.7273 | 0.031709 | NOx control | Selective Catalytic Reduction | 2008-03-01 | Other control | Activated carbon injection | 2008-03-01 | SO2 control | Dry FGD - Spray Dryer | 2008-03-01 | PM control | Fabric Filter, pulse | 2008-01-01
3140_2 | coal | 103 |  | 3140 | PPL Brunner Island | 2 | U2 | Conventional Boiler | Tangential firing | 393 | 3790 | Filterable Particulate | 0.0033 | lb/MMBtu | Part II | BI12N09 | 1 | 1 |  |  |  | 0.0033 |  | 0.0033 |  | 9.6438 | 0.031824 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2009-10-01 | SO2 control | Wet FGD - Tray Type | 2009-11-01
708_2 | coal | 104 |  | 708 | Hammond | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 115 | 1138.032 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT |  | 6 | 6 | 1984 |  | 0.0032502 | 0.0032502 |  | 0.0032502 |  | 9.8959 | 0.032164 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-04-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
641_5 | coal | 105 |  | 641 | Crist | 5 | Unit 5 | Conventional Boiler | Tangential firing | 82 | 817.83 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT |  | 6 | 6 | 1894 |  | 0.0032284 | 0.0032284 |  | 0.0032284 |  | 9.9735 | 0.032199 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
641_6 | coal | 106 |  | 641 | Crist | 6 | Unit 6 | Conventional Boiler | Wall firing - front firing | 320 | 3193.348 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT |  | 6 | 6 | 1894 |  | 0.0032284 | 0.0032284 |  | 0.0032284 |  | 9.9792 | 0.032217 | NOx control | Selective Noncatalytic Reduction | 2005-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
708_3 | coal | 107 |  | 708 | Hammond | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 115 | 1141.392 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT |  | 6 | 6 | 1984 |  | 0.0032502 | 0.0032502 |  | 0.0032502 |  | 9.9251 | 0.032259 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
602_2 | coal | 108 |  | 602 | Brandon Shores | 2 | 002 | Conventional Boiler | Wall firing - unspecified | 690 | 6700 | Filterable Particulate | 0.0033275 | lb/MMBtu | ERT |  | 3 | 3 | 2259 |  | 0.0033275 | 0.0033275 |  | 0.0033275 |  | 9.7101 | 0.032311 | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, hot side, unspecified |  | Other control | Activated carbon injection |  | Other control | Other (specify): lime injection |  | PM control | Fabric Filter, unspecified |  | SO2 control | Wet FGD - Unspecified
2837_3 | coal | 109 |  | 2837 | Eastlake | 3 | Unit 3 | Conventional Boiler | Tangential firing | 144 | 1205 | Filterable Particulate | 0.0038742 | lb/MMBtu | ERT |  | 6 | 6 | 22791 |  | 0.0038742 | 0.0038742 |  | 0.0038742 |  | 8.3681 | 0.032419 | NOx control | Selective Noncatalytic Reduction | 1999-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-01-01
2718_ES-3 | coal | 110 |  | 2718 | G G Allen | ES-3 | 3-2009 | Conventional Boiler | Tangential firing | 281.5 | 2228 | Filterable Particulate | 0.0041114 | lb/MMBtu | ERT |  | 3 | 3 | 900 |  | 0.0041114 | 0.0041114 |  | 0.0041114 |  | 7.9147 | 0.032541 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2002-06-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
2727_Unit 1 | coal | 111 |  | 2727 | Marshall | Unit 1 | U12007 | Conventional Boiler | Tangential firing | 400 | 3658.2 | Filterable Particulate | 0.0035667 | lb/MMBtu | Part II | CS001020409 | 3 | 3 |  |  | 0.0035667 | 0.0035667 |  | 0.0038032 | Corrected | 9.1455 | 0.032619
2727_Unit 2 | coal | 112 |  | 2727 | Marshall | Unit 2 | U22007 | Conventional Boiler | Tangential firing | 400 | 3663.2 | Filterable Particulate | 0.0035667 | lb/MMBtu | Part II | CS001020409 | 3 | 3 |  |  | 0.0035667 | 0.0035667 |  | 0.0038032 | Corrected | 9.158 | 0.032664
708_1 | coal | 113 |  | 708 | Hammond | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 115 | 1158.752 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT |  | 6 | 6 | 1984 |  | 0.0032502 | 0.0032502 |  | 0.0032502 |  | 10.0761 | 0.03275 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-02-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
2718_ES-4 | coal | 114 |  | 2718 | G G Allen | ES-4 | 4-2009 | Conventional Boiler | Tangential firing | 297.3 | 2380 | Filterable Particulate | 0.0041114 | lb/MMBtu | ERT |  | 3 | 3 | 900 |  | 0.0041114 | 0.0041114 |  | 0.0041114 |  | 8.0054 | 0.032913 | NOx control | Selective Noncatalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1999-02-01 | SO2 control | Wet FGD - Spray Type | 2009-04-01
2727_Unit 4 | coal | 115 |  | 2727 | Marshall | Unit 4 | U4 | Conventional Boiler | Tangential firing | 700 | 6029.8 | Filterable Particulate | 0.0038333 | lb/MMBtu | Part II | U4020509 | 3 | 3 |  |  | 0.0038333 | 0.0038333 |  | 0.0038333 |  | 8.614 | 0.03302
2451_Unit 4 | coal | 116 |  | 2451 | San Juan | Unit 4 | Unit 4 | Conventional Boiler | Wall firing - opposed firing | 544 | 5649 | Filterable Particulate | 0.0031961 | lb/MMBtu | ERT |  | 3 | 3 | 23153 |  | 0.0031961 | 0.0031961 |  | 0.0031961 |  | 10.3842 | 0.033189 | Other control | Activated carbon injection | 2008-04-01 | PM control | Fabric Filter, pulse | 2007-10-01 | SO2 control | Wet FGD - Spray Type | 1998-04-01
3140_1 | coal | 117 |  | 3140 | PPL Brunner Island | 1 | U1 | Conventional Boiler | Tangential firing | 330 | 3345 | Filterable Particulate | 0.0033 | lb/MMBtu | Part II | BI12N09 | 1 | 1 |  |  |  | 0.0033 |  | 0.0033 |  | 10.1364 | 0.03345 | PM control | Fabric Filter, pulse | 1965-01-01 | SO2 control | Wet FGD - Tray Type | 2009-11-01
56068_1 | coal | 118 |  | 56068 | Elm Road Generating Station | 1 | ERGS-B1 | Conventional Boiler | Wall firing - unspecified | 677 | 6515 | Filterable Particulate | 0.0035045 | lb/MMBtu | ERT |  | 3 | 3 | 2319 |  | 0.0035045 | 0.0035045 |  | 0.0035045 |  | 9.6233 | 0.033725 | NOx control | Selective Catalytic Reduction | 2009-10-01 | PM control | Fabric Filter, pulse | 2009-10-01 | SO2 control | Wet FGD - Spray Type | 2009-10-01 | Other control | Wet electrostatic precipitator | 2009-10-01
7213_1 | coal | 119 |  | 7213 | Clover | 1 | Unit 1 | Conventional Boiler | Tangential firing | 431 | 4923 | Filterable Particulate | 0.0029671 | lb/MMBtu | ERT |  | 3 | 3 | 1534 |  | 0.0029671 | 0.0029671 |  | 0.0029671 |  | 11.4223 | 0.033891 | PM control | Fabric Filter, reverse air | 2003-05-01 | SO2 control | Wet FGD - Spray Type | 2003-05-01
50_5 | coal | 120 |  | 50 | Widows Creek | 5 | 5 | Conventional Boiler | Wall firing - front firing | 140.6 | 1589 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | WCF5 - 10/25/2006 | 3 | 3 |  |  | 0.003 | 0.003 |  | 0.0033048 | Corrected | 11.3016 | 0.033905
1710_Unit 3 | coal | 121 |  | 1710 | Consumers Energy - J.H. Campbell | Unit 3 | JHC3-Conf | Conventional Boiler | Wall firing - front firing | 869 | 8199 | Filterable Particulate | 0.0036 | lb/MMBtu | Part II | JHC3 - 2008 Particulate Test | 3 | 3 |  |  | 0.0036 | 0.0036 |  | 0.0036 |  | 9.435 | 0.033966
641_7 | coal | 122 |  | 641 | Crist | 7 | Unit 7 | Conventional Boiler | Wall firing - front firing | 500 | 5279.792 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT |  | 6 | 6 | 1894 |  | 0.0032284 | 0.0032284 |  | 0.0032284 |  | 10.5596 | 0.034091 | NOx control | Selective Catalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2004-04-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
708_4 | coal | 123 |  | 708 | Hammond | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 520 | 5458.53 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT |  | 6 | 6 | 1984 |  | 0.0032502 | 0.0032502 |  | 0.0032502 |  | 10.4972 | 0.034118 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
641_4 | coal | 124 |  | 641 | Crist | 4 | Unit 4 | Conventional Boiler | Tangential firing | 82 | 868.842 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT |  | 6 | 6 | 1894 |  | 0.0032284 | 0.0032284 |  | 0.0032284 |  | 10.5956 | 0.034207 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
10672_CBB | coal | 125 |  | 10672 | Cedar Bay Generating Company L.P. | CBB | CBB1 | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | CBB2009pm | 1 | 1 |  |  |  | 0.003 |  | 0.003 |  | 11.5543 | 0.034663 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
47_1 | coal | 126 |  | 47 | Colbert | 1 | 1 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | COF1 - 2006 | 3 | 3 |  |  | 0.0033333 | 0.0033333 |  | 0.0033333 |  | 10.605 | 0.03535
6016_1 | coal | 127 |  | 6016 | Duck Creek | 1 | 001 | Conventional Boiler | Wall firing - unspecified | 400 | 4500 | Filterable Particulate | 0.0032 | lb/MMBtu | Part II | 3 | 1 | 0 |  |  |  | 0.0032 |  | 0.0032 |  | 11.25 | 0.036 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2009-03-01 | SO2 control | Wet FGD - Venturi Type | 2009-03-01
10151_BLR1B | coal | 128 |  | 10151 | Grant Town Power Plant | BLR1B | GEN1 | Fluidized bed firing | Fluidized bed firing | 47.5 | 675 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | 3 | 3 | 0 |  |  | 0.0025333 | 0.0025333 |  | 0.0025333 |  | 14.2105 | 0.036 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | PM control | Fabric Filter, pulse | 1992-07-01 | PM control | Fabric Filter, pulse | 2005-05-01
10151_BLR1A | coal | 129 |  | 10151 | Grant Town Power Plant | BLR1A | GEN1 | Fluidized bed firing | Fluidized bed firing | 47.5 | 675 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | 3 | 3 | 0 |  |  | 0.0025333 | 0.0025333 |  | 0.0025333 |  | 14.2105 | 0.036 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | PM control | Fabric Filter, pulse | 1992-07-01 | PM control | Fabric Filter, pulse | 2005-05-01
2442_5 | coal | 130 |  | 2442 | Four Corners | 5 | 005 | Conventional Boiler | Cell burner | 825 | 7520 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 6 | 1 | 0 |  |  |  | 0.004 |  | 0.004 |  | 9.1152 | 0.036461
6021_C1 | coal | 131 |  | 6021 | Craig | C1 | C1 | Conventional Boiler | Wall firing - opposed firing | 456 | 4028 | Filterable Particulate | 0.0041381 | lb/MMBtu | ERT |  | 2 | 2 | 1307 |  | 0.0041381 | 0.0041381 |  | 0.0041381 |  | 8.8333 | 0.036553 | PM control | Fabric Filter, pulse | 2003-11-01 | SO2 control | Wet FGD - Spray Type | 1980-07-01
113_4 | coal | 132 |  | 113 | Cholla | 4 | 004 | Conventional Boiler | Tangential firing | 425 | 4268 | Filterable Particulate | 0.0036504 | lb/MMBtu | ERT |  | 3 | 3 | 1648 |  | 0.0036504 | 0.0036504 |  | 0.0036504 |  | 10.0424 | 0.036659 | PM control | Fabric Filter, unspecified | 2008-01-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
3403_2 | coal | 133 |  | 3403 | Gallatin | 2 | 2 | Conventional Boiler | Tangential firing | 300 | 2750 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | GAF1-2 - 2006 | 3 | 3 |  |  | 0.004 | 0.004 |  | 0.004 |  | 9.1667 | 0.036667 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-09-01
3403_1 | coal | 134 |  | 3403 | Gallatin | 1 | 1 | Conventional Boiler | Tangential firing | 300 | 2750 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | GAF1-2 - 2006 | 3 | 3 |  |  | 0.004 | 0.004 |  | 0.004 |  | 9.1667 | 0.036667
207_PPBoiler2 | coal | 135 |  | 207 | St Johns River Power Park | PPBoiler2 | PPUnit2Configuration | Conventional Boiler | Wall firing - opposed firing | 660 | 6144 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | S2_2009_PM | 3 | 3 |  |  | 0.004 | 0.004 |  | 0.004 |  | 9.3091 | 0.037236
6113_2 | coal | 136 |  | 6113 | Gibson | 2 | 2-2007-FGDIN | Conventional Boiler | Wall firing - opposed firing | 661 | 6444 | Filterable Particulate | 0.0038317 | lb/MMBtu | ERT |  | 3 | 3 | 1638 |  | 0.0038317 | 0.0038317 |  | 0.0038317 |  | 9.7489 | 0.037355 | NOx control | Selective Catalytic Reduction | 2001-12-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-01-01 | SO2 control | Wet FGD - Tray Type | 2007-05-01
54304_1A | coal | 137 |  | 54304 | Birchwood Power Facility | 1A | 1A | Conventional Boiler | Tangential firing | 222 | 2300 | Filterable Particulate | 0.0036333 | lb/MMBtu | Part II | 5/3/06 Stack Test | 3 | 3 |  |  | 0.0036333 | 0.0036333 |  | 0.0036333 |  | 10.3604 | 0.037643 | NOx control | Selective Catalytic Reduction | 1996-10-01 | SO2 control | Dry FGD - Spray Dryer | 1996-10-01 | PM control | Fabric Filter, reverse air | 1996-10-01
525_1 | coal | 138 |  | 525 | Hayden | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 202 | 1963 | Filterable Particulate | 0.0038751 | lb/MMBtu | ERT |  | 3 | 3 | 560 |  | 0.0038751 | 0.0038751 |  | 0.0038751 |  | 9.7178 | 0.037658 | SO2 control | Dry FGD - Spray Dryer | 1998-12-01 | PM control | Fabric Filter, reverse air | 1998-12-01
2451_Unit 1 | coal | 139 |  | 2451 | San Juan | Unit 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 370 | 3707 | Filterable Particulate | 0.0037689 | lb/MMBtu | ERT |  | 3 | 3 | 2315 |  | 0.0037689 | 0.0037689 |  | 0.0037689 |  | 10.0189 | 0.03776 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, pulse | 2008-10-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
8042_Unit 2 | coal | 140 |  | 8042 | Belews Creek Steam Station | Unit 2 | 2-2008 | Conventional Boiler | Wall firing - opposed firing | 1183 | 10800 | Filterable Particulate | 0.0041667 | lb/MMBtu | Part II | UNIT2(2/18/09) | 3 | 0 |  |  | 0.0041667 | 0.0041667 |  | 0.0041667 |  | 9.1293 | 0.038039
2837_1 | coal | 141 |  | 2837 | Eastlake | 1 | Unit 1 | Conventional Boiler | Tangential firing | 144 | 1205 | Filterable Particulate | 0.0045984 | lb/MMBtu | ERT |  | 6 | 6 | 2279 |  | 0.0045984 | 0.0045984 |  | 0.0045984 |  | 8.3681 | 0.03848 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
3149_1 | coal | 142 |  | 3149 | PPL Montour | 1 | U1 | Conventional Boiler | Tangential firing | 797 | 7239 | Filterable Particulate | 0.00426 | lb/MMBtu | Part II | M1PM509 | 1 | 1 |  |  |  | 0.00426 |  | 0.00426 |  | 9.0828 | 0.038693 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2001-05-01 | NOx control | Selective Catalytic Reduction | 2001-05-01 | SO2 control | Wet FGD - Tray Type | 2008-05-01
2836_12 | coal | 143 |  | 2836 | Avon Lake | 12 | AL12-2 | Conventional Boiler | Wall firing - opposed firing | 680 | 6581 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | AL-16 | 3 | 3 |  |  | 0.004 | 0.004 |  | 0.004 |  | 9.6779 | 0.038712 | NOx control | Selective Noncatalytic Reduction | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1985-01-01
6041_1 | coal | 144 |  | 6041 | H L Spurlock Station | 1 | Unit 01 | Conventional Boiler | Wall firing - opposed firing | 344 | 3641 | Filterable Particulate | 0.0036839 | lb/MMBtu | ERT |  | 3 | 3 | 994 |  | 0.0036839 | 0.0036839 |  | 0.0036839 |  | 10.5843 | 0.038991 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2003-05-01 | NOx control | Selective Catalytic Reduction | 2003-05-01 | SO2 control | Wet FGD - Unspecified | 2009-04-01 | Other control | Wet electrostatic precipitator | 2009-04-01
1252_9 | coal | 145 |  | 1252 | Tecumseh Energy Center | 9 | 9 | Conventional Boiler | Tangential firing | 82 | 846 | Filterable Particulate | 0.0038 | lb/MMBtu | Part II | PREC 0708/9 | 3 | 1 |  |  | 0.0038 | 0.0038 |  | 0.0038 |  | 10.3171 | 0.039205 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-08-01
6249_1 | coal | 146 |  | 6249 | Winyah | 1 | W1 | Conventional Boiler | Wall firing - rear firing | 295 | 2904 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | W1PM2009 | 1 | 1 |  |  |  | 0.004 |  | 0.004 |  | 9.8441 | 0.039376 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-03-01 | SO2 control | Wet FGD - Spray Type | 2007-04-01
6098_001 | coal | 147 |  | 6098 | Big Stone | 001 | 001 | Conventional Boiler | Cyclone firing | 495 | 5309 | Filterable Particulate | 0.0037255 | lb/MMBtu | ERT |  | 6 | 6 | 1151 |  | 0.0037255 | 0.0037255 |  | 0.0037255 |  | 10.7253 | 0.039956 | PM control | Fabric Filter, pulse | 2007-12-01
3944_1 | coal | 148 |  | 3944 | Harrison Power Station | 1 | Boiler1 | Conventional Boiler | Wall firing - unspecified | 693 | 5779 | Filterable Particulate | 0.0048 | lb/MMBtu | Part II | 3 | 3 | 0 |  |  | 0.0048 | 0.0048 |  | 0.0048 |  | 8.3391 | 0.040028
130_2 | coal | 149 |  | 130 | Cross | 2 | C2 | Conventional Boiler | Tangential firing | 595 | 6011 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | C2PM2009 | 1 | 1 |  |  |  | 0.004 |  | 0.004 |  | 10.1025 | 0.04041
26_2 | coal | 150 |  | 26 | E. C. Gaston | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 270 | 2511.8462 | Filterable Particulate | 0.0043667 | lb/MMBtu | Part II | Unit 2 PM Emissions Test (May 11, 2005) | 3 | 0 |  |  | 0.0043667 | 0.0043667 |  | 0.0043667 |  | 9.3031 | 0.040624
2848_H-5 | coal | 151 |  | 2848 | O H Hutchings | H-5 | H-5 | Conventional Boiler | Tangential firing | 63 | 641 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 2009 H-5 EF trail baseline metals | 2 | 2 |  |  | 0.004 | 0.004 |  | 0.004 |  | 10.1746 | 0.040698 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
50951_1 | coal | 152 |  | 50951 | Sunnyside Cogen Associates | 1 | Config 1 | Fluidized bed firing | Fluidized bed firing | 60 | 700 | Filterable Particulate | 0.0035593 | lb/MMBtu | ERT |  | 6 | 6 | 1942 |  | 0.0035593 | 0.0035593 |  | 0.0035593 |  | 11.6667 | 0.041525 | NOx control | Other (specify): Anhydrous ammonia injection | 1993-01-01 | SO2 control | Dry FGD - Sorbent Injection | 1993-01-01 | PM control | Fabric Filter, pulse | 1993-01-01
6257_3 | coal | 153 |  | 6257 | Scherer | 3 | Unit 3 | Conventional Boiler | Tangential firing | 880 | 9362.5 | Filterable Particulate | 0.003917 | lb/MMBtu | Part II | Unit 3 PM Emissions Test (January 5, 2010) | 3 | 0 |  |  | 0.003917 | 0.003917 |  | 0.003917 |  | 10.6392 | 0.041674
2727_Unit 3 | coal | 154 |  | 2727 | Marshall | Unit 3 | U3 | Conventional Boiler | Tangential firing | 700 | 6103.1 | Filterable Particulate | 0.0048 | lb/MMBtu | Part II | U3020309 | 3 | 3 |  |  | 0.0048 | 0.0048 |  | 0.0048 |  | 8.7187 | 0.04185
60_1 | coal | 155 |  | 60 | Whelan Energy Center Unit 1 (WEC1) | 1 | 1 | Conventional Boiler | Tangential firing | 83.6 | 845.1 | Filterable Particulate | 0.0041454 | lb/MMBtu | ERT |  | 6 | 6 | 3197 |  | 0.0041454 | 0.0041454 |  | 0.0041454 |  | 10.1089 | 0.041906 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
1893_3 | coal | 156 |  | 1893 | Boswell Energy Center | 3 | BEC3 | Conventional Boiler | Tangential firing | 371.3 | 4115 | Filterable Particulate | 0.0038 | lb/MMBtu | Part II | 3-Feb2010-PM | 1 | 0 |  |  |  | 0.0038 |  | 0.0038 |  | 11.0827 | 0.042114
1040_2 | coal | 157 |  | 1040 | Whitewater Valley | 2 | 002 | Conventional Boiler | Tangential firing | 69 | 730 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 4 | 1 | 0 |  |  | 0.004 | 0.004 |  | 0.004 |  | 10.5797 | 0.042319
564_2 | coal | 158 |  | 564 | Stanton Energy Center | 2 | 2 coal | Conventional Boiler | Wall firing - opposed firing | 468 | 4286 | Filterable Particulate | 0.0046667 | lb/MMBtu | Part II | Unit 2 PM 2009 | 3 | 3 |  |  | 0.0046667 | 0.0046667 |  | 0.0046667 |  | 9.1581 | 0.042738 | NOx control | Selective Catalytic Reduction | 1996-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1996-06-01 | SO2 control | Wet FGD - Spray Type | 1996-06-01
6021_C2 | coal | 159 |  | 6021 | Craig | C2 | C2 | Conventional Boiler | Wall firing - opposed firing | 456 | 4269 | Filterable Particulate | 0.0045678 | lb/MMBtu | ERT |  | 3 | 3 | 1327 |  | 0.0045678 | 0.0045678 |  | 0.0045678 |  | 9.3618 | 0.042763 | PM control | Fabric Filter, pulse | 2004-05-01 | SO2 control | Wet FGD - Spray Type | 1979-11-01
1040_1 | coal | 160 |  | 1040 | Whitewater Valley | 1 | 001 | Conventional Boiler | Wall firing - unspecified | 36 | 385 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 4 | 1 | 0 |  |  | 0.004 | 0.004 |  | 0.004 |  | 10.6944 | 0.042778
2823_B1 | coal | 161 |  | 2823 | Milton R. Young Station | B1 | 1 | Conventional Boiler | Cyclone firing | 250 | 3200 | Filterable Particulate | 0.0034635 | lb/MMBtu | Part II | Sept2005 PM emissions compliance study | 1 | 0 |  |  |  | 0.0034635 |  | 0.0034635 |  | 12.8 | 0.044333
6170_1 | coal | 162 |  | 6170 | Pleasant Prairie | 1 | PPPPB1 | Conventional Boiler | Wall firing - opposed firing | 655 | 6449 | Filterable Particulate | 0.0045134 | lb/MMBtu | Part II | PPPP-PM-U1-1.2009 | 3 | 3 |  |  | 0.0045134 | 0.0045134 |  | 0.0045134 |  | 9.8458 | 0.044438
6019_1 | coal | 163 |  | 6019 | W H Zimmer | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1408 | 12656 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | U1072809 | 3 | 3 |  |  | 0.005 | 0.005 |  | 0.005 |  | 8.9886 | 0.044943 | Other control | Other (specify): Magnesium Hydroxide Injection |  | NOx control | Selective Catalytic Reduction | 2004-01-01 | Other control | Dry sorbent injection | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-03-01 | SO2 control | Wet FGD - Spray Type | 2004-06-01
1825_3 | coal | 164 |  | 1825 | Grand Haven City of J.B. Sims | 3 | 001 | Conventional Boiler | Wall firing - unspecified | 79.7 | 755 | Filterable Particulate | 0.0048 | lb/MMBtu | Part II | 2 | 1 | 0 |  |  |  | 0.0048 |  | 0.0048 |  | 9.473 | 0.045471
2442_4 | coal | 165 |  | 2442 | Four Corners | 4 | 004 | Conventional Boiler | Cell burner | 825 | 7520 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 16 | 1 | 0 |  |  |  | 0.005 |  | 0.005 |  | 9.1152 | 0.045576
4072_8 | coal | 166 |  | 4072 | Pulliam | 8 | 8 | Conventional Boiler | Wall firing - rear firing | 137.9 | 1510 | Filterable Particulate | 0.0041887 | lb/MMBtu | ERT |  | 6 | 6 | 1597 |  | 0.0041887 | 0.0041887 |  | 0.0041887 |  | 10.95 | 0.045866 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1964-12-01
6204_1 | coal | 167 |  | 6204 | Laramie River Station | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 605 | 6420 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | Unit 1 Particulate 2005 | 3 | 3 |  |  | 0.0043333 | 0.0043333 |  | 0.0043333 |  | 10.6116 | 0.045983
6204_1 | coal | 168 |  | 6204 | Laramie River Station | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 605 | 6420 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | Unit 1 Particulate 2009 | 3 | 3 |  |  | 0.0043333 | 0.0043333 |  | 0.0043333 |  | 10.6116 | 0.045983
3122_3 | coal | 169 |  | 3122 | Homer City Station | 3 | HC3CONFIG | Conventional Boiler | Wall firing - opposed firing | 680 | 6175 | Filterable Particulate | 0.0051333 | lb/MMBtu | Part II | HC 3 Jan 2009 PM Test | 3 | 3 |  |  | 0.0051333 | 0.0051333 |  | 0.0051333 |  | 9.0809 | 0.046615
2451_Unit 2 | coal | 170 |  | 2451 | San Juan | Unit 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 370 | 3688 | Filterable Particulate | 0.0046789 | lb/MMBtu | ERT |  | 3 | 3 | 23151 |  | 0.0046789 | 0.0046789 |  | 0.0046789 |  | 9.9676 | 0.046637 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, pulse | 2009-04-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
10743_CFB2 | coal | 171 |  | 10743 | Morgantown Energy Facility | CFB2 | Unit 1&2 | Fluidized bed firing | Fluidized bed firing | 29 | 457 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 3/5/2005PM | 1 | 0 |  |  |  | 0.003 |  | 0.003 |  | 15.6897 | 0.047069 | PM control | Fabric Filter, pulse | 1992-01-01 | PM control | Fabric Filter, pulse | 1992-01-01
10743_CFB1 | coal | 172 |  | 10743 | Morgantown Energy Facility | CFB1 | Unit 1&2 | Fluidized bed firing | Fluidized bed firing | 29 | 457 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 3/5/2005PM | 1 | 0 |  |  |  | 0.003 |  | 0.003 |  | 15.6897 | 0.047069 | PM control | Fabric Filter, pulse | 1992-01-01 | PM control | Fabric Filter, pulse | 1992-01-01
3399_2 | coal | 173 |  | 3399 | Cumberland | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 1300 | 14130 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | CUF2 - 2007 | 3 | 3 |  |  | 0.0043333 | 0.0043333 |  | 0.0043333 |  | 10.8692 | 0.0471
4271_B1 | coal | 174 |  | 4271 | John P. Madgett | B1 | 001 | Conventional Boiler | Turbo | 425.73 | 4029.5 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 2 | 3 | 0 |  |  | 0.005 | 0.005 |  | 0.005 |  | 9.4649 | 0.047325
4271_B1 | coal | 175 |  | 4271 | John P. Madgett | B1 | 001 | Conventional Boiler | Turbo | 425.73 | 4029.5 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 3 | 3 | 0 |  |  | 0.005 | 0.005 |  | 0.005 |  | 9.4649 | 0.047325
642_1 | coal | 176 |  | 642 | Scholz | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 49 | 581.091 | Filterable Particulate | 0.0040071 | lb/MMBtu | ERT |  | 3 | 3 | 2179 |  | 0.0040071 | 0.0040071 |  | 0.0040071 |  | 11.859 | 0.04752 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01
6249_2 | coal | 177 |  | 6249 | Winyah | 2 | W2 | Conventional Boiler | Wall firing - opposed firing | 305 | 2908 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | W2PM2009 | 1 | 1 |  |  |  | 0.005 |  | 0.005 |  | 9.5344 | 0.047672 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-07-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
50879_50879 | coal | 178 |  | 50879 | Wheelabrator Frackville Energy Co. | 50879 | 1 | Fluidized bed firing | Fluidized bed firing | 45 | 590 | Filterable Particulate | 0.0036667 | lb/MMBtu | Part II | StackTest-3 | 3 | 0 |  |  | 0.0036667 | 0.0036667 |  | 0.0036667 |  | 13.1111 | 0.048074
6664_101 | coal | 179 |  | 6664 | Louisa | 101 | 101 | Conventional Boiler | Wall firing - unspecified | 805 | 8624 | Filterable Particulate | 0.004512 | lb/MMBtu | ERT |  | 3 | 3 | 2206 |  | 0.004512 | 0.004512 |  | 0.004512 |  | 10.713 | 0.048337 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-12-01 | PM control | Fabric Filter, pulse | 2007-12-01
113_1 | coal | 180 |  | 113 | Cholla | 1 | 001 | Conventional Boiler | Tangential firing | 131 | 1270 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 17 | 1 | 0 |  |  |  | 0.005 |  | 0.005 |  | 9.6947 | 0.048473
54144_BRBR1 | coal | 181 |  | 54144 | Piney Creek Project | BRBR1 | BRBRI | Fluidized bed firing | Fluidized bed firing | 36 | 450 | Filterable Particulate | 0.0039147 | lb/MMBtu | ERT |  | 3 | 3 | 2088 |  | 0.0039147 | 0.0039147 |  | 0.0039147 |  | 12.5 | 0.048934 | NOx control | Selective Noncatalytic Reduction | 2002-08-01 | PM control | Fabric Filter, pulse | 1992-11-01
643_1 | coal | 182 |  | 643 | Lansing Smith | 1 | Unit 1 | Conventional Boiler | Tangential firing | 172 | 1728.216 | Filterable Particulate | 0.0049442 | lb/MMBtu | Part II | Unit 1 Particulate Steady State Test (8/19/09) | 3 | 0 |  |  | 0.0049442 | 0.0049442 |  | 0.0049442 |  | 10.0478 | 0.049678
6204_2 | coal | 183 |  | 6204 | Laramie River Station | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 602 | 6420 | Filterable Particulate | 0.0046667 | lb/MMBtu | Part II | Unit 2 Particulate 2007 | 3 | 2 |  |  | 0.0046667 | 0.0046667 |  | 0.0046667 |  | 10.6645 | 0.049767
6170_2 | coal | 184 |  | 6170 | Pleasant Prairie | 2 | PPPPB2 | Conventional Boiler | Wall firing - opposed firing | 643 | 6449 | Filterable Particulate | 0.0049645 | lb/MMBtu | Part II | PPPP-PM-U2-1.2009 | 3 | 3 |  |  | 0.0049645 | 0.0049645 |  | 0.0049645 |  | 10.0295 | 0.049792
884_1 | coal | 185 | Retired | 884 | Will County | 1 | WC1CONFIG | Conventional Boiler | Cyclone firing | 167 | 1689.992 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | WillCo1 PM | 3 | 3 |  |  | 0.005 | 0.005 |  | 0.005 |  | 10.1197 | 0.050599
3788_2 | coal | 186 |  | 3788 | Potomac River | 2 | 2 | Conventional Boiler | Tangential firing | 93 | 970 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | C2 PM STK 1206 | 1 | 1 |  |  |  | 0.005 |  | 0.005 |  | 10.4301 | 0.052151
988_4 | coal | 187 |  | 988 | Tanners Creek | 4 | TC-4 | Conventional Boiler | Cyclone firing | 579.7 | 4990 | Filterable Particulate | 0.0060958 | lb/MMBtu | ERT |  | 6 | 6 | 12861 |  | 0.0060958 | 0.0060958 |  | 0.0060958 |  | 8.6079 | 0.052472 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-11-01
1606_1 | coal | 188 |  | 1606 | Mount Tom | 1 | 1 current | Conventional Boiler | Wall firing - front firing | 155 | 1480 | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | Turbosorp - initial compliance test | 1 | 0 |  |  | 0.0055 | 0.0055 |  | 0.0055 |  | 9.5484 | 0.052516 | NOx control | Selective Catalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-09-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-12-01 | PM control | Fabric Filter, pulse | 2009-12-01
642_2 | coal | 189 |  | 642 | Scholz | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 49 | 644.742 | Filterable Particulate | 0.0040071 | lb/MMBtu | ERT |  | 3 | 3 | 2179 |  | 0.0040071 | 0.0040071 |  | 0.0040071 |  | 13.158 | 0.052725 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2007-12-01
1091_3 | coal | 190 |  | 1091 | George Neal North | 3 | 3 | Conventional Boiler | Wall firing - unspecified | 531 | 5021 | Filterable Particulate | 0.0057227 | lb/MMBtu | Part II | 7/15/2008-PM | 1 | 0 |  |  |  | 0.0057227 |  | 0.0057227 |  | 9.4557 | 0.054112
6034_1 | coal | 191 |  | 6034 | Belle River | 1 | BR1-Config | Conventional Boiler | Wall firing - opposed firing | 674 | 6814 | Filterable Particulate | 0.005375 | lb/MMBtu | Part II | PM2009_1 | 8 | 0 |  |  | 0.005375 | 0.005375 |  | 0.005375 |  | 10.1098 | 0.05434
3138_4 | coal | 192 |  | 3138 | New Castle Plant | 4 | NC4-2 | Conventional Boiler | Wall firing - front firing | 114 | 1025 | Filterable Particulate | 0.00607 | lb/MMBtu | Part II | NC-39B | 3 | 3 |  |  | 0.00607 | 0.00607 |  | 0.00607 |  | 8.9912 | 0.054577
1008_4 | coal | 193 |  | 1008 | R. Gallagher | 4 | 4-2008 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | STACKB052908 | 3 | 3 |  |  | 0.0056667 | 0.0056667 |  | 0.0056667 |  | 9.7333 | 0.055156
1008_3 | coal | 194 |  | 1008 | R. Gallagher | 3 | 3-2008 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | STACKB052908 | 3 | 3 |  |  | 0.0056667 | 0.0056667 |  | 0.0056667 |  | 9.7333 | 0.055156
3788_1 | coal | 195 |  | 3788 | Potomac River | 1 | 1 | Conventional Boiler | Tangential firing | 93 | 970 | Filterable Particulate | 0.0053 | lb/MMBtu | Part II | C1 PM SBC60 0508 | 1 | 1 |  |  |  | 0.0053 |  | 0.0053 |  | 10.4301 | 0.05528
2712_4B | coal | 196 |  | 2712 | Roxboro Steam Electric Plant | 4B | Rox_Cfg_4c | Conventional Boiler | Wall firing - opposed firing | 372.5 | 3469 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | Rox_Unit_4_Test_7d | 4 | 4 |  |  | 0.006 | 0.006 |  | 0.006 |  | 9.3128 | 0.055877
2712_4A | coal | 197 |  | 2712 | Roxboro Steam Electric Plant | 4A | Rox_Cfg_4c | Conventional Boiler | Wall firing - opposed firing | 372.5 | 3469 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | Rox_Unit_4_Test_7d | 4 | 4 |  |  | 0.006 | 0.006 |  | 0.006 |  | 9.3128 | 0.055877
6113_1 | coal | 198 |  | 6113 | Gibson | 1 | 1-2007-FGDIN | Conventional Boiler | Wall firing - opposed firing | 661 | 6368 | Filterable Particulate | 0.0058648 | lb/MMBtu | ERT |  | 3 | 3 | 1637 |  | 0.0058648 | 0.0058648 |  | 0.0058648 |  | 9.6339 | 0.0565 | NOx control | Selective Catalytic Reduction | 2005-04-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-01-01 | SO2 control | Wet FGD - Tray Type | 2007-10-01
47_4 | coal | 199 |  | 47 | Colbert | 4 | 4 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | Filterable Particulate | 0.0053333 | lb/MMBtu | Part II | COF4 - 2006 | 3 | 3 |  |  | 0.0053333 | 0.0053333 |  | 0.0053333 |  | 10.605 | 0.05656 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-01-01
47_2 | coal | 200 |  | 47 | Colbert | 2 | 2 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | Filterable Particulate | 0.0053333 | lb/MMBtu | Part II | COF2 - 2008 | 3 | 3 |  |  | 0.0053333 | 0.0053333 |  | 0.0053333 |  | 10.605 | 0.05656
508_4 | coal | 201 |  | 508 | Lamar Plant | 4 | 001 | Fluidized bed firing | Fluidized bed firing | 44 | 180 | Filterable Particulate | 0.0049078 | lb/MMBtu | Part II | 1 | 2 | 0 |  |  | 0.0011447 | 0.0049078 | Corrected | 0.0098157 | Corrected | 11.5864 | 0.056864
1743_4 | coal | 202 |  | 1743 | St Clair Power Plant | 4 | SC4-Config | Conventional Boiler | Wall firing - front firing | 157 | 1692 | Filterable Particulate | 0.0053333 | lb/MMBtu | Part II | PM2007_Sep4 | 3 | 0 |  |  | 0.0053333 | 0.0053333 |  | 0.0053333 |  | 10.7771 | 0.057478
10672_CBA | coal | 203 |  | 10672 | Cedar Bay Generating Company L.P. | CBA | CBA1 | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | CBA2006pm | 3 | 2 |  |  | 0.005 | 0.005 |  | 0.005 |  | 11.5543 | 0.057772 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
1915_Boiler 1 | coal | 204 |  | 1915 | Allen S King | Boiler 1 | Unit 1 | Conventional Boiler | Cyclone firing | 580 | 4730 | Filterable Particulate | 0.0071 | lb/MMBtu | Part II | King PM 05-2009 | 1 | 1 |  |  |  | 0.0071 |  | 0.0071 |  | 8.1552 | 0.057902
130_3 | coal | 205 |  | 130 | Cross | 3 | C3 | Conventional Boiler | Tangential firing | 625 | 6058 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | C3PM2007 | 1 | 1 |  |  |  | 0.006 |  | 0.006 |  | 9.6928 | 0.058157 | NOx control | Selective Catalytic Reduction | 2006-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2006-08-01 | SO2 control | Wet FGD - Spray Type | 2006-08-01
3138_5 | coal | 206 |  | 3138 | New Castle Plant | 5 | NC5-2 | Conventional Boiler | Wall firing - front firing | 143.3 | 1441 | Filterable Particulate | 0.0058 | lb/MMBtu | Part II | NC-48 | 3 | 3 |  |  | 0.0058 | 0.0058 |  | 0.0058 |  | 10.0558 | 0.058324 | NOx control | Selective Noncatalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
2823_B2 | coal | 207 |  | 2823 | Milton R. Young Station | B2 | 2 | Conventional Boiler | Cyclone firing | 477 | 6300 | Filterable Particulate | 0.0044195 | lb/MMBtu | Part II | Sept2005 PM emissions compliance study | 1 | 0 |  |  |  | 0.0044195 |  | 0.0044195 |  | 13.2075 | 0.058371
2324_4 | coal | 208 |  | 2324 | Reid Gardner | 4 | 4 | Conventional Boiler | Wall firing - front firing | 281 | 2956 | Filterable Particulate | 0.0056433 | lb/MMBtu | Part II | U4_2005_COMPLIANCE ALT | 3 | 3 |  |  | 0.0056433 | 0.0056433 |  | 0.0056433 |  | 10.5196 | 0.059365 | PM control | Fabric Filter, pulse | 1983-07-01 | SO2 control | Wet FGD - Venturi Type | 1983-07-01
892_Unit 1 | coal | 209 |  | 892 | Hennepin Power Station | Unit 1 | 001 | Conventional Boiler | Tangential firing | 75 | 776 | Filterable Particulate | 0.0058037 | lb/MMBtu | ERT |  | 3 | 3 | 1884 |  | 0.0058037 | 0.0058037 |  | 0.0058037 |  | 10.3467 | 0.060049 | PM control | Electrostatic precipitator, cold side, unspecified | 1972-08-01 | Other control | Activated carbon injection | 2009-12-01 | PM control | Fabric Filter, unspecified | 2008-10-01
628_4 | coal | 210 |  | 628 | Crystal River Power Plant | 4 | CryR_Cfg_4 | Conventional Boiler | Wall firing - opposed firing | 769 | 7613 | Filterable Particulate | 0.0060667 | lb/MMBtu | Part II | CryR_Blr_4_Test_4 | 3 | 3 |  |  | 0.0060667 | 0.0060667 |  | 0.0060667 |  | 9.8999 | 0.060059
47_3 | coal | 211 |  | 47 | Colbert | 3 | 3 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | COF3 - 2009 | 3 | 3 |  |  | 0.0056667 | 0.0056667 |  | 0.0056667 |  | 10.605 | 0.060095 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-05-01
1241_2 | coal | 212 |  | 1241 | La Cygne | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 685 | 7700 | Filterable Particulate | 0.0053594 | lb/MMBtu | ERT |  | 6 | 6 | 1372 |  | 0.0053594 | 0.0053594 |  | 0.0053594 |  | 11.2409 | 0.060244 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
4143_1 | coal | 213 |  | 4143 | Genoa | 1 | 001 | Conventional Boiler | Tangential firing | 373.5 | 3627.69 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 3 | 3 | 0 |  |  | 0.0063333 | 0.0063333 |  | 0.0063333 |  | 9.7127 | 0.061514
10641_B1 | coal | 214 |  | 10641 | Cambria Cogen | B1 | 001 | Fluidized bed firing | Fluidized bed firing | 49 | 560 | Filterable Particulate | 0.0054023 | lb/MMBtu | ERT |  | 3 | 3 | 2226 |  | 0.0054023 | 0.0054023 |  | 0.0054023 |  | 11.4286 | 0.06174 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
892_Unit 2 | coal | 215 |  | 892 | Hennepin Power Station | Unit 2 | 002 | Conventional Boiler | Tangential firing | 234 | 2500 | Filterable Particulate | 0.0058037 | lb/MMBtu | ERT |  | 3 | 3 | 1884 |  | 0.0058037 | 0.0058037 |  | 0.0058037 |  | 10.6838 | 0.062005 | PM control | Electrostatic precipitator, cold side, unspecified | 1974-06-01 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, unspecified | 2008-12-01
1250_3 | coal | 216 |  | 1250 | Lawrence Energy Center | 3 | 3 | Conventional Boiler | Tangential firing | 58 | 645 | Filterable Particulate | 0.0055865 | lb/MMBtu | ERT |  | 3 | 3 | 1854 |  | 0.0055865 | 0.0055865 |  | 0.0055865 |  | 11.1207 | 0.062126 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
50_7 | coal | 217 |  | 50 | Widows Creek | 7 | 7 | Conventional Boiler | Tangential firing | 575 | 5681 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | WCF7 - 10/30/2008 | 3 | 3 |  |  | 0.0063333 | 0.0063333 |  | 0.0063333 |  | 9.88 | 0.062573
10075_2 | coal | 218 |  | 10075 | Taconite Harbor Energy Center | 2 | THEC2 | Conventional Boiler | Tangential firing | 79.2 | 913 | Filterable Particulate | 0.0054656 | lb/MMBtu | ERT |  | 6 | 6 | 1734 |  | 0.0054656 | 0.0054656 |  | 0.0054656 |  | 11.5278 | 0.063006 | NOx control |  | 2007-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2007-01-01
3118_1 | coal | 219 |  | 3118 | Conemaugh | 1 | CON-1 | Conventional Boiler | Tangential firing | 936 | 8985 | Filterable Particulate | 0.0065667 | lb/MMBtu | Part II | C-190 | 3 | 3 |  |  | 0.0065667 | 0.0065667 |  | 0.0065667 |  | 9.5994 | 0.063036
983_3 | coal | 220 |  | 983 | Clifty Creek | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 215 | 2233.798 | Filterable Particulate | 0.0061 | lb/MMBtu | Part II | Stack1Particulate2007 | 1 | 1 |  |  |  | 0.0061 |  | 0.0061 |  | 10.3898 | 0.063378
4041_6 | coal | 221 |  | 4041 | South Oak Creek | 6 | OCPP-B6 | Conventional Boiler | Wall firing - front firing | 278 | 2516 | Filterable Particulate | 0.0070333 | lb/MMBtu | Part II | OCPP-PM.Hg-B6-6.2005 | 3 | 3 |  |  | 0.0070333 | 0.0070333 |  | 0.0070333 |  | 9.0504 | 0.063654 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-04-01
983_2 | coal | 222 |  | 983 | Clifty Creek | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 215 | 2247.252 | Filterable Particulate | 0.0061 | lb/MMBtu | Part II | Stack1Particulate2007 | 1 | 1 |  |  |  | 0.0061 |  | 0.0061 |  | 10.4523 | 0.063759
3297_WAT1 | coal | 223 |  | 3297 | Wateree | WAT1 | WAT001 | Conventional Boiler | Wall firing - unspecified | 383 | 3329.7 | Filterable Particulate | 0.00734 | lb/MMBtu | Part II | PM-HCL-HF-HG-07/06-WAT1 | 1 | 0 |  |  |  | 0.00734 |  | 0.00734 |  | 8.6937 | 0.063812 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Fabric Filter, unspecified | 2001-05-01 | SO2 control | Wet FGD - Unspecified
6639_G1 | coal | 224 |  | 6639 | R D Green | G1 | 1 | Conventional Boiler | Wall firing - opposed firing | 250 | 2704.2 | Filterable Particulate | 0.0059367 | lb/MMBtu | Part II | G1 compliance test 2008 | 3 | 3 |  |  | 0.0059367 | 0.0059367 |  | 0.0059367 |  | 10.8168 | 0.064216
7343_4 | coal | 225 |  | 7343 | George Neal South | 4 | 4 | Conventional Boiler | Wall firing - unspecified | 682 | 6900 | Filterable Particulate | 0.0064393 | lb/MMBtu | Part II | PM-July 2008 | 1 | 0 |  |  |  | 0.0064393 |  | 0.0064393 |  | 10.1173 | 0.065148
983_1 | coal | 226 |  | 983 | Clifty Creek | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 215 | 2305.842 | Filterable Particulate | 0.0061 | lb/MMBtu | Part II | Stack1Particulate2007 | 1 | 1 |  |  |  | 0.0061 |  | 0.0061 |  | 10.7248 | 0.065422
4041_5 | coal | 227 |  | 4041 | South Oak Creek | 5 | OCPP-B5 | Conventional Boiler | Wall firing - front firing | 273 | 2488 | Filterable Particulate | 0.0072 | lb/MMBtu | Part II | OCPP-PM-B5-3.2007 | 3 | 3 |  |  | 0.0072 | 0.0072 |  | 0.0072 |  | 9.1136 | 0.065618 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-03-01
4042_1 | coal | 228 |  | 4042 | Valley | 1 | VAPP-B1 | Conventional Boiler | Wall firing - front firing | 72 | 868 | Filterable Particulate | 0.005443 | lb/MMBtu | ERT |  | 6 | 6 | 1244 |  | 0.005443 | 0.005443 |  | 0.005443 |  | 12.0556 | 0.065618 | PM control | Fabric Filter, pulse | 1994-06-01
3788_5 | coal | 229 |  | 3788 | Potomac River | 5 | 5 | Conventional Boiler | Tangential firing | 108 | 961 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | C5 PM 0908 | 1 | 1 |  |  | 0.0074 | 0.0074 |  | 0.0074 |  | 8.8981 | 0.065846
4042_2 | coal | 230 |  | 4042 | Valley | 2 | VAPP-B2 | Conventional Boiler | Wall firing - front firing | 72 | 868 | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | VAPP-PM-B1B2-8.2005 | 3 | 3 |  |  | 0.0055 | 0.0055 |  | 0.0055 |  | 12.0556 | 0.066306 | PM control | Fabric Filter, pulse | 1994-06-01
4042_2 | coal | 231 |  | 4042 | Valley | 2 | VAPP-B2 | Conventional Boiler | Wall firing - front firing | 72 | 868 | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | VAPP-PM-B1B2B3B4-8.2005 | 3 | 3 |  |  | 0.0055 | 0.0055 |  | 0.0055 |  | 12.0556 | 0.066306 | PM control | Fabric Filter, pulse | 1994-06-01
1378_3 | coal | 232 |  | 1378 | Paradise | 3 | 3 | Conventional Boiler | Cyclone firing | 1150.2 | 11457 | Filterable Particulate | 0.0066667 | lb/MMBtu | Part II | PAF3 - 2007 | 3 | 3 |  |  | 0.0066667 | 0.0066667 |  | 0.0066667 |  | 9.9609 | 0.066406
3947_3 | coal | 233 |  | 3947 | Kammer | 3 | K-3 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | July2009PM | 1 | 0 |  |  |  | 0.0074 |  | 0.0074 |  | 9.0779 | 0.067176
3947_2 | coal | 234 |  | 3947 | Kammer | 2 | K-2 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | July2009PM | 1 | 0 |  |  |  | 0.0074 |  | 0.0074 |  | 9.0779 | 0.067176
3947_1 | coal | 235 |  | 3947 | Kammer | 1 | K-1 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | July2009PM | 1 | 0 |  |  |  | 0.0074 |  | 0.0074 |  | 9.0779 | 0.067176
1379_5 | coal | 236 |  | 1379 | Shawnee | 5 | 5 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | SHF1-5 - 2007 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 9.6629 | 0.06764
1379_4 | coal | 237 |  | 1379 | Shawnee | 4 | 4 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | SHF1-5 - 2007 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 9.6629 | 0.06764
1379_3 | coal | 238 |  | 1379 | Shawnee | 3 | 3 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | SHF1-5 - 2007 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 9.6629 | 0.06764
1379_2 | coal | 239 |  | 1379 | Shawnee | 2 | 2 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | SHF1-5 - 2007 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 9.6629 | 0.06764
1379_1 | coal | 240 |  | 1379 | Shawnee | 1 | 1 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | SHF1-5 - 2007 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 9.6629 | 0.06764
3131_1 | coal | 241 |  | 3131 | Shawville | 1 | SHAW1-2 | Conventional Boiler | Wall firing - front firing | 125 | 1349 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | SH-185B | 3 | 3 |  |  | 0.0063333 | 0.0063333 |  | 0.0063333 |  | 10.792 | 0.068349
10641_B2 | coal | 242 |  | 10641 | Cambria Cogen | B2 | 002 | Fluidized bed firing | Fluidized bed firing | 49 | 560 | Filterable Particulate | 0.0059818 | lb/MMBtu | ERT |  | 3 | 3 | 22261 |  | 0.0059818 | 0.0059818 |  | 0.0059818 |  | 11.4286 | 0.068363 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
4054_2 | coal | 243 |  | 4054 | Nelson Dewey | 2 | Unit 2 | Conventional Boiler | Cyclone firing | 117.1 | 1161 | Filterable Particulate | 0.0069 | lb/MMBtu | Part II | ND2-PM-20091013 | 1 | 1 |  |  |  | 0.0069 |  | 0.0069 |  | 9.9146 | 0.068411
3407_4 | coal | 244 |  | 3407 | Kingston | 4 | 4 | Conventional Boiler | Tangential firing | 175 | 1641 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | KIF1-5 - 2005 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 9.3771 | 0.068766
3407_3 | coal | 245 |  | 3407 | Kingston | 3 | 3 | Conventional Boiler | Tangential firing | 175 | 1641 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | KIF1-5 - 2005 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 9.3771 | 0.068766
3407_2 | coal | 246 |  | 3407 | Kingston | 2 | 2 | Conventional Boiler | Tangential firing | 175 | 1641 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | KIF1-5 - 2005 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 9.3771 | 0.068766
3407_1 | coal | 247 |  | 3407 | Kingston | 1 | 1 | Conventional Boiler | Tangential firing | 175 | 1641 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | KIF1-5 - 2005 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 9.3771 | 0.068766
50_2 | coal | 248 |  | 50 | Widows Creek | 2 | 2 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | WCF2 - 2007 | 3 | 3 |  |  | 0.0063333 | 0.0063333 |  | 0.0063333 |  | 10.8677 | 0.068829
2790_B2 | coal | 249 |  | 2790 | R.M. Heskett Station | B2 | B2 | Fluidized bed firing | Fluidized bed firing | 78 | 900 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 7 | 1 | 0 |  |  |  | 0.006 |  | 0.006 |  | 11.5385 | 0.069231
8224_2 | coal | 250 |  | 8224 | North Valmy | 2 | 2 | Conventional Boiler | Wall firing - front firing | 270.2 | 2881 | Filterable Particulate | 0.0065 | lb/MMBtu | Part II | U2_2008_COMPLIANCE | 3 | 3 |  |  | 0.0065 | 0.0065 |  | 0.0065 |  | 10.6625 | 0.069306 | SO2 control | Dry FGD - Spray Dryer | 1985-05-01 | PM control | Fabric Filter, reverse air | 1985-05-01
6249_4 | coal | 251 |  | 6249 | Winyah | 4 | W4 | Conventional Boiler | Wall firing - opposed firing | 305 | 3051 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | W4PM2009 | 1 | 1 |  |  |  | 0.007 |  | 0.007 |  | 10.0033 | 0.070023 | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1981-11-01 | SO2 control | Wet FGD - Spray Type | 1981-11-01
10_2 | coal | 252 |  | 10 | Greene County | 2 | Unit 2 | Conventional Boiler | Wall firing - opposed firing | 260 | 2392.821 | Filterable Particulate | 0.0077 | lb/MMBtu | Part II | Unit 2 PM Emissions Test (May 15, 2007) | 3 | 0 |  |  | 0.0077 | 0.0077 |  | 0.0077 |  | 9.2032 | 0.070864
6177_U2B | coal | 253 |  | 6177 | Coronado Generating Station | U2B | U2B | Conventional Boiler | Wall firing - unspecified | 456.6 | 4719 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 7 | 1 | 0 |  |  |  | 0.007 |  | 0.007 |  | 10.3351 | 0.072346
6009_2 | coal | 254 |  | 6009 | White Bluff | 2 | 002 | Conventional Boiler | Tangential firing | 881 | 8700 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 2 | 3 | 0 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 9.8751 | 0.072418
1832_EU001 | coal | 255 |  | 1832 | Erickson Station | EU001 | 001 | Conventional Boiler | Wall firing - front firing | 165 | 1668 | Filterable Particulate | 0.0071836 | lb/MMBtu | ERT |  | 6 | 6 | 942 |  | 0.0071618 | 0.0071836 | corrected | 0.0072272 | corrected | 10.1091 | 0.07262 | PM control | Electrostatic precipitator, unspecified | 1998-01-01
1381_C3 | coal | 256 |  | 1381 | Kenneth C Coleman | C3 | 4 | Conventional Boiler | Wall firing - front firing | 157.6 | 1623 | Filterable Particulate | 0.00693 | lb/MMBtu | Part II | Coleman compliance test 2009 | 3 | 3 |  |  | 0.00693 | 0.00693 |  | 0.00693 |  | 10.4887 | 0.072687
1381_C2 | coal | 257 |  | 1381 | Kenneth C Coleman | C2 | 4 | Conventional Boiler | Wall firing - front firing | 157.6 | 1623 | Filterable Particulate | 0.00693 | lb/MMBtu | Part II | Coleman compliance test 2009 | 3 | 3 |  |  | 0.00693 | 0.00693 |  | 0.00693 |  | 10.4887 | 0.072687
1381_C1 | coal | 258 |  | 1381 | Kenneth C Coleman | C1 | 4 | Conventional Boiler | Wall firing - front firing | 157.6 | 1623 | Filterable Particulate | 0.00693 | lb/MMBtu | Part II | Coleman compliance test 2009 | 3 | 3 |  |  | 0.00693 | 0.00693 |  | 0.00693 |  | 10.4887 | 0.072687
47_5 | coal | 259 |  | 47 | Colbert | 5 | 5 | Conventional Boiler | Wall firing - opposed firing | 550 | 5547 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | COF5 - 2009 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 10.0855 | 0.07396
6096_NC2 | coal | 260 |  | 6096 | Nebraska City | NC2 | NC2 | Conventional Boiler | Wall firing - front firing | 682 | 6920.254 | Filterable Particulate | 0.0073 | lb/MMBtu | Part II | PM NC Unit 2 | 1 | 0 |  |  |  | 0.0073 |  | 0.0073 |  | 10.147 | 0.074073 | NOx control | Selective Catalytic Reduction | 2009-05-01 | Other control | Activated carbon injection | 2009-05-01 | SO2 control | Dry FGD - Spray Dryer | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01
3130_2 | coal | 261 |  | 3130 | Seward | 2 | SEW-1 | Fluidized bed firing | Fluidized bed firing | 292.5 | 3100 | Filterable Particulate | 0.0070333 | lb/MMBtu | Part II | SE-116 | 3 | 3 |  |  | 0.0070333 | 0.0070333 |  | 0.0070333 |  | 10.5983 | 0.074541 | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Fabric Filter, pulse | 2004-03-01
3130_1 | coal | 262 |  | 3130 | Seward | 1 | SEW-1 | Fluidized bed firing | Fluidized bed firing | 292.5 | 3100 | Filterable Particulate | 0.0070333 | lb/MMBtu | Part II | SE-116 | 3 | 3 |  |  | 0.0070333 | 0.0070333 |  | 0.0070333 |  | 10.5983 | 0.074541 | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Fabric Filter, pulse | 2004-03-01
1008_2 | coal | 263 |  | 1008 | R. Gallagher | 2 | 2-2007 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | STACKA052808 | 3 | 3 |  |  | 0.0076667 | 0.0076667 |  | 0.0076667 |  | 9.7333 | 0.074622 | PM control | Fabric Filter, shake and deflate | 2007-12-01
1008_1 | coal | 264 |  | 1008 | R. Gallagher | 1 | 1-2007 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | STACKA052808 | 3 | 3 |  |  | 0.0076667 | 0.0076667 |  | 0.0076667 |  | 9.7333 | 0.074622
3788_4 | coal | 265 |  | 3788 | Potomac River | 4 | 4 | Conventional Boiler | Tangential firing | 108 | 961 | Filterable Particulate | 0.0084 | lb/MMBtu | Part II | C4 PM 0108 | 1 | 1 |  |  | 0.0084 | 0.0084 |  | 0.0084 |  | 8.8981 | 0.074744
3407_5 | coal | 266 |  | 3407 | Kingston | 5 | 5 | Conventional Boiler | Tangential firing | 200 | 2056 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | KIF1-5 - 2005 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 10.28 | 0.075387
6204_3 | coal | 267 |  | 6204 | Laramie River Station | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 610 | 6600 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | Unit 3 Particulate 2005 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 10.8197 | 0.075738
3399_1 | coal | 268 |  | 3399 | Cumberland | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1300 | 14130 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | CUF1 - 2007 | 3 | 3 |  |  | 0.007 | 0.007 |  | 0.007 |  | 10.8692 | 0.076085
130_4 | coal | 269 |  | 130 | Cross | 4 | C4 | Conventional Boiler | Tangential firing | 625 | 6798 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | C4PM2008 | 1 | 1 |  |  |  | 0.007 |  | 0.007 |  | 10.8768 | 0.076138 | NOx control | Selective Catalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2008-05-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
113_2 | coal | 270 |  | 113 | Cholla | 2 | 002 | Conventional Boiler | Tangential firing | 305 | 2938 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 3 | 1 | 0 |  |  |  | 0.008 |  | 0.008 |  | 9.6328 | 0.077062
6034_2 | coal | 271 |  | 6034 | Belle River | 2 | BR2-Config | Conventional Boiler | Wall firing - opposed firing | 677.1 | 6814 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | PM2007_Aug_2 | 3 | 0 |  |  | 0.0076667 | 0.0076667 |  | 0.0076667 |  | 10.0635 | 0.077154
3_4 | coal | 272 |  | 3 | Barry | 4 | Unit 4 | Conventional Boiler | Tangential firing | 376 | 3512.6521 | Filterable Particulate | 0.0083 | lb/MMBtu | Part II | Unit 4 PM Emissions Test (June 3, 2009) | 3 | 0 |  |  | 0.0083 | 0.0083 |  | 0.0083 |  | 9.3422 | 0.07754
10343_SG-101 | coal | 273 |  | 10343 | Foster Wheeler Mt Carmel Cogen | SG-101 | SG-101 | Fluidized bed firing | Fluidized bed firing | 43 | 505 | Filterable Particulate | 0.0066667 | lb/MMBtu | Part II | PM 2007 | 3 | 3 |  |  | 0.0066667 | 0.0066667 |  | 0.0066667 |  | 11.7442 | 0.078295 | PM control | Fabric Filter, reverse air | 1990-01-01
6021_C3 | coal | 274 |  | 6021 | Craig | C3 | C3 | Conventional Boiler | Wall firing - opposed firing | 478 | 4124 | Filterable Particulate | 0.0091333 | lb/MMBtu | Part II | C3 2009 PM test | 3 | 3 |  |  | 0.0091333 | 0.0091333 |  | 0.0091333 |  | 8.6276 | 0.078799
6002_1 | coal | 275 |  | 6002 | James H. Miller Jr. | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 725 | 7015.9856 | Filterable Particulate | 0.0081507 | lb/MMBtu | Part II | Unit 1 PM Emissions Test (April 16, 2008) | 3 | 0 |  |  | 0.0081507 | 0.0081507 |  | 0.0081507 |  | 9.6772 | 0.078876
55749_PC1 | coal | 276 |  | 55749 | Hardin Generator Project | PC1 | PC1 | Conventional Boiler | Wall firing - unspecified | 119 | 1304 | Filterable Particulate | 0.0072 | lb/MMBtu | Part II | 1 | 1 | 0 |  |  |  | 0.0072 |  | 0.0072 |  | 10.958 | 0.078897 | NOx control | Selective Catalytic Reduction | 2006-04-01 | Other control | Activated carbon injection |  | SO2 control | Dry FGD - Spray Dryer | 2006-04-01 | PM control | Fabric Filter, pulse | 2006-04-01
3942_2 | coal | 277 |  | 3942 | Albright Power Station | 2 | Unit_2 | Conventional Boiler | Wall firing - unspecified | 81 | 643 | Filterable Particulate | 0.0099574 | lb/MMBtu | ERT |  | 3 | 3 | 1113 |  | 0.0099574 | 0.0099574 |  | 0.0099574 |  | 7.9383 | 0.079045 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
50_3 | coal | 278 |  | 50 | Widows Creek | 3 | 3 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | WCF3 - 2006 | 3 | 3 |  |  | 0.0073333 | 0.0073333 |  | 0.0073333 |  | 10.8677 | 0.079697
3118_2 | coal | 279 |  | 3118 | Conemaugh | 2 | CON-2 | Conventional Boiler | Tangential firing | 936 | 8985 | Filterable Particulate | 0.008362 | lb/MMBtu | Part II | C-193 | 3 | 3 |  |  | 0.0080667 | 0.008362 | Corrected | 0.0086574 | Corrected | 9.5994 | 0.08027
6017_2 | coal | 280 |  | 6017 | Newton | 2 | 002 | Conventional Boiler | Tangential firing | 620 | 5500 | Filterable Particulate | 0.0091158 | lb/MMBtu | ERT |  | 3 | 3 | 1902 |  | 0.0091158 | 0.0091158 |  | 0.0091158 |  | 8.871 | 0.080866 | Other control | Other (specify): Flue gas conditioning | 2001-04-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning
10_1 | coal | 281 |  | 10 | Greene County | 1 | Unit 1 | Conventional Boiler | Wall firing - opposed firing | 272 | 2452.624 | Filterable Particulate | 0.0090448 | lb/MMBtu | Part II | Units 1 and 2 PM Emissions Test (June 11, 2008) | 3 | 0 |  |  | 0.0090448 | 0.0090448 |  | 0.0090448 |  | 9.017 | 0.081557
6073_1 | coal | 282 |  | 6073 | Victor J. Daniel Jr | 1 | Unit 1 | Conventional Boiler | Tangential firing | 537 | 5206.306 | Filterable Particulate | 0.0085 | lb/MMBtu | Part II | Unit 1 PM Test Report May 19, 2009 | 1 | 1 |  |  |  | 0.0085 |  | 0.0085 |  | 9.6952 | 0.082409
6177_U1B | coal | 283 |  | 6177 | Coronado Generating Station | U1B | U1B | Conventional Boiler | Wall firing - unspecified | 456.6 | 4719 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 3 | 1 | 0 |  |  |  | 0.008 |  | 0.008 |  | 10.3351 | 0.082681
1743_1 | coal | 284 |  | 1743 | St Clair Power Plant | 1 | SC1-Config | Conventional Boiler | Wall firing - front firing | 161 | 1753 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | PM2007_Sep1 | 3 | 0 |  |  | 0.0076667 | 0.0076667 |  | 0.0076667 |  | 10.8882 | 0.083476
6018_2 | coal | 285 |  | 6018 | East Bend Station | 2 | 2 | Conventional Boiler | Wall firing - front firing | 650.7246 | 6313 | Filterable Particulate | 0.0087203 | lb/MMBtu | ERT |  | 3 | 3 | 2055 |  | 0.0087203 | 0.0087203 |  | 0.0087203 |  | 9.7015 | 0.0846 | Other control | Dry sorbent injection | 2005-01-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1981-01-01 | NOx control | Selective Catalytic Reduction | 2002-01-01 | SO2 control | Wet FGD - Spray Type | 1981-01-01
6073_2 | coal | 286 |  | 6073 | Victor J. Daniel Jr | 2 | Unit 2 | Conventional Boiler | Tangential firing | 536 | 5166.728 | Filterable Particulate | 0.0088 | lb/MMBtu | Part II | Unit 2 PMTest Report ‐ June 5, 2009 | 1 | 1 |  |  |  | 0.0088 |  | 0.0088 |  | 9.6394 | 0.084827
2549_67 | coal | 287 |  | 2549 | CR Huntley Generating Station | 67 | 067 | Conventional Boiler | Tangential firing | 204 | 1836 | Filterable Particulate | 0.0094333 | lb/MMBtu | Part II | Stack-PM-0609 | 3 | 0 |  |  | 0.0094333 | 0.0094333 |  | 0.0094333 |  | 9 | 0.0849
2378_2 | coal | 288 |  | 2378 | BL England | 2 | 2 Coal w or w/o TDF | Conventional Boiler | Cyclone firing | 167.3 | 1600 | Filterable Particulate | 0.0089098 | lb/MMBtu | Part II | CAM 238-015 | 3 | 3 |  |  | 0.0089098 | 0.0089098 |  | 0.0089098 |  | 9.5637 | 0.08521 | NOx control | Selective Noncatalytic Reduction | 1998-06-01 | Other control | Activated carbon injection | 2007-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
6113_4 | coal | 289 |  | 6113 | Gibson | 4 | 4 | Conventional Boiler | Wall firing - opposed firing | 661 | 6265 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | UNIT4(10/7/09) | 3 | 0 |  |  | 0.009 | 0.009 |  | 0.009 |  | 9.4781 | 0.085303 | NOx control | Selective Catalytic Reduction | 2003-04-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01 | SO2 control | Wet FGD - Tray Type | 1994-12-01
2850_B002 | coal | 290 |  | 2850 | J M Stuart | B002 | MS2W | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | Filterable Particulate | 0.0092333 | lb/MMBtu | Part II | U2PM2009 | 3 | 3 |  |  | 0.0092333 | 0.0092333 |  | 0.0092333 |  | 9.3098 | 0.08596
525_2 | coal | 291 |  | 525 | Hayden | 2 | Unit 2 | Conventional Boiler | Tangential firing | 285 | 2712 | Filterable Particulate | 0.0090426 | lb/MMBtu | ERT |  | 4 | 4 | 565 |  | 0.0090426 | 0.0090426 |  | 0.0090426 |  | 9.5158 | 0.086047 | SO2 control | Dry FGD - Spray Dryer | 1999-06-01 | PM control | Fabric Filter, reverse air | 1999-06-01
2549_68 | coal | 292 |  | 2549 | CR Huntley Generating Station | 68 | 068 | Conventional Boiler | Tangential firing | 201 | 1836 | Filterable Particulate | 0.0094333 | lb/MMBtu | Part II | Stack-PM-0609 | 3 | 0 |  |  | 0.0094333 | 0.0094333 |  | 0.0094333 |  | 9.1343 | 0.086167
6139_1 | coal | 293 |  | 6139 | Welsh | 1 | WE-1 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | Filterable Particulate | 0.0093454 | lb/MMBtu | ERT |  | 6 | 6 | 10040004 |  | 0.0093454 | 0.0093454 |  | 0.0093454 |  | 9.2401 | 0.086353 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-03-01
6085_14 | coal | 294 |  | 6085 | R.M. Schahfer | 14 | R.M.0014 | Conventional Boiler | Cyclone firing | 468 | 4650 | Filterable Particulate | 0.008887 | lb/MMBtu | Part II | RMSG U#14 M5 09/15/2009 | 1 | 1 |  |  |  | 0.008887 |  | 0.008887 |  | 9.9359 | 0.0883 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-06-01
3297_WAT2 | coal | 295 |  | 3297 | Wateree | WAT2 | WAT002 | Conventional Boiler | Wall firing - unspecified | 380 | 3305.1 | Filterable Particulate | 0.0102 | lb/MMBtu | Part II | PM-0506-WAT2 | 1 | 0 |  |  |  | 0.0102 |  | 0.0102 |  | 8.6976 | 0.088716 | NOx control | Selective Catalytic Reduction | 2004-04-01 | PM control | Fabric Filter, unspecified | 2001-07-01 | SO2 control | Wet FGD - Unspecified
1001_2 | coal | 296 |  | 1001 | Cayuga | 2 | 2-2008-FGDIN | Conventional Boiler | Tangential firing | 525 | 5040 | Filterable Particulate | 0.00925 | lb/MMBtu | Part II | UNIT2(9/1/09) | 4 | 0 |  |  | 0.00925 | 0.00925 |  | 0.00925 |  | 9.6 | 0.0888
1740_2 | coal | 297 |  | 1740 | River Rouge Power Plant | 2 | RR2-Config | Conventional Boiler | Tangential firing | 269 | 2317 | Filterable Particulate | 0.010333 | lb/MMBtu | Part II | 2009Mar | 3 | 0 |  |  | 0.010333 | 0.010333 |  | 0.010333 |  | 8.6134 | 0.089005
7790_1-1 | coal | 298 |  | 7790 | Bonanza Power Plant | 1-1 | 1-1 | Conventional Boiler | Wall firing - opposed firing | 483 | 4899 | Filterable Particulate | 0.0088 | lb/MMBtu | Part II | Total particulate 2005 | 3 | 3 |  |  | 0.0088 | 0.0088 |  | 0.0088 |  | 10.1429 | 0.089257
1745_9A | coal | 299 |  | 1745 | Trenton Channel Power Plant | 9A | TC9A-Config | Conventional Boiler | Tangential firing | 540 | 4045 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | PM2008_Jun9c | 1 | 0 |  |  | 0.012 | 0.012 |  | 0.012 |  | 7.4907 | 0.089889
2094_3 | coal | 300 |  | 2094 | Sibley | 3 | 3 | Conventional Boiler | Cyclone firing | 419 | 4094.1 | Filterable Particulate | 0.0091995 | lb/MMBtu | ERT |  | 3 | 3 | 894 |  | 0.0091995 | 0.0091995 |  | 0.0091995 |  | 9.7711 | 0.089889 | NOx control | Selective Catalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-04-01
991_6 | coal | 301 |  | 991 | Eagle Valley | 6 | 6 | Conventional Boiler | Tangential firing | 105 | 1017 | Filterable Particulate | 0.0094993 | lb/MMBtu | ERT |  | 6 | 6 | 1178 |  | 0.0094993 | 0.0094993 |  | 0.0094993 |  | 9.6857 | 0.092008 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-12-01
6082_1 | coal | 302 |  | 6082 | AES Somerset LLC | 1 | 001 | Conventional Boiler | Wall firing - opposed firing | 680.8 | 6280 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | PM2_Aug_2006 | 1 | 0 |  |  |  | 0.01 |  | 0.01 |  | 9.2244 | 0.092244 | NOx control | Selective Catalytic Reduction | 1999-01-01 | Other control | Dry sorbent injection |  | PM control | Electrostatic precipitator, unspecified | 1984-01-01 | SO2 control | Wet FGD - Spray Type | 1984-01-01
10672_CBC | coal | 303 |  | 10672 | Cedar Bay Generating Company L.P. | CBC | CBC1 | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | CBC2005pm | 3 | 3 |  |  | 0.008 | 0.008 |  | 0.008 |  | 11.5543 | 0.092435 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
3948_2 | coal | 304 |  | 3948 | Mitchell | 2 | MI-2 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | Filterable Particulate | 0.0108 | lb/MMBtu | Part II | April2009PM2 | 1 | 0 |  |  |  | 0.0108 |  | 0.0108 |  | 8.5998 | 0.092878
8042_Unit 1 | coal | 305 |  | 8042 | Belews Creek Steam Station | Unit 1 | 1-2008 | Conventional Boiler | Wall firing - opposed firing | 1185.8 | 10800 | Filterable Particulate | 0.0103 | lb/MMBtu | Part II | UNIT1(2/10/09) | 3 | 0 |  |  | 0.0103 | 0.0103 |  | 0.0103 |  | 9.1078 | 0.09381
3776_6 | coal | 306 |  | 3776 | Glen Lyn | 6 | GL-6 | Conventional Boiler | Wall firing - front firing | 237.5 | 2040 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | Sept2007 | 1 | 0 |  |  |  | 0.011 |  | 0.011 |  | 8.5895 | 0.094484
2824_10 | coal | 307 |  | 2824 | Stanton | 10 | u10 | Conventional Boiler | Tangential firing | 60 | 642 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | Particulate test | 1 | 1 |  |  |  | 0.009 |  | 0.009 |  | 10.7 | 0.0963 | SO2 control | Dry FGD - Spray Dryer | 2000-01-01 | PM control | Fabric Filter, reverse air | 2000-01-01
8222_B1 | coal | 308 |  | 8222 | Coyote | B1 | 001 | Conventional Boiler | Cyclone firing | 448 | 5214 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | Particulate Emissions Test | 3 | 3 |  |  | 0.0083333 | 0.0083333 |  | 0.0083333 |  | 11.6384 | 0.096987
3161_2 | coal | 309 |  | 3161 | Eddystone Generating Station | 2 | Unit 2 | Conventional Boiler | Tangential firing | 339 | 2808 | Filterable Particulate | 0.011767 | lb/MMBtu | Part II | Particulate Emissions Test - Unit 2 | 3 | 3 |  |  | 0.011767 | 0.011767 |  | 0.011767 |  | 8.2832 | 0.097465 | NOx control | Selective Noncatalytic Reduction | 2003-06-01 | PM control | Multiple cyclone | 1960-11-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1960-11-01 | PM control | PM scrubber - Venturi | 1982-12-01 | SO2 control | Wet FGD - Spray Type | 1982-12-01
3936_2 | coal | 310 |  | 3936 | Kanawha River | 2 | KR-2 | Conventional Boiler | Vertical firing | 219.6 | 1950 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | March2009PM | 1 | 0 |  |  |  | 0.011 |  | 0.011 |  | 8.8798 | 0.097678
3936_1 | coal | 311 |  | 3936 | Kanawha River | 1 | KR-1 | Conventional Boiler | Vertical firing | 219.6 | 1950 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | March2009PM | 1 | 0 |  |  |  | 0.011 |  | 0.011 |  | 8.8798 | 0.097678
50_1 | coal | 312 |  | 50 | Widows Creek | 1 | 1 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | WCF1 - 2006 | 3 | 3 |  |  | 0.009 | 0.009 |  | 0.009 |  | 10.8677 | 0.097809
50776_BLR2 | coal | 313 |  | 50776 | PANTHER CREEK ENERGY FACILITY | BLR2 | BG2 | Fluidized bed firing | Fluidized bed firing | 46.5 | 600 | Filterable Particulate | 0.0077674 | lb/MMBtu | ERT |  | 6 | 6 | 2090 |  | 0.0077674 | 0.0077674 |  | 0.0077674 |  | 12.9032 | 0.10022 | NOx control | Selective Noncatalytic Reduction | 1992-10-01 | PM control | Fabric Filter, pulse | 1992-10-01
50776_BLR1 | coal | 314 |  | 50776 | PANTHER CREEK ENERGY FACILITY | BLR1 | BG1 | Fluidized bed firing | Fluidized bed firing | 46.5 | 600 | Filterable Particulate | 0.0077674 | lb/MMBtu | ERT |  | 6 | 6 | 2090 |  | 0.0077674 | 0.0077674 |  | 0.0077674 |  | 12.9032 | 0.10022 | NOx control | Selective Noncatalytic Reduction | 1992-10-01 | PM control | Fabric Filter, pulse | 1992-10-01
6264_1 | coal | 315 |  | 6264 | Mountaineer | 1 | Mt-1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11960 | Filterable Particulate | 0.0111 | lb/MMBtu | Part II | July2009PM | 1 | 0 |  |  |  | 0.0111 |  | 0.0111 |  | 9.0606 | 0.10057
50835_1 | coal | 316 |  | 50835 | TES Filer City Station | 1 | TES1-Conf | Conventional Boiler | Stoker - spreader | 32.2 | 408 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 2007-Unit 1 PM | 2 | 2 |  |  | 0.008 | 0.008 |  | 0.008 |  | 12.6708 | 0.10137
4054_1 | coal | 317 |  | 4054 | Nelson Dewey | 1 | Unit 1 | Conventional Boiler | Cyclone firing | 120 | 1222 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | ND1-PM-20090929 | 1 | 1 |  |  |  | 0.01 |  | 0.01 |  | 10.1833 | 0.10183
2094_1 | coal | 318 |  | 2094 | Sibley | 1 | 1 | Conventional Boiler | Cyclone firing | 55 | 609.6 | Filterable Particulate | 0.0091995 | lb/MMBtu | ERT |  | 3 | 3 | 894 |  | 0.0091995 | 0.0091995 |  | 0.0091995 |  | 11.0836 | 0.10196 | NOx control | Selective Noncatalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-01-01
1893_1 | coal | 319 |  | 1893 | Boswell Energy Center | 1 | BEC1 | Conventional Boiler | Wall firing - front firing | 73 | 750 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 1,2-Jul2009-PM | 2 | 0 |  |  | 0.01 | 0.01 |  | 0.01 |  | 10.274 | 0.10274
1893_2 | coal | 320 |  | 1893 | Boswell Energy Center | 2 | BEC2 | Conventional Boiler | Wall firing - front firing | 72 | 750 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 1,2,3,4-May2007-PM | 1 | 0 |  |  |  | 0.01 |  | 0.01 |  | 10.4167 | 0.10417 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified | 1977-01-01
1893_2 | coal | 321 |  | 1893 | Boswell Energy Center | 2 | BEC2 | Conventional Boiler | Wall firing - front firing | 72 | 750 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 1,2-Jul2009-PM | 2 | 0 |  |  | 0.01 | 0.01 |  | 0.01 |  | 10.4167 | 0.10417 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified | 1977-01-01
988_3 | coal | 322 |  | 988 | Tanners Creek | 3 | TC-3 | Conventional Boiler | Vertical firing | 215.4 | 1844 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | Aug2009PM | 1 | 0 |  |  |  | 0.0122 |  | 0.0122 |  | 8.5608 | 0.10444
6009_1 | coal | 323 |  | 6009 | White Bluff | 1 | 001 | Conventional Boiler | Tangential firing | 853 | 8700 | Filterable Particulate | 0.010333 | lb/MMBtu | Part II | 1 | 3 | 0 |  |  | 0.010333 | 0.010333 |  | 0.010333 |  | 10.1993 | 0.10539
2324_3 | coal | 324 |  | 2324 | Reid Gardner | 3 | 3 | Conventional Boiler | Wall firing - front firing | 111 | 1237 | Filterable Particulate | 0.0095933 | lb/MMBtu | Part II | U3_2009_COMPLIANCE | 3 | 3 |  |  | 0.0095933 | 0.0095933 |  | 0.0095933 |  | 11.1441 | 0.10691
2104_4 | coal | 325 |  | 2104 | Meramec | 4 | 004 | Conventional Boiler | Wall firing - unspecified | 362 | 3782 | Filterable Particulate | 0.0103 | lb/MMBtu | Part II | 4 | 1 | 0 |  |  |  | 0.0103 |  | 0.0103 |  | 10.4475 | 0.10761
50835_2 | coal | 326 |  | 50835 | TES Filer City Station | 2 | TES2-Conf | Conventional Boiler | Stoker - spreader | 32.2 | 408 | Filterable Particulate | 0.0085 | lb/MMBtu | Part II | 2007 -Unit 2 PM | 2 | 1 |  |  | 0.0085 | 0.0085 |  | 0.0085 |  | 12.6708 | 0.1077
2872_5 | coal | 327 |  | 2872 | Muskingum River | 5 | MR-5 | Conventional Boiler | Cyclone firing | 615.2 | 5550 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | Mar2006PM | 1 | 0 |  |  |  | 0.012 |  | 0.012 |  | 9.0215 | 0.10826
10678_BLR1 | coal | 328 |  | 10678 | AES Warrior Run Cogeneration Facility | BLR1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 202 | 2047 | Filterable Particulate | 0.010695 | lb/MMBtu | ERT |  | 6 | 6 | 1539 |  | 0.010695 | 0.010695 |  | 0.010695 |  | 10.1337 | 0.10838 | NOx control | Selective Noncatalytic Reduction | 2000-02-01 | PM control | Fabric Filter, pulse | 2000-02-01
8102_1 | coal | 329 |  | 8102 | General James M. Gavin | 1 | GA-1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11936 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | Feb2009PM | 1 | 0 |  |  |  | 0.012 |  | 0.012 |  | 9.0424 | 0.10851
3161_1 | coal | 330 | Retired | 3161 | Eddystone Generating Station | 1 | Unit 1 | Conventional Boiler | Tangential firing | 314 | 2637 | Filterable Particulate | 0.012933 | lb/MMBtu | Part II | Particulate Emissions Test - Unit 1 | 3 | 3 |  |  | 0.012933 | 0.012933 |  | 0.012933 |  | 8.3981 | 0.10862
3938_51 | coal | 331 |  | 3938 | Philip Sporn | 51 | SP-5 | Conventional Boiler | Wall firing - opposed firing | 495.5 | 3961 | Filterable Particulate | 0.0136 | lb/MMBtu | Part II | June2005PM | 1 | 0 |  |  |  | 0.0136 |  | 0.0136 |  | 7.9939 | 0.10872
54081_2B | coal | 332 |  | 54081 | Spruance Genco, LLC | 2B | GEN2 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.0084421 | lb/MMBtu | ERT |  | 3 | 3 | 13461 |  | 0.0084421 | 0.0084421 |  | 0.0084421 |  | 13.0662 | 0.11031 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_2A | coal | 333 |  | 54081 | Spruance Genco, LLC | 2A | GEN2 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.0084421 | lb/MMBtu | ERT |  | 3 | 3 | 13461 |  | 0.0084421 | 0.0084421 |  | 0.0084421 |  | 13.0662 | 0.11031 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_4B | coal | 334 |  | 54081 | Spruance Genco, LLC | 4B | GEN4 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.00845 | lb/MMBtu | Part II | 2006 Emissions Testing at Boilers 4A and 4B | 2 | 2 |  |  | 0.00845 | 0.00845 |  | 0.00845 |  | 13.0662 | 0.11041 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_4A | coal | 335 |  | 54081 | Spruance Genco, LLC | 4A | GEN4 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.00845 | lb/MMBtu | Part II | 2006 Emissions Testing at Boilers 4A and 4B | 2 | 2 |  |  | 0.00845 | 0.00845 |  | 0.00845 |  | 13.0662 | 0.11041 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
988_2 | coal | 336 |  | 988 | Tanners Creek | 2 | TC-2 | Conventional Boiler | Vertical firing | 152.5 | 1391 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | Aug2009PM | 1 | 0 |  |  |  | 0.0122 |  | 0.0122 |  | 9.1213 | 0.11128
988_1 | coal | 337 |  | 988 | Tanners Creek | 1 | TC-1 | Conventional Boiler | Vertical firing | 152.5 | 1391 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | Aug2009PM | 1 | 0 |  |  |  | 0.0122 |  | 0.0122 |  | 9.1213 | 0.11128
2442_1 | coal | 338 |  | 2442 | Four Corners | 1 | 001 | Conventional Boiler | Wall firing - unspecified | 199 | 1707.7 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 13 | 1 | 0 |  |  |  | 0.013 |  | 0.013 |  | 8.5814 | 0.11156
1393_6 | coal | 339 |  | 1393 | RS Nelson | 6 | 001 | Conventional Boiler | Tangential firing | 580 | 5761 | Filterable Particulate | 0.011306 | lb/MMBtu | ERT |  | 3 | 3 | 2103 |  | 0.011306 | 0.011306 |  | 0.011306 |  | 9.9328 | 0.1123 | PM control | Electrostatic precipitator, unspecified | 1982-05-01
50_4 | coal | 340 |  | 50 | Widows Creek | 4 | 4 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | Filterable Particulate | 0.010333 | lb/MMBtu | Part II | WCF4 - 2005 | 3 | 3 |  |  | 0.010333 | 0.010333 |  | 0.010333 |  | 10.8677 | 0.1123
2104_2 | coal | 341 |  | 2104 | Meramec | 2 | 002 | Conventional Boiler | Tangential firing | 128 | 1566 | Filterable Particulate | 0.0092 | lb/MMBtu | Part II | 2 | 1 | 0 |  |  |  | 0.0092 |  | 0.0092 |  | 12.2344 | 0.11256
3992_7 | coal | 342 |  | 3992 | Blount Street | 7 | 7B1345T | Conventional Boiler | Cell burner | 22.4 | 310 | Filterable Particulate | 0.0081333 | lb/MMBtu | Part II | M074302 | 3 | 3 |  |  | 0.0081333 | 0.0081333 |  | 0.0081333 |  | 13.8393 | 0.11256
2094_2 | coal | 343 |  | 2094 | Sibley | 2 | 2 | Conventional Boiler | Cyclone firing | 51 | 627.3 | Filterable Particulate | 0.0091995 | lb/MMBtu | ERT |  | 3 | 3 | 894 |  | 0.0091995 | 0.0091995 |  | 0.0091995 |  | 12.3 | 0.11315 | NOx control | Selective Noncatalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-01-01
6249_3 | coal | 344 |  | 6249 | Winyah | 3 | W3 | Conventional Boiler | Wall firing - opposed firing | 305 | 2877 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | W3PM2008 | 1 | 1 |  |  |  | 0.012 |  | 0.012 |  | 9.4328 | 0.11319 | NOx control | Selective Catalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Spray Type | 1980-05-01
2840_4 | coal | 345 |  | 2840 | Conesville | 4 | CV-4 | Conventional Boiler | Tangential firing | 841.5 | 7960 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | Feb2010PM2 | 1 | 0 |  |  |  | 0.012 |  | 0.012 |  | 9.4593 | 0.11351
2832_Unit 7 | coal | 346 |  | 2832 | Miami Fort | Unit 7 | U7 | Conventional Boiler | Wall firing - opposed firing | 550 | 4995 | Filterable Particulate | 0.0125 | lb/MMBtu | Part II | U7050108 | 4 | 4 |  |  | 0.0125 | 0.0125 |  | 0.0125 |  | 9.0818 | 0.11352
727_3 | coal | 347 |  | 727 | Mitchell | 3 | Unit 3 | Conventional Boiler | Tangential firing | 164 | 855 | Filterable Particulate | 0.022033 | lb/MMBtu | Part II | Unit 3 PM Emissions Test (August 8, 2006) | 3 | 0 |  |  | 0.022033 | 0.022033 |  | 0.022033 |  | 5.2134 | 0.11487
3149_2 | coal | 348 |  | 3149 | PPL Montour | 2 | U2 | Conventional Boiler | Tangential firing | 792 | 7239 | Filterable Particulate | 0.0126 | lb/MMBtu | Part II | M2409 | 1 | 1 |  |  |  | 0.0126 |  | 0.0126 |  | 9.1402 | 0.11517 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-05-01 | NOx control | Selective Catalytic Reduction | 2000-05-01 | SO2 control | Wet FGD - Tray Type | 2008-03-01
3_2 | coal | 349 |  | 3 | Barry | 2 | Unit 2 | Conventional Boiler | Tangential firing | 145 | 1372.7464 | Filterable Particulate | 0.012171 | lb/MMBtu | Part II | Unit 2 PM Emissions Test (May 21, 2008) | 3 | 0 |  |  | 0.012171 | 0.012171 |  | 0.012171 |  | 9.4672 | 0.11522
6068_3 | coal | 350 |  | 6068 | Jeffrey Energy Center | 3 | 3 | Conventional Boiler | Tangential firing | 783 | 7815 | Filterable Particulate | 0.011567 | lb/MMBtu | Part II | PM 0707/3 | 3 | 1 |  |  | 0.011567 | 0.011567 |  | 0.011567 |  | 9.9808 | 0.11545 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-05-01 | SO2 control | Wet FGD - Spray Type | 1983-05-01
1702_2 | coal | 351 |  | 1702 | D.E. Karn | 2 | DEK2-Conf | Conventional Boiler | Wall firing - front firing | 281 | 2587 | Filterable Particulate | 0.012667 | lb/MMBtu | Part II | DEK2 - 2008 PM Testing | 3 | 3 |  |  | 0.012667 | 0.012667 |  | 0.012667 |  | 9.2064 | 0.11661
3_3 | coal | 352 |  | 3 | Barry | 3 | Unit 3 | Conventional Boiler | Tangential firing | 263 | 2434.4652 | Filterable Particulate | 0.012667 | lb/MMBtu | Part II | Unit 3 PM Emissions Test (May 22, 2008) | 3 | 0 |  |  | 0.012667 | 0.012667 |  | 0.012667 |  | 9.2565 | 0.11725
2828_2 | coal | 353 |  | 2828 | Cardinal | 2 | CD-U2 | Conventional Boiler | Wall firing - opposed firing | 615.2 | 5275 | Filterable Particulate | 0.0138 | lb/MMBtu | Part II | June2009PM2 | 1 | 0 |  |  |  | 0.0138 |  | 0.0138 |  | 8.5744 | 0.11833
1897_4 | coal | 354 |  | 1897 | Hibbard Energy Center | 4 | HREC4 | Conventional Boiler | Stoker - spreader | 36 | 471 | Filterable Particulate | 0.00905 | lb/MMBtu | Part II | PM_CO-Boiler4 | 4 | 0 |  |  | 0.00905 | 0.00905 |  | 0.00905 |  | 13.0833 | 0.1184
26_4 | coal | 355 |  | 26 | E. C. Gaston | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 270 | 2468.352 | Filterable Particulate | 0.013022 | lb/MMBtu | Part II | Report 4 | 3 | 0 |  |  | 0.013022 | 0.013022 |  | 0.013022 |  | 9.142 | 0.11905
733_1 | coal | 356 |  | 733 | Kraft | 1 | Unit 1 | Conventional Boiler | Tangential firing | 50 | 547.536 | Filterable Particulate | 0.01089 | lb/MMBtu | Part II | Unit 1 PM Emissions Test (September 27, 2007) | 3 | 0 |  |  | 0.01089 | 0.01089 |  | 0.01089 |  | 10.9507 | 0.11925
6085_17 | coal | 357 |  | 6085 | R.M. Schahfer | 17 | R.M.0017 | Conventional Boiler | Tangential firing | 393 | 3967 | Filterable Particulate | 0.011848 | lb/MMBtu | Part II | RMSGS U#17 M5 04/21/2009 | 1 | 1 |  |  |  | 0.011848 |  | 0.011848 |  | 10.0941 | 0.11959
2876_4 | coal | 358 |  | 2876 | Kyger Creek | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 213 | 2158.716 | Filterable Particulate | 0.0119 | lb/MMBtu | Part II | Unit4Particulate2005 | 1 | 1 |  |  |  | 0.0119 |  | 0.0119 |  | 10.1348 | 0.1206
3393_1 | coal | 359 |  | 3393 | Allen Steam Plant | 1 | 1 | Conventional Boiler | Cyclone firing | 330 | 3064 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | ALF1 - 2008 | 3 | 3 |  |  | 0.013 | 0.013 |  | 0.013 |  | 9.2848 | 0.1207
1374_1374-2 | coal | 360 |  | 1374 | Elmer Smith Station | 1374-2 | Unit001 | Conventional Boiler | Cyclone firing | 153 | 1370 | Filterable Particulate | 0.014672 | lb/MMBtu | ERT |  | 6 | 6 | 1330 |  | 0.014672 | 0.014672 |  | 0.014672 |  | 8.2947 | 0.1217 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
1374_1374 | coal | 361 |  | 1374 | Elmer Smith Station | 1374 | Unit001 | Conventional Boiler | Cyclone firing | 153 | 1370 | Filterable Particulate | 0.014672 | lb/MMBtu | ERT |  | 6 | 6 | 1330 |  | 0.014672 | 0.014672 |  | 0.014672 |  | 8.2947 | 0.1217 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
10774_2 | coal | 362 |  | 10774 | Southampton Power Station | 2 | Unit 1 & 2 | Conventional Boiler | Stoker - spreader | 34 | 442 | Filterable Particulate | 0.0093337 | lb/MMBtu | ERT |  | 3 | 3 | 1524 |  | 0.0093337 | 0.0093337 |  | 0.0093337 |  | 13.0735 | 0.12202 | PM control | Multiple cyclone | 1992-03-01 | PM control | Multiple cyclone | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01
10774_1 | coal | 363 |  | 10774 | Southampton Power Station | 1 | Unit 1 & 2 | Conventional Boiler | Stoker - spreader | 34 | 442 | Filterable Particulate | 0.0093337 | lb/MMBtu | ERT |  | 3 | 3 | 1524 |  | 0.0093337 | 0.0093337 |  | 0.0093337 |  | 13.0735 | 0.12202 | PM control | Multiple cyclone | 1992-03-01 | PM control | Multiple cyclone | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01
728_Y7BR | coal | 364 |  | 728 | Yates | Y7BR | Y7BR | Conventional Boiler | Tangential firing | 361 | 3437.82 | Filterable Particulate | 0.012828 | lb/MMBtu | Part II | Unit 7 PM Emissions Test (April 27, 2005) | 3 | 0 |  |  | 0.012828 | 0.012828 |  | 0.012828 |  | 9.523 | 0.12216
2324_2 | coal | 365 |  | 2324 | Reid Gardner | 2 | 2 | Conventional Boiler | Wall firing - front firing | 111 | 1215 | Filterable Particulate | 0.011267 | lb/MMBtu | Part II | U2_2009_COMPLIANCE | 3 | 3 |  |  | 0.011267 | 0.011267 |  | 0.011267 |  | 10.9459 | 0.12332
1382_H1 | coal | 366 |  | 1382 | HMP&L Station Two Henderson | H1 | 1 | Conventional Boiler | Wall firing - rear firing | 166.1 | 1799 | Filterable Particulate | 0.011467 | lb/MMBtu | Part II | H1 compliance 2007 | 3 | 3 |  |  | 0.011467 | 0.011467 |  | 0.011467 |  | 10.8308 | 0.12419
3140_3 | coal | 367 |  | 3140 | PPL Brunner Island | 3 | U3 | Conventional Boiler | Tangential firing | 780 | 7239 | Filterable Particulate | 0.0134 | lb/MMBtu | Part II | B3509 | 1 | 1 |  |  |  | 0.0134 |  | 0.0134 |  | 9.2808 | 0.12436
2952_6 | coal | 368 |  | 2952 | Muskogee | 6 | MK6 Config | Conventional Boiler | Tangential firing | 371 | 5214.89 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | Stack Sampling Report\ Muskogee 6 | 1 | 1 |  |  |  | 0.009 |  | 0.009 |  | 14.0563 | 0.12651
898_Unit 5 | coal | 369 |  | 898 | Wood River | Unit 5 | 5 | Conventional Boiler | Tangential firing | 391 | 4123 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 15 | 1 | 0 |  |  | 0.012 | 0.012 |  | 0.012 |  | 10.5448 | 0.12654
3131_4 | coal | 370 |  | 3131 | Shawville | 4 | SHAW4-2 | Conventional Boiler | Tangential firing | 188 | 1794 | Filterable Particulate | 0.013283 | lb/MMBtu | ERT |  | 9 | 9 | 1471 |  | 0.013283 | 0.013283 |  | 0.013283 |  | 9.5426 | 0.12675 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
3131_3 | coal | 371 |  | 3131 | Shawville | 3 | SHAW3-2 | Conventional Boiler | Tangential firing | 188 | 1794 | Filterable Particulate | 0.013283 | lb/MMBtu | ERT |  | 9 | 9 | 1471 |  | 0.013283 | 0.013283 |  | 0.013283 |  | 9.5426 | 0.12675 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1959-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
3159_1 | coal | 372 | Retired | 3159 | Cromby Generating Station | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 161 | 1537 | Filterable Particulate | 0.013433 | lb/MMBtu | Part II | 6/16/09 PM/PM2.5 | 3 | 3 |  |  | 0.013433 | 0.013433 |  | 0.013433 |  | 9.5466 | 0.12824
6085_18 | coal | 373 |  | 6085 | R.M. Schahfer | 18 | R.M.0018 | Conventional Boiler | Tangential firing | 393 | 3967 | Filterable Particulate | 0.013022 | lb/MMBtu | Part II | RMSGS U#18 M5b 05/02/2006 | 1 | 1 |  |  |  | 0.013022 |  | 0.013022 |  | 10.0941 | 0.13144
645_1 | coal | 374 |  | 645 | Big Bend | 1 | BB01_pre-SCR | Conventional Boiler | Wall firing - opposed firing | 410 | 4037 | Filterable Particulate | 0.013489 | lb/MMBtu | Part II | BB#1_FY2007 | 1 | 0 |  |  |  | 0.013489 |  | 0.013489 |  | 9.8463 | 0.13281
4259_1 | coal | 375 |  | 4259 | Endicott Station | 1 | 1 | Conventional Boiler | Wall firing - front firing | 60 | 617 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | PM 7/1/2008 | 3 | 3 |  |  | 0.013 | 0.013 |  | 0.013 |  | 10.2833 | 0.13368
3935_1 | coal | 376 |  | 3935 | John E. Amos | 1 | AM-1 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | Filterable Particulate | 0.0156 | lb/MMBtu | Part II | CS012 | 1 | 0 |  |  |  | 0.0156 |  | 0.0156 |  | 8.5998 | 0.13416
8102_2 | coal | 377 |  | 8102 | General James M. Gavin | 2 | GA-2 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11936 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | Feb2009PM2 | 1 | 0 |  |  |  | 0.015 |  | 0.015 |  | 9.0424 | 0.13564
56_2 | coal | 378 |  | 56 | Charles R. Lowman | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 258 | 2500 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 2009 PM Test - 2 | 1 | 1 |  |  | 0 | 0.014 |  | 0.014 |  | 9.6899 | 0.13566
1363_5 | coal | 379 |  | 1363 | Cane Run | 5 | CR5 | Conventional Boiler | Wall firing - front firing | 181 | 2182 | Filterable Particulate | 0.011257 | lb/MMBtu | ERT |  | 3 | 3 | 18261 |  | 0.011257 | 0.011257 |  | 0.011257 |  | 12.0552 | 0.13571 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-03-01 | SO2 control | Wet FGD - Spray Type | 1978-05-01
1356_4 | coal | 380 |  | 1356 | Ghent | 4 | GH4 | Conventional Boiler | Wall firing - opposed firing | 525 | 5967 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | GH4-PM-2008 | 1 | 1 |  |  |  | 0.012 |  | 0.012 |  | 11.3657 | 0.13639
6139_3 | coal | 381 |  | 6139 | Welsh | 3 | WE-3 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | Filterable Particulate | 0.0148 | lb/MMBtu | Part II | May2008PM | 1 | 0 |  |  |  | 0.0148 |  | 0.0148 |  | 9.2401 | 0.13675
7030_U2 | coal | 382 |  | 7030 | Twin Oaks Power One | U2 | U2 | Fluidized bed firing | Fluidized bed firing | 172 | 1717 | Filterable Particulate | 0.013838 | lb/MMBtu | ERT |  | 6 | 6 | 941 |  | 0.013838 | 0.013838 |  | 0.013838 |  | 9.9826 | 0.13814
2442_2 | coal | 383 |  | 2442 | Four Corners | 2 | 002 | Conventional Boiler | Wall firing - unspecified | 197 | 1707.7 | Filterable Particulate | 0.016 | lb/MMBtu | Part II | 2 | 1 | 0 |  |  |  | 0.016 |  | 0.016 |  | 8.6685 | 0.1387
3393_3 | coal | 384 |  | 3393 | Allen Steam Plant | 3 | 3 | Conventional Boiler | Cyclone firing | 330 | 3064 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | ALF3 - 2008 | 3 | 3 |  |  | 0.015 | 0.015 |  | 0.015 |  | 9.2848 | 0.13927
2963_3314 | coal | 385 |  | 2963 | Northeastern | 3314 | NE-4 | Conventional Boiler | Tangential firing | 490 | 4775 | Filterable Particulate | 0.0143 | lb/MMBtu | Part II | June2006PM | 1 | 0 |  |  |  | 0.0143 |  | 0.0143 |  | 9.7449 | 0.13935
2963_3313 | coal | 386 |  | 2963 | Northeastern | 3313 | NE-3 | Conventional Boiler | Tangential firing | 490 | 4775 | Filterable Particulate | 0.0143 | lb/MMBtu | Part II | June2006PM | 1 | 0 |  |  |  | 0.0143 |  | 0.0143 |  | 9.7449 | 0.13935
994_4 | coal | 387 |  | 994 | AES Petersburg | 4 | 4s | Conventional Boiler | Tangential firing | 584 | 5550 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | Unit 4 - PM 08/2009 | 3 | 3 |  |  | 0.014667 | 0.014667 |  | 0.014667 |  | 9.5034 | 0.13938 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1986-12-01 | SO2 control | Wet FGD - Spray Type | 1986-12-01
645_3 | coal | 388 |  | 645 | Big Bend | 3 | BB03_SCR_iso | Conventional Boiler | Wall firing - opposed firing | 400 | 4115 | Filterable Particulate | 0.013609 | lb/MMBtu | Part II | BB#3_FY2009 | 1 | 0 |  |  |  | 0.013609 |  | 0.013609 |  | 10.2875 | 0.14
2848_H-1 | coal | 389 |  | 2848 | O H Hutchings | H-1 | H-1 | Conventional Boiler | Tangential firing | 53 | 607 | Filterable Particulate | 0.012233 | lb/MMBtu | Part II | 2006 H-1 retest | 3 | 3 |  |  | 0.012233 | 0.012233 |  | 0.012233 |  | 11.4528 | 0.14011 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
3944_3 | coal | 390 |  | 3944 | Harrison Power Station | 3 | Boiler3 | Conventional Boiler | Wall firing - unspecified | 692 | 5876 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 10 | 3 | 0 |  |  | 0.016667 | 0.016667 |  | 0.016667 |  | 8.4913 | 0.14152
54081_1B | coal | 391 |  | 54081 | Spruance Genco, LLC | 1B | GEN1 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.01085 | lb/MMBtu | ERT |  | 3 | 3 | 1346 |  | 0.01085 | 0.01085 |  | 0.01085 |  | 13.0662 | 0.14177
54081_1A | coal | 392 |  | 54081 | Spruance Genco, LLC | 1A | GEN1 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.01085 | lb/MMBtu | ERT |  | 3 | 3 | 1346 |  | 0.01085 | 0.01085 |  | 0.01085 |  | 13.0662 | 0.14177
3113_1 | coal | 393 |  | 3113 | Portland | 1 | POR-1 | Conventional Boiler | Tangential firing | 172 | 1719 | Filterable Particulate | 0.0142 | lb/MMBtu | Part II | P-92-U1 | 3 | 3 |  |  | 0.0142 | 0.0142 |  | 0.0142 |  | 9.9942 | 0.14192 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1989-01-01
728_Y6BR | coal | 394 |  | 728 | Yates | Y6BR | Y6BR | Conventional Boiler | Tangential firing | 363 | 3492.896 | Filterable Particulate | 0.014795 | lb/MMBtu | Part II | Unit 6 PM Emissions Test (February 28, 2007) | 3 | 0 |  |  | 0.014795 | 0.014795 |  | 0.014795 |  | 9.6223 | 0.14236 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-07-01
2718_ES-2 | coal | 395 |  | 2718 | G G Allen | ES-2 | 2-2009 | Conventional Boiler | Tangential firing | 177 | 1509 | Filterable Particulate | 0.016933 | lb/MMBtu | Part II | CS125(4/23/09) | 3 | 0 |  |  | 0.016933 | 0.016933 |  | 0.016933 |  | 8.5254 | 0.14436
2535_1 | coal | 396 |  | 2535 | AES Cayuga, LLC | 1 | Unit_1 | Conventional Boiler | Tangential firing | 164 | 1462 | Filterable Particulate | 0.0162 | lb/MMBtu | Part II | 9_902519TSP_a | 1 | 1 |  |  |  | 0.0162 |  | 0.0162 |  | 8.9146 | 0.14442 | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning |  | SO2 control | Wet FGD - Spray Type | 1995-06-01
10603_031 | coal | 397 |  | 10603 | Ebensburg Power Company | 031 | EPC01 | Fluidized bed firing | Fluidized bed firing | 58 | 830 | Filterable Particulate | 0.010167 | lb/MMBtu | Part II | 2005 Emissions | 6 | 6 |  |  | 0.010167 | 0.010167 |  | 0.010167 |  | 14.3103 | 0.14549 | PM control | Fabric Filter, pulse | 1990-11-01
6641_1 | coal | 398 |  | 6641 | Independence | 1 | 001 | Conventional Boiler | Tangential firing | 853 | 8700 | Filterable Particulate | 0.014333 | lb/MMBtu | Part II | 1 | 3 | 0 |  |  | 0.014333 | 0.014333 |  | 0.014333 |  | 10.1993 | 0.14619
55076_AA-002 | coal | 399 |  | 55076 | Red Hills Generating Facility | AA-002 | 002 | Fluidized bed firing | Fluidized bed firing | 250 | 2382.3 | Filterable Particulate | 0.015443 | lb/MMBtu | ERT |  | 3 | 3 | 1060 |  | 0.015443 | 0.015443 |  | 0.015443 |  | 9.5292 | 0.14716
2828_3 | coal | 400 |  | 2828 | Cardinal | 3 | CD-U3 | Conventional Boiler | Wall firing - opposed firing | 650 | 5275 | Filterable Particulate | 0.018161 | lb/MMBtu | ERT |  | 6 | 6 | 1004 |  | 0.018161 | 0.018161 |  | 0.018161 |  | 8.1154 | 0.14738 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-09-01 | NOx control | Selective Catalytic Reduction | 2003-01-01
55076_AA-001 | coal | 401 |  | 55076 | Red Hills Generating Facility | AA-001 | 001 | Fluidized bed firing | Fluidized bed firing | 250 | 2401 | Filterable Particulate | 0.015443 | lb/MMBtu | ERT |  | 3 | 3 | 1058 |  | 0.015443 | 0.015443 |  | 0.015443 |  | 9.604 | 0.14831
2832_Unit 8 | coal | 402 |  | 2832 | Miami Fort | Unit 8 | U8 | Conventional Boiler | Wall firing - opposed firing | 550 | 5003 | Filterable Particulate | 0.016333 | lb/MMBtu | Part II | U8082907 | 3 | 3 |  |  | 0.016333 | 0.016333 |  | 0.016333 |  | 9.0964 | 0.14857
3152_4 | coal | 403 |  | 3152 | Sunbury Generation LP | 4 | Boiler 4 | Conventional Boiler | Wall firing - front firing | 128 | 1360 | Filterable Particulate | 0.014 | lb/MMBtu | ERT |  | 6 | 6 | 2306 |  | 0.014 | 0.014 |  | 0.014 |  | 10.625 | 0.14875 | Other control | Other (specify): SO3 injection | 1980-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-06-01
6768_1 | coal | 404 |  | 6768 | Sikeston Power Station | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 233 | 2780 | Filterable Particulate | 0.012533 | lb/MMBtu | Part II | 2007 CPM | 3 | 0 |  |  | 0.012533 | 0.012533 |  | 0.012533 |  | 11.9313 | 0.14954 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-09-01
3407_9 | coal | 405 |  | 3407 | Kingston | 9 | 9 | Conventional Boiler | Tangential firing | 200 | 2056 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | KIF6-9 - 2007 | 3 | 3 |  |  | 0.014667 | 0.014667 |  | 0.014667 |  | 10.28 | 0.15077
3407_8 | coal | 406 |  | 3407 | Kingston | 8 | 8 | Conventional Boiler | Tangential firing | 200 | 2056 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | KIF6-9 - 2007 | 3 | 3 |  |  | 0.014667 | 0.014667 |  | 0.014667 |  | 10.28 | 0.15077
3407_7 | coal | 407 |  | 3407 | Kingston | 7 | 7 | Conventional Boiler | Tangential firing | 200 | 2056 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | KIF6-9 - 2007 | 3 | 3 |  |  | 0.014667 | 0.014667 |  | 0.014667 |  | 10.28 | 0.15077
3407_6 | coal | 408 |  | 3407 | Kingston | 6 | 6 | Conventional Boiler | Tangential firing | 200 | 2056 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | KIF6-9 - 2007 | 3 | 3 |  |  | 0.014667 | 0.014667 |  | 0.014667 |  | 10.28 | 0.15077
2828_1 | coal | 409 |  | 2828 | Cardinal | 1 | CD-U1 | Conventional Boiler | Wall firing - opposed firing | 615.2 | 5275 | Filterable Particulate | 0.0176 | lb/MMBtu | Part II | June2009PM | 1 | 0 |  |  |  | 0.0176 |  | 0.0176 |  | 8.5744 | 0.15091
2917_9 | coal | 410 |  | 2917 | Hamilton | 9 | Unit 9 | Conventional Boiler | Tangential firing | 50.6 | 729 | Filterable Particulate | 0.0105 | lb/MMBtu | Part II | U9-Particulate | 6 | 6 |  |  | 0.0105 | 0.0105 |  | 0.0105 |  | 14.4071 | 0.15127
6085_15 | coal | 411 |  | 6085 | R.M. Schahfer | 15 | R.M.0015 | Conventional Boiler | Wall firing - opposed firing | 502 | 5100 | Filterable Particulate | 0.014908 | lb/MMBtu | Part II | RMSGS U#15 M5 04/04/2006 | 1 | 1 |  |  |  | 0.014908 |  | 0.014908 |  | 10.1594 | 0.15145
136_1 | coal | 412 |  | 136 | Seminole Generating Station | 1 | Unit 1 | Conventional Boiler | Wall firing - opposed firing | 694 | 7172 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | Multi-Pollutant Test Report 2009 (Unit 1) | 3 | 3 |  |  | 0.014667 | 0.014667 |  | 0.014667 |  | 10.3343 | 0.15157 | NOx control | Selective Catalytic Reduction | 2009-02-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-01-01 | Other control | Dry sorbent injection | 2009-02-01 | SO2 control | Wet FGD - Spray Type | 1984-01-01
1385_3 | coal | 413 |  | 1385 | Dale Station | 3 | 03 | Conventional Boiler | Wall firing - front firing | 80 | 944 | Filterable Particulate | 0.012871 | lb/MMBtu | ERT |  | 3 | 3 | 993 |  | 0.012871 | 0.012871 |  | 0.012871 |  | 11.8 | 0.15188 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning
990_60 | coal | 414 |  | 990 | Harding Street | 60 | 60s | Conventional Boiler | Tangential firing | 112 | 1017 | Filterable Particulate | 0.016765 | lb/MMBtu | ERT |  | 6 | 6 | 632 |  | 0.016765 | 0.016765 |  | 0.016765 |  | 9.0804 | 0.15223 | NOx control | Selective Noncatalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-12-01
3406_9 | coal | 415 |  | 3406 | Johnsonville | 9 | 9 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 10.0347 | 0.15387
3406_8 | coal | 416 |  | 3406 | Johnsonville | 8 | 8 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 10.0347 | 0.15387
3406_7 | coal | 417 |  | 3406 | Johnsonville | 7 | 7 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 10.0347 | 0.15387
3406_10 | coal | 418 |  | 3406 | Johnsonville | 10 | 10 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 10.0347 | 0.15387
2442_3 | coal | 419 |  | 2442 | Four Corners | 3 | 003 | Conventional Boiler | Wall firing - unspecified | 256 | 2189.6 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 15 | 1 | 0 |  |  |  | 0.018 |  | 0.018 |  | 8.5531 | 0.15396
6823_W1 | coal | 420 |  | 6823 | D B Wilson | W1 | 1 | Conventional Boiler | Wall firing - opposed firing | 443 | 4477 | Filterable Particulate | 0.0153 | lb/MMBtu | Part II | W1 Compliance 2008 | 3 | 3 |  |  | 0.0153 | 0.0153 |  | 0.0153 |  | 10.1061 | 0.15462
10143_AAB01 | coal | 421 |  | 10143 | Colver Power Project | AAB01 | AAB01 | Fluidized bed firing | Fluidized bed firing | 131 | 1204 | Filterable Particulate | 0.016939 | lb/MMBtu | ERT |  | 6 | 6 | 1293 |  | 0.016939 | 0.016939 |  | 0.016939 |  | 9.1908 | 0.15569 | NOx control | Selective Noncatalytic Reduction | 1995-05-01 | PM control | Fabric Filter, pulse | 1995-05-01
733_3 | coal | 422 |  | 733 | Kraft | 3 | Unit 3 | Conventional Boiler | Tangential firing | 107 | 1052.334 | Filterable Particulate | 0.016107 | lb/MMBtu | Part II | Unit 3 PM Emissions Test (September 21, 2006) | 3 | 0 |  |  | 0.016107 | 0.016107 |  | 0.016107 |  | 9.8349 | 0.15841
2535_2 | coal | 423 |  | 2535 | AES Cayuga, LLC | 2 | Unit_2 | Conventional Boiler | Tangential firing | 168 | 1450 | Filterable Particulate | 0.0185 | lb/MMBtu | Part II | 2_902306_b | 1 | 1 |  |  |  | 0.0185 |  | 0.0185 |  | 8.631 | 0.15967 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning |  | SO2 control | Wet FGD - Spray Type | 1995-01-01
1831_EUBoiler5 | coal | 424 |  | 1831 | Otto E. Eckert Station | EUBoiler5 | 005 | Conventional Boiler | Wall firing - front firing | 71 | 807 | Filterable Particulate | 0.014067 | lb/MMBtu | Part II | PM-5-9/05 | 3 | 0 |  |  | 0.014067 | 0.014067 |  | 0.014067 |  | 11.3662 | 0.15988
2716_2 | coal | 425 |  | 2716 | W.H. Weatherspoon Plant | 2 | Wea_Cfg_1 | Conventional Boiler | Wall firing - front firing | 53 | 472 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | Wea_Blr_1_Test_6 | 3 | 3 |  |  | 0.018 | 0.018 |  | 0.018 |  | 8.9057 | 0.1603 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
2716_1 | coal | 426 |  | 2716 | W.H. Weatherspoon Plant | 1 | Wea_Cfg_1 | Conventional Boiler | Wall firing - front firing | 53 | 472 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | Wea_Blr_1_Test_6 | 3 | 3 |  |  | 0.018 | 0.018 |  | 0.018 |  | 8.9057 | 0.1603 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
2718_ES-5 | coal | 427 |  | 2718 | G G Allen | ES-5 | 5-2009 | Conventional Boiler | Tangential firing | 285.3 | 2705 | Filterable Particulate | 0.016933 | lb/MMBtu | Part II | CS125(4/23/09) | 3 | 0 |  |  | 0.016933 | 0.016933 |  | 0.016933 |  | 9.4812 | 0.16055
6068_1 | coal | 428 |  | 6068 | Jeffrey Energy Center | 1 | 1 | Conventional Boiler | Tangential firing | 790 | 8396 | Filterable Particulate | 0.015213 | lb/MMBtu | Part II | PM TEST 0709\1 | 3 | 3 |  |  | 0.015213 | 0.015213 |  | 0.015213 |  | 10.6278 | 0.16168
1077_2 | coal | 429 |  | 1077 | Sutherland | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 30.9 | 375.6 | Filterable Particulate | 0.0134 | lb/MMBtu | Part II | SUTH2-PM-20060517 | 1 | 1 |  |  |  | 0.0134 |  | 0.0134 |  | 12.1553 | 0.16288 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-11-01
1702_1 | coal | 430 |  | 1702 | D.E. Karn | 1 | DEK1-Conf | Conventional Boiler | Tangential firing | 275 | 2445 | Filterable Particulate | 0.018333 | lb/MMBtu | Part II | DEK1 - 2005 PM Testing | 3 | 3 |  |  | 0.018333 | 0.018333 |  | 0.018333 |  | 8.8909 | 0.163
3406_6 | coal | 431 |  | 3406 | Johnsonville | 6 | 6 | Conventional Boiler | Tangential firing | 147 | 1566 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 10.6531 | 0.16335
3406_5 | coal | 432 |  | 3406 | Johnsonville | 5 | 5 | Conventional Boiler | Tangential firing | 147 | 1566 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 10.6531 | 0.16335
2718_ES-1 | coal | 433 |  | 2718 | G G Allen | ES-1 | 1-2009 | Conventional Boiler | Tangential firing | 176.2 | 1738 | Filterable Particulate | 0.016933 | lb/MMBtu | Part II | CS125(4/23/09) | 3 | 0 |  |  | 0.016933 | 0.016933 |  | 0.016933 |  | 9.8638 | 0.16703
6124_1 | coal | 434 |  | 6124 | McIntosh | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 165 | 1598.3345 | Filterable Particulate | 0.017305 | lb/MMBtu | Part II | + | 3 | 0 |  |  | 0.017305 | 0.017305 |  | 0.017305 |  | 9.6869 | 0.16763
6641_2 | coal | 435 |  | 6641 | Independence | 2 | 002 | Conventional Boiler | Tangential firing | 879 | 8700 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 2 | 3 | 0 |  |  | 0.017 | 0.017 |  | 0.017 |  | 9.8976 | 0.16826
2161_5 | coal | 436 |  | 2161 | James River Power Station | 5 | Unit_5_JRPS | Conventional Boiler | Wall firing - front firing | 105 | 1010 | Filterable Particulate | 0.017637 | lb/MMBtu | ERT |  | 3 | 3 | 21351 |  | 0.017637 | 0.017637 |  | 0.017637 |  | 9.619 | 0.16965 | NOx control | Selective Noncatalytic Reduction | 2009-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-05-01
3406_1 | coal | 437 |  | 3406 | Johnsonville | 1 | 1 | Conventional Boiler | Tangential firing | 125 | 1405 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | JOF1-10 - 2005 | 3 | 3 |  |  | 0.015333 | 0.015333 |  | 0.015333 |  | 11.24 | 0.17235
2732_9 | coal | 438 |  | 2732 | Riverbend | 9 | 9 | Conventional Boiler | Tangential firing | 141.7 | 1318 | Filterable Particulate | 0.018567 | lb/MMBtu | Part II | BLR9(3/20/07) | 3 | 0 |  |  | 0.018567 | 0.018567 |  | 0.018567 |  | 9.3013 | 0.17269
1382_H2 | coal | 439 |  | 1382 | HMP&L Station Two Henderson | H2 | 2 | Conventional Boiler | Wall firing - rear firing | 173.1 | 1866.2 | Filterable Particulate | 0.016067 | lb/MMBtu | Part II | H2 compliance 2006 | 3 | 3 |  |  | 0.016067 | 0.016067 |  | 0.016067 |  | 10.7811 | 0.17322
6071_1 | coal | 440 |  | 6071 | Trimble Co. | 1 | TC01 | Conventional Boiler | Tangential firing | 547 | 5602 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | TC1-PM-2008 | 1 | 1 |  |  |  | 0.017 |  | 0.017 |  | 10.2413 | 0.1741
2832_Unit 6 | coal | 441 |  | 2832 | Miami Fort | Unit 6 | U6 | Conventional Boiler | Tangential firing | 175 | 1253 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | U6032708 | 3 | 3 |  |  | 0.024333 | 0.024333 |  | 0.024333 |  | 7.16 | 0.17423
3935_3 | coal | 442 |  | 3935 | John E. Amos | 3 | AM-3 | Conventional Boiler | Wall firing - opposed firing | 1300 | 11936 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | Unit 3 | 1 | 0 |  |  |  | 0.019 |  | 0.019 |  | 9.1815 | 0.17445
6031_2 | coal | 443 |  | 6031 | Killen Station | 2 | 2-Operation | Conventional Boiler | Wall firing - opposed firing | 658 | 5928 | Filterable Particulate | 0.019433 | lb/MMBtu | Part II | PM Test 2007 | 3 | 3 |  |  | 0.019433 | 0.019433 |  | 0.019433 |  | 9.0091 | 0.17508
3938_21 | coal | 444 |  | 3938 | Philip Sporn | 21 | SP-2 | Conventional Boiler | Vertical firing | 152.5 | 1311 | Filterable Particulate | 0.0206 | lb/MMBtu | Part II | July2005PM | 1 | 0 |  |  |  | 0.0206 |  | 0.0206 |  | 8.5967 | 0.17709
3938_11 | coal | 445 |  | 3938 | Philip Sporn | 11 | SP-1 | Conventional Boiler | Vertical firing | 152.5 | 1311 | Filterable Particulate | 0.0206 | lb/MMBtu | Part II | July2005PM | 1 | 0 |  |  |  | 0.0206 |  | 0.0206 |  | 8.5967 | 0.17709
6061_2 | coal | 446 |  | 6061 | South Mississippi El Pwr Assn | 2 | 2 | Conventional Boiler | Turbo | 204 | 2600 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | Morrow PM 2008 | 1 | 1 |  |  |  | 0.014 |  | 0.014 |  | 12.7451 | 0.17843
6061_1 | coal | 447 |  | 6061 | South Mississippi El Pwr Assn | 1 | 1 | Conventional Boiler | Turbo | 204 | 2600 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | Morrow PM 2008 | 1 | 1 |  |  |  | 0.014 |  | 0.014 |  | 12.7451 | 0.17843
898_Unit 4 | coal | 448 |  | 898 | Wood River | Unit 4 | 4 | Conventional Boiler | Tangential firing | 97 | 1181 | Filterable Particulate | 0.0147 | lb/MMBtu | Part II | 10 | 1 | 0 |  |  | 0.0147 | 0.0147 |  | 0.0147 |  | 12.1753 | 0.17898
2732_10 | coal | 449 |  | 2732 | Riverbend | 10 | 10 | Conventional Boiler | Tangential firing | 141.1 | 1318 | Filterable Particulate | 0.0193 | lb/MMBtu | Part II | BLR10(3/5/09) | 3 | 0 |  |  | 0.0193 | 0.0193 |  | 0.0193 |  | 9.3409 | 0.18028
6166_MB2 | coal | 450 |  | 6166 | Rockport | MB2 | RP-2 | Conventional Boiler | Wall firing - opposed firing | 1320 | 12374 | Filterable Particulate | 0.0194 | lb/MMBtu | Part II | Feb2010PMwPAC | 1 | 0 |  |  |  | 0.0194 |  | 0.0194 |  | 9.3742 | 0.18186
6166_MB1 | coal | 451 |  | 6166 | Rockport | MB1 | RP-1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 12374 | Filterable Particulate | 0.0194 | lb/MMBtu | Part II | Feb2010PMwPAC | 1 | 0 |  |  |  | 0.0194 |  | 0.0194 |  | 9.3742 | 0.18186
2824_1 | coal | 452 |  | 2824 | Stanton | 1 | u1 | Conventional Boiler | Wall firing - front firing | 132 | 1800 | Filterable Particulate | 0.0135 | lb/MMBtu | Part II | Particulate test | 4 | 4 |  |  |  | 0.0135 |  | 0.0135 |  | 13.6364 | 0.18409 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-01-01
7253_1 | coal | 453 |  | 7253 | Richard Gorsuch | 1 | UNIT1 | Conventional Boiler | Radiant | 53.3 | 455.3 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | Particulate2008(1,2,4) | 3 | 3 |  |  | 0.022 | 0.022 |  | 0.022 |  | 8.5422 | 0.18793
990_70 | coal | 454 |  | 990 | Harding Street | 70 | 70ss | Conventional Boiler | Tangential firing | 463 | 4123 | Filterable Particulate | 0.021119 | lb/MMBtu | ERT |  | 6 | 6 | 1177 |  | 0.021119 | 0.021119 |  | 0.021119 |  | 8.905 | 0.18806 | NOx control | Selective Catalytic Reduction | 2005-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-12-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
6139_2 | coal | 455 |  | 6139 | Welsh | 2 | WE-2 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | Filterable Particulate | 0.0204 | lb/MMBtu | Part II | Jan2008PM | 1 | 0 |  |  |  | 0.0204 |  | 0.0204 |  | 9.2401 | 0.1885
3098_4 | coal | 456 |  | 3098 | Elrama Power Plant | 4 | ELR4-2 | Conventional Boiler | Wall firing - front firing | 185 | 1921 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT |  | 9 | 9 | 966 |  | 0.018448 | 0.018448 |  | 0.018448 |  | 10.3838 | 0.19156 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1960-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-11-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
3098_3 | coal | 457 |  | 3098 | Elrama Power Plant | 3 | ELR3-2 | Conventional Boiler | Vertical firing | 125 | 1303 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT |  | 9 | 9 | 966 |  | 0.018448 | 0.018448 |  | 0.018448 |  | 10.424 | 0.1923 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1954-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1954-11-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
2161_4 | coal | 458 |  | 2161 | James River Power Station | 4 | Unit_4_JRPS | Conventional Boiler | Wall firing - front firing | 60 | 600 | Filterable Particulate | 0.019434 | lb/MMBtu | ERT |  | 3 | 3 | 2135 |  | 0.019434 | 0.019434 |  | 0.019434 |  | 10 | 0.19434 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-08-01
709_2 | coal | 459 |  | 709 | Harllee Branch | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 332 | 3091.725 | Filterable Particulate | 0.020999 | lb/MMBtu | Part II | Unit 1&2 PM Emissions Test (June 15, 2005) | 3 | 0 |  |  | 0.020999 | 0.020999 |  | 0.020999 |  | 9.3124 | 0.19555
136_2 | coal | 460 |  | 136 | Seminole Generating Station | 2 | Unit 2 | Conventional Boiler | Wall firing - opposed firing | 694 | 7172 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | Multi-Pollutant Test Report 2009 (Unit 2) | 3 | 3 |  |  | 0.019 | 0.019 |  | 0.019 |  | 10.3343 | 0.19635 | NOx control | Selective Catalytic Reduction | 2009-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-12-01 | Other control | Dry sorbent injection | 2009-04-01 | SO2 control | Wet FGD - Spray Type | 1984-12-01
995_8 | coal | 461 |  | 995 | Bailly | 8 | 8 | Conventional Boiler | Cyclone firing | 352 | 3374 | Filterable Particulate | 0.020491 | lb/MMBtu | Part II | BGS U#7/8 M5 06/27/2006 | 1 | 1 |  |  |  | 0.020491 |  | 0.020491 |  | 9.5852 | 0.19641
3152_2A | coal | 462 |  | 3152 | Sunbury Generation LP | 2A | Boiler 2A | Conventional Boiler | Arch firing | 40 | 525 | Filterable Particulate | 0.014996 | lb/MMBtu | Part II | PM_012709 | 3 | 3 |  |  | 0.014996 | 0.014996 |  | 0.014996 |  | 13.125 | 0.19682 | PM control | Fabric Filter, reverse air | 1970-06-01
3948_1 | coal | 463 |  | 3948 | Mitchell | 1 | MI-1 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | Filterable Particulate | 0.023 | lb/MMBtu | Part II | April2009PM | 1 | 0 |  |  |  | 0.023 |  | 0.023 |  | 8.5998 | 0.19779
6096_NC1 | coal | 464 |  | 6096 | Nebraska City | NC1 | NC1 | Conventional Boiler | Wall firing - front firing | 646 | 6554.962 | Filterable Particulate | 0.0195 | lb/MMBtu | Part II | PM NC Unit 1 | 1 | 0 |  |  |  | 0.0195 |  | 0.0195 |  | 10.147 | 0.19787
68029_BLR1 | coal | 465 |  | 68029 | AES Puerto Rico Cogeneration Facility | BLR1 | Unit_1 | Fluidized bed firing | Fluidized bed firing | 255 | 2461.4 | Filterable Particulate | 0.020522 | lb/MMBtu | ERT |  | 6 | 6 | 2027 |  | 0.020522 | 0.020522 |  | 0.020522 |  | 9.6525 | 0.19809 | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Spray Dryer |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
709_1 | coal | 466 |  | 709 | Harllee Branch | 1 | Unit 1 | Conventional Boiler | Cell burner | 267 | 2542.694 | Filterable Particulate | 0.020999 | lb/MMBtu | Part II | Unit 1&2 PM Emissions Test (June 15, 2005) | 3 | 0 |  |  | 0.020999 | 0.020999 |  | 0.020999 |  | 9.5232 | 0.19998
6254_1 | coal | 467 |  | 6254 | Ottumwa | 1 | Unit 1 | Conventional Boiler | Tangential firing | 765.1 | 7990 | Filterable Particulate | 0.0193 | lb/MMBtu | Part II | OGS1-PM-20060615 | 1 | 1 |  |  |  | 0.0193 |  | 0.0193 |  | 10.4431 | 0.20155 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1981-05-01
3280_CAN2 | coal | 468 |  | 3280 | Canadys Steam | CAN2 | CAN002 | Conventional Boiler | Tangential firing | 123 | 1175.7 | Filterable Particulate | 0.0211 | lb/MMBtu | Part II | PM-03/06-CAN2 | 1 | 0 |  |  |  | 0.0211 |  | 0.0211 |  | 9.5585 | 0.20169 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-12-01
3938_41 | coal | 469 |  | 3938 | Philip Sporn | 41 | SP-4 | Conventional Boiler | Vertical firing | 152.5 | 1311 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | Feb2009PM | 1 | 0 |  |  |  | 0.0235 |  | 0.0235 |  | 8.5967 | 0.20202
3938_31 | coal | 470 |  | 3938 | Philip Sporn | 31 | SP-3 | Conventional Boiler | Vertical firing | 152.5 | 1311 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | Feb2009PM | 1 | 0 |  |  |  | 0.0235 |  | 0.0235 |  | 8.5967 | 0.20202
1731_1 | coal | 471 |  | 1731 | Harbor Beach Power Plant | 1 | HB1-Config | Conventional Boiler | Wall firing - front firing | 110 | 1181 | Filterable Particulate | 0.018913 | lb/MMBtu | Part II | PM2005_NovB | 1 | 0 |  |  | 0.018913 | 0.018913 |  | 0.018913 |  | 10.7364 | 0.20306
10075_1 | coal | 472 |  | 10075 | Taconite Harbor Energy Center | 1 | THEC1 | Conventional Boiler | Tangential firing | 83 | 847 | Filterable Particulate | 0.020079 | lb/MMBtu | ERT |  | 6 | 6 | 1735 |  | 0.020079 | 0.020079 |  | 0.020079 |  | 10.2048 | 0.2049 | NOx control | Selective Noncatalytic Reduction | 2008-01-01 | Other control | Dry sorbent injection | 2008-01-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2008-01-01
2836_10 | coal | 473 |  | 2836 | Avon Lake | 10 | AL10 | Conventional Boiler | Tangential firing | 101 | 1447 | Filterable Particulate | 0.014333 | lb/MMBtu | Part II | AL-15 | 3 | 2 |  |  | 0.014333 | 0.014333 |  | 0.014333 |  | 14.3267 | 0.20535 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
3393_2 | coal | 474 |  | 3393 | Allen Steam Plant | 2 | 2 | Conventional Boiler | Cyclone firing | 330 | 3064 | Filterable Particulate | 0.022333 | lb/MMBtu | Part II | ALF2 - 2006 | 3 | 3 |  |  | 0.022333 | 0.022333 |  | 0.022333 |  | 9.2848 | 0.20736
2850_B001 | coal | 475 |  | 2850 | J M Stuart | B001 | MS1W | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | Filterable Particulate | 0.022333 | lb/MMBtu | Part II | U1PM2009 | 3 | 3 |  |  | 0.022333 | 0.022333 |  | 0.022333 |  | 9.3098 | 0.20792
2104_3 | coal | 476 |  | 2104 | Meramec | 3 | 003 | Conventional Boiler | Wall firing - unspecified | 282 | 3172 | Filterable Particulate | 0.0185 | lb/MMBtu | Part II | 3 | 1 | 0 |  |  |  | 0.0185 |  | 0.0185 |  | 11.2482 | 0.20809
4072_7 | coal | 477 |  | 4072 | Pulliam | 7 | 7 | Conventional Boiler | Wall firing - rear firing | 87.7 | 999 | Filterable Particulate | 0.018333 | lb/MMBtu | Part II | P7 PM 2008 | 3 | 3 |  |  | 0.018333 | 0.018333 |  | 0.018333 |  | 11.3911 | 0.20884 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1958-11-01
6064_N1 | coal | 478 |  | 6064 | Nearman Creek | N1 | N1 | Conventional Boiler | Wall firing - front firing | 257.4 | 2433 | Filterable Particulate | 0.0223 | lb/MMBtu | Part II | PM Test Report | 3 | 3 |  |  | 0.0223 | 0.0223 |  | 0.0223 |  | 9.4522 | 0.21078
3_1 | coal | 479 |  | 3 | Barry | 1 | Unit 1 | Conventional Boiler | Tangential firing | 145 | 1380.8842 | Filterable Particulate | 0.022297 | lb/MMBtu | Part II | Unit 1 PM Emissions Test (June 2, 2009) | 3 | 0 |  |  | 0.022297 | 0.022297 |  | 0.022297 |  | 9.5233 | 0.21234
56_3 | coal | 480 |  | 56 | Charles R. Lowman | 3 | 3D | Conventional Boiler | Wall firing - opposed firing | 258 | 2500 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 2009 PM Test - 3 | 1 | 1 |  |  |  | 0.022 |  | 0.022 |  | 9.6899 | 0.21318
2708_5 | coal | 481 |  | 2708 | Cape Fear Steam Electric Plant | 5 | Cap_Cfg_5b | Conventional Boiler | Tangential firing | 153 | 1242 | Filterable Particulate | 0.026504 | lb/MMBtu | ERT |  | 6 | 6 | 981 |  | 0.026504 | 0.026504 |  | 0.026504 |  | 8.1176 | 0.21515 | NOx control | Selective Noncatalytic Reduction | 2006-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-11-01
6095_1 | coal | 482 |  | 6095 | Sooner | 1 | SO1 Config | Conventional Boiler | Tangential firing | 401 | 5428.8091 | Filterable Particulate | 0.016 | lb/MMBtu | Part II | Stack Sampling Report\Sooner 1 | 1 | 1 |  |  |  | 0.016 |  | 0.016 |  | 13.5382 | 0.21661
26_1 | coal | 483 |  | 26 | E. C. Gaston | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 270 | 2430.2362 | Filterable Particulate | 0.024086 | lb/MMBtu | Part II | Unit 1 Particulate Emissions Test (May 12, 2005) | 3 | 0 |  |  | 0.024086 | 0.024086 |  | 0.024086 |  | 9.0009 | 0.2168
663_B-2 | coal | 484 |  | 663 | Deerhaven Generating Station | B-2 | 001 | Conventional Boiler | Wall firing - unspecified | 235 | 2428 | Filterable Particulate | 0.021 | lb/MMBtu | Part II | 5 | 1 | 0 |  |  |  | 0.021 |  | 0.021 |  | 10.3319 | 0.21697
6068_2 | coal | 485 |  | 6068 | Jeffrey Energy Center | 2 | 2 | Conventional Boiler | Tangential firing | 786 | 8124 | Filterable Particulate | 0.021067 | lb/MMBtu | Part II | PM 0707/2 | 3 | 1 |  |  | 0.021067 | 0.021067 |  | 0.021067 |  | 10.3359 | 0.21774
51_24641 | coal | 486 |  | 51 | Dolet Hills | 24641 | 001 | Conventional Boiler | Wall firing - opposed firing | 723 | 7546 | Filterable Particulate | 0.020974 | lb/MMBtu | Part II | Stack Compliance Test DHPS | 3 | 0 |  |  | 0.020974 | 0.020974 |  | 0.020974 |  | 10.4371 | 0.2189
6250_1B | coal | 487 |  | 6250 | Mayo Electric Generating Facility | 1B | May_Cfg_1b | Conventional Boiler | Wall firing - opposed firing | 396 | 3743 | Filterable Particulate | 0.023333 | lb/MMBtu | Part II | May_Unit_1_Test_6h | 3 | 3 |  |  | 0.023333 | 0.023333 |  | 0.023333 |  | 9.452 | 0.22055
6250_1A | coal | 488 |  | 6250 | Mayo Electric Generating Facility | 1A | May_Cfg_1b | Conventional Boiler | Wall firing - opposed firing | 396 | 3743 | Filterable Particulate | 0.023333 | lb/MMBtu | Part II | May_Unit_1_Test_6h | 3 | 3 |  |  | 0.023333 | 0.023333 |  | 0.023333 |  | 9.452 | 0.22055
6095_2 | coal | 489 |  | 6095 | Sooner | 2 | SO2 Config | Conventional Boiler | Tangential firing | 383 | 5661.8362 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | Stack Sampling Report\Sooner 2 | 1 | 1 |  |  |  | 0.015 |  | 0.015 |  | 14.7829 | 0.22174
2848_H-6 | coal | 490 |  | 2848 | O H Hutchings | H-6 | H-6 | Conventional Boiler | Tangential firing | 60.5 | 646 | Filterable Particulate | 0.021 | lb/MMBtu | Part II | 2005 H-6 | 3 | 3 |  |  | 0.021 | 0.021 |  | 0.021 |  | 10.6777 | 0.22423 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
6076_3 | coal | 491 |  | 6076 | Colstrip | 3 | Unit3 | Conventional Boiler | Tangential firing | 805 | 7573 | Filterable Particulate | 0.024066 | lb/MMBtu | ERT |  | 6 | 6 | 1558 |  | 0.024066 | 0.024066 |  | 0.024066 |  | 9.4075 | 0.2264 | Other control | Activated carbon injection | 2009-12-01 | SO2 control | Wet FGD - Venturi Type | 1984-01-01 | PM control | PM scrubber - Venturi | 1984-01-01
2103_4 | coal | 492 |  | 2103 | Labadie | 4 | 004 | Conventional Boiler | Tangential firing | 633 | 6107 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 6 | 1 | 0 |  |  |  | 0.0235 |  | 0.0235 |  | 9.6477 | 0.22672
7253_3 | coal | 493 |  | 7253 | Richard Gorsuch | 3 | UNIT3 | Conventional Boiler | Radiant | 53.3 | 553 | Filterable Particulate | 0.021855 | lb/MMBtu | ERT |  | 6 | 6 | 1906 |  | 0.021855 | 0.021855 |  | 0.021855 |  | 10.3752 | 0.22675 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-06-01
3181_33 | coal | 494 |  | 3181 | Mitchell Power Station | 33 | 033 | Conventional Boiler | Tangential firing | 289 | 2563 | Filterable Particulate | 0.026 | lb/MMBtu | Part II | 1 | 3 | 3 |  |  | 0.026 | 0.026 |  | 0.026 |  | 8.8685 | 0.23058 | PM control | Electrostatic precipitator, cold side, unspecified | 1971-01-01 | SO2 control | Wet FGD - Spray Type | 1983-01-01
3098_2 | coal | 495 |  | 3098 | Elrama Power Plant | 2 | ELR2-2 | Conventional Boiler | Vertical firing | 100 | 1254 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT |  | 9 | 9 | 966 |  | 0.018448 | 0.018448 |  | 0.018448 |  | 12.54 | 0.23134 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1953-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1953-03-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
3098_1 | coal | 496 |  | 3098 | Elrama Power Plant | 1 | ELR1-2 | Conventional Boiler | Vertical firing | 100 | 1254 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT |  | 9 | 9 | 966 |  | 0.018448 | 0.018448 |  | 0.018448 |  | 12.54 | 0.23134 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1952-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1952-06-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
2732_7 | coal | 497 |  | 2732 | Riverbend | 7 | 7 | Conventional Boiler | Tangential firing | 99.5 | 1059 | Filterable Particulate | 0.021767 | lb/MMBtu | Part II | BLR7(2/12/08) | 3 | 0 |  |  | 0.021767 | 0.021767 |  | 0.021767 |  | 10.6432 | 0.23167 | NOx control | Selective Noncatalytic Reduction | 2007-02-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1995-01-01
2848_H-4 | coal | 498 |  | 2848 | O H Hutchings | H-4 | H-4 | Conventional Boiler | Tangential firing | 64 | 696 | Filterable Particulate | 0.021333 | lb/MMBtu | Part II | 2007 H-4 | 3 | 3 |  |  | 0.021333 | 0.021333 |  | 0.021333 |  | 10.875 | 0.232 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2732_8 | coal | 499 |  | 2732 | Riverbend | 8 | 8 | Conventional Boiler | Tangential firing | 100 | 1059 | Filterable Particulate | 0.021967 | lb/MMBtu | Part II | BLR8(2/25/09) | 3 | 0 |  |  | 0.021967 | 0.021967 |  | 0.021967 |  | 10.59 | 0.23263
4072_6 | coal | 500 |  | 4072 | Pulliam | 6 | 6 | Conventional Boiler | Wall firing - rear firing | 73.7 | 875 | Filterable Particulate | 0.019667 | lb/MMBtu | Part II | P5 PM 2008 | 3 | 3 |  |  | 0.019667 | 0.019667 |  | 0.019667 |  | 11.8725 | 0.23349 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1951-11-01
54755_BLR2 | coal | 501 |  | 54755 | Roanoke Valley II | BLR2 | Boiler 2 | Conventional Boiler | Wall firing - front firing | 50 | 560 | Filterable Particulate | 0.021314 | lb/MMBtu | ERT |  | 6 | 6 | 2021 |  | 0.021314 | 0.021314 |  | 0.021314 |  | 11.2 | 0.23871 | NOx control | Selective Noncatalytic Reduction | 1995-06-01 | SO2 control | Dry FGD - Spray Dryer | 1995-06-01 | PM control | Fabric Filter, pulse | 1995-06-01
7253_4 | coal | 502 |  | 7253 | Richard Gorsuch | 4 | UNIT4 | Conventional Boiler | Radiant | 53.3 | 519 | Filterable Particulate | 0.024667 | lb/MMBtu | Part II | Particulate2008(1,2,4) | 3 | 3 |  |  | 0.024667 | 0.024667 |  | 0.024667 |  | 9.7373 | 0.24019
628_1 | coal | 503 |  | 628 | Crystal River Power Plant | 1 | CryR_Cfg_1 | Conventional Boiler | Tangential firing | 400 | 3837 | Filterable Particulate | 0.025133 | lb/MMBtu | Part II | CryR_Blr_1_Test_4 | 3 | 3 |  |  | 0.025133 | 0.025133 |  | 0.025133 |  | 9.5925 | 0.24109 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
2850_B003 | coal | 504 |  | 2850 | J M Stuart | B003 | MS3W | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | Filterable Particulate | 0.025967 | lb/MMBtu | Part II | U3PM2009 | 3 | 3 |  |  | 0.025967 | 0.025967 |  | 0.025967 |  | 9.3098 | 0.24174
887_1 | coal | 505 |  | 887 | Joppa Steam | 1 | 1 | Conventional Boiler | Tangential firing | 183.3 | 1800 | Filterable Particulate | 0.024659 | lb/MMBtu | ERT |  | 6 | 6 | 2097 |  | 0.024659 | 0.024659 |  | 0.024659 |  | 9.82 | 0.24215 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-01-01
889_Unit 3 | coal | 506 |  | 889 | Baldwin Energy Complex | Unit 3 | 003 | Conventional Boiler | Tangential firing | 622 | 6031 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 15 | 1 | 0 |  |  |  | 0.025 |  | 0.025 |  | 9.6961 | 0.2424
1904_4 | coal | 507 |  | 1904 | Black Dog | 4 | Boiler 4 | Conventional Boiler | Wall firing - front firing | 178 | 1735 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | Boiler 3 & 4 PM 2008 | 1 | 1 |  |  |  | 0.025 |  | 0.025 |  | 9.7472 | 0.24368
6113_5 | coal | 508 |  | 6113 | Gibson | 5 | 5 | Conventional Boiler | Wall firing - opposed firing | 661 | 6655 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | UNIT5(10/6/09) | 3 | 0 |  |  | 0.024333 | 0.024333 |  | 0.024333 |  | 10.0681 | 0.24499
8_6 | coal | 509 |  | 8 | Gorgas | 6 | Unit 6 | Conventional Boiler | Wall firing - front firing | 110 | 1291.846 | Filterable Particulate | 0.020867 | lb/MMBtu | Part II | Unit 6 Particulate Emissions Test (July 1, 2009) | 3 | 0 |  |  | 0.020867 | 0.020867 |  | 0.020867 |  | 11.7441 | 0.24506
3178_2 | coal | 510 |  | 3178 | Armstrong Power Station | 2 | Unit 2 | Conventional Boiler | Wall firing - unspecified | 183 | 1706 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 06092009 | 3 | 3 |  |  | 0.026333 | 0.026333 |  | 0.026333 |  | 9.3224 | 0.24549
2952_5 | coal | 511 |  | 2952 | Muskogee | 5 | MK5 Config | Conventional Boiler | Tangential firing | 415 | 5373.0016 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | Stack Sampling Report\ Muskogee 5 | 1 | 1 |  |  |  | 0.019 |  | 0.019 |  | 12.947 | 0.24599
1831_EUBoiler4 | coal | 512 |  | 1831 | Otto E. Eckert Station | EUBoiler4 | 004 | Conventional Boiler | Wall firing - front firing | 72 | 807 | Filterable Particulate | 0.021967 | lb/MMBtu | Part II | PM-4-9/05 | 3 | 0 |  |  | 0.021967 | 0.021967 |  | 0.021967 |  | 11.2083 | 0.24621 | PM control | Electrostatic precipitator, unspecified | 1976-01-01
2720_Boiler 6 | coal | 513 |  | 2720 | Buck | Boiler 6 | 6 | Conventional Boiler | Tangential firing | 40 | 619 | Filterable Particulate | 0.016214 | lb/MMBtu | Part II | BLR6(2/28/07) | 7 | 0 |  |  | 0.016214 | 0.016214 |  | 0.016214 |  | 15.475 | 0.25092
994_3 | coal | 514 |  | 994 | AES Petersburg | 3 | 3ss | Conventional Boiler | Tangential firing | 580 | 5540 | Filterable Particulate | 0.0265 | lb/MMBtu | Part II | Unit 3 - PM 07/2005 | 2 | 2 |  |  | 0.0265 | 0.0265 |  | 0.0265 |  | 9.5517 | 0.25312 | NOx control | Selective Catalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1977-12-01 | SO2 control | Wet FGD - Spray Type | 1977-12-01
1295_1 | coal | 515 |  | 1295 | Quindaro | 1 | Unit 1 | Conventional Boiler | Cyclone firing | 77 | 782 | Filterable Particulate | 0.024933 | lb/MMBtu | Part II | PM Testing August 2009 | 3 | 3 |  |  | 0.024933 | 0.024933 |  | 0.024933 |  | 10.1558 | 0.25322
7_1 | coal | 516 |  | 7 | Gadsden | 1 | Unit 1 | Conventional Boiler | Tangential firing | 68 | 792.0615 | Filterable Particulate | 0.021762 | lb/MMBtu | Part II | Unit 1 PM Emissions Test (August 17, 2006) | 3 | 0 |  |  | 0.021762 | 0.021762 |  | 0.021762 |  | 11.648 | 0.25348
6138_1 | coal | 517 |  | 6138 | Flint Creek | 1 | FC-1 | Conventional Boiler | Wall firing - opposed firing | 558 | 6324 | Filterable Particulate | 0.0224 | lb/MMBtu | Part II | March2006PM&CO | 1 | 0 |  |  |  | 0.0224 |  | 0.0224 |  | 11.3333 | 0.25387
4072_5 | coal | 518 |  | 4072 | Pulliam | 5 | 5 | Conventional Boiler | Wall firing - rear firing | 53.63 | 693 | Filterable Particulate | 0.019667 | lb/MMBtu | Part II | P5 PM 2008 | 3 | 3 |  |  | 0.019667 | 0.019667 |  | 0.019667 |  | 12.9219 | 0.25413 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1953-01-01
1379_9 | coal | 519 |  | 1379 | Shawnee | 9 | 9 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | SHF6-9 - 04/20/2007 | 3 | 3 |  |  | 0.026333 | 0.026333 |  | 0.026333 |  | 9.6629 | 0.25446
1379_8 | coal | 520 |  | 1379 | Shawnee | 8 | 8 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | SHF6-9 - 04/20/2007 | 3 | 3 |  |  | 0.026333 | 0.026333 |  | 0.026333 |  | 9.6629 | 0.25446
1379_7 | coal | 521 |  | 1379 | Shawnee | 7 | 7 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | SHF6-9 - 04/20/2007 | 3 | 3 |  |  | 0.026333 | 0.026333 |  | 0.026333 |  | 9.6629 | 0.25446
1379_6 | coal | 522 |  | 1379 | Shawnee | 6 | 6 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | SHF6-9 - 04/20/2007 | 3 | 3 |  |  | 0.026333 | 0.026333 |  | 0.026333 |  | 9.6629 | 0.25446
1904_3 | coal | 523 |  | 1904 | Black Dog | 3 | Boiler 3 | Conventional Boiler | Wall firing - front firing | 96 | 985 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | Boiler 3 & 4 PM 2008 | 1 | 1 |  |  |  | 0.025 |  | 0.025 |  | 10.2604 | 0.25651
2840_6 | coal | 524 |  | 2840 | Conesville | 6 | CV-6 | Conventional Boiler | Tangential firing | 443.9 | 4091 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | Oct2005PM | 1 | 0 |  |  |  | 0.028 |  | 0.028 |  | 9.216 | 0.25805
2840_5 | coal | 525 |  | 2840 | Conesville | 5 | CV-5 | Conventional Boiler | Tangential firing | 443.9 | 4091 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | Oct2005PM | 1 | 0 |  |  |  | 0.028 |  | 0.028 |  | 9.216 | 0.25805
2952_4 | coal | 526 |  | 2952 | Muskogee | 4 | MK4 Config | Conventional Boiler | Tangential firing | 391 | 5360.25 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | Stack Sampling Report\ Muskogee 4 | 1 | 1 |  |  |  | 0.019 |  | 0.019 |  | 13.7091 | 0.26047
2876_2 | coal | 527 |  | 2876 | Kyger Creek | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 213 | 2135.931 | Filterable Particulate | 0.0261 | lb/MMBtu | Part II | Unit2Particulate2007 | 1 | 1 |  |  |  | 0.0261 |  | 0.0261 |  | 10.0278 | 0.26173
7253_2 | coal | 528 |  | 7253 | Richard Gorsuch | 2 | UNIT2 | Conventional Boiler | Radiant | 53.3 | 550.9 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | Particulate2008(1,2,4) | 3 | 3 |  |  | 0.025333 | 0.025333 |  | 0.025333 |  | 10.3358 | 0.26184
1077_1 | coal | 529 |  | 1077 | Sutherland | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 31 | 401.5 | Filterable Particulate | 0.0203 | lb/MMBtu | Part II | SUTH1-PM-20060516 | 1 | 1 |  |  |  | 0.0203 |  | 0.0203 |  | 12.9516 | 0.26292 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-11-01
733_2 | coal | 530 |  | 733 | Kraft | 2 | Unit 2 | Conventional Boiler | Tangential firing | 54 | 532.584 | Filterable Particulate | 0.027064 | lb/MMBtu | Part II | Unit 2 PM Emissions Test (September 20, 2006) | 3 | 0 |  |  | 0.027064 | 0.027064 |  | 0.027064 |  | 9.8627 | 0.26693
1831_EUBoiler1 | coal | 531 |  | 1831 | Otto E. Eckert Station | EUBoiler1 | 001 | Conventional Boiler | Wall firing - front firing | 40 | 509 | Filterable Particulate | 0.021133 | lb/MMBtu | Part II | PM-1-9/05 | 3 | 0 |  |  | 0.021133 | 0.021133 |  | 0.021133 |  | 12.725 | 0.26892 | PM control | Electrostatic precipitator, unspecified | 1978-01-01
6257_4 | coal | 532 |  | 6257 | Scherer | 4 | Unit 4 | Conventional Boiler | Tangential firing | 880 | 8821.5854 | Filterable Particulate | 0.02687 | lb/MMBtu | Part II | Unit 4 PM Emissions Test (January 5, 2010) | 3 | 0 |  |  | 0.02687 | 0.02687 |  | 0.02687 |  | 10.0245 | 0.26936
54035_BLR1 | coal | 533 |  | 54035 | Roanoke Valley I | BLR1 | Boiler 1 | Conventional Boiler | Wall firing - front firing | 182 | 1700 | Filterable Particulate | 0.028971 | lb/MMBtu | ERT |  | 4 | 4 | 2022 |  | 0.028971 | 0.028971 |  | 0.028971 |  | 9.3407 | 0.27061 | SO2 control | Dry FGD - Spray Dryer | 1994-05-01 | PM control | Fabric Filter, reverse air | 1994-05-01
6004_1 | coal | 534 |  | 6004 | Pleasants Power Station | 1 | 001 | Conventional Boiler | Wall firing - unspecified | 700 | 5969 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 7 | 1 | 1 |  |  | 0.032 | 0.032 |  | 0.032 |  | 8.5271 | 0.27287
3179_1 | coal | 535 |  | 3179 | Hatfield's Ferry Power Station | 1 | 001 | Conventional Boiler | Wall firing - opposed firing | 590 | 5700 | Filterable Particulate | 0.028667 | lb/MMBtu | Part II | PM-CO-VOC-11/09-1 | 3 | 0 |  |  | 0.028667 | 0.028667 |  | 0.028667 |  | 9.661 | 0.27695 | PM control | Electrostatic precipitator, cold side, unspecified | 1969-01-01 | SO2 control | Wet FGD - Spray Type | 2009-06-01
1363_6 | coal | 536 |  | 1363 | Cane Run | 6 | CR6 | Conventional Boiler | Tangential firing | 261 | 3017 | Filterable Particulate | 0.024 | lb/MMBtu | Part II | CR6-PM-2009 | 1 | 1 |  |  |  | 0.024 |  | 0.024 |  | 11.5594 | 0.27743
1695_4 | coal | 537 |  | 1695 | B.C. Cobb | 4 | BCCobb4-Conf | Conventional Boiler | Tangential firing | 167 | 1656 | Filterable Particulate | 0.028133 | lb/MMBtu | Part II | BCC4 - 2006 PM Testing | 3 | 3 |  |  | 0.028133 | 0.028133 |  | 0.028133 |  | 9.9162 | 0.27897
884_4 | coal | 538 |  | 884 | Will County | 4 | WC4CONFIG | Conventional Boiler | Tangential firing | 542 | 5254.53 | Filterable Particulate | 0.028842 | lb/MMBtu | ERT |  | 6 | 6 | 2011 |  | 0.028842 | 0.028842 |  | 0.028842 |  | 9.6947 | 0.27961 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1963-06-01
3406_4 | coal | 539 |  | 3406 | Johnsonville | 4 | 4 | Conventional Boiler | Tangential firing | 125 | 1405 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | JOF1-10 - 2009 | 3 | 3 |  |  | 0.025333 | 0.025333 |  | 0.025333 |  | 11.24 | 0.28475
3406_2 | coal | 540 |  | 3406 | Johnsonville | 2 | 2 | Conventional Boiler | Tangential firing | 125 | 1405 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | JOF1-10 - 2009 | 3 | 3 |  |  | 0.025333 | 0.025333 |  | 0.025333 |  | 11.24 | 0.28475
2103_3 | coal | 541 |  | 2103 | Labadie | 3 | 003 | Conventional Boiler | Tangential firing | 633 | 6107 | Filterable Particulate | 0.0298 | lb/MMBtu | Part II | 5 | 1 | 0 |  |  |  | 0.0298 |  | 0.0298 |  | 9.6477 | 0.2875
1295_2 | coal | 542 |  | 1295 | Quindaro | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 119.8 | 1394 | Filterable Particulate | 0.024767 | lb/MMBtu | Part II | PM Testing August 2009 | 3 | 3 |  |  | 0.024767 | 0.024767 |  | 0.024767 |  | 11.6361 | 0.28819 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1986-05-01
2291_NO4 | coal | 543 |  | 2291 | North Omaha | NO4 | NO4 | Conventional Boiler | Tangential firing | 138.2 | 1471.0008 | Filterable Particulate | 0.0272 | lb/MMBtu | Part II | PM Testing Unit 4 (NO4) | 1 | 0 |  |  |  | 0.0272 |  | 0.0272 |  | 10.644 | 0.28952
10771_10771-02 | coal | 544 |  | 10771 | Hopewell | 10771-02 | 1 & 2 | Conventional Boiler | Stoker - spreader | 34 | 433 | Filterable Particulate | 0.02308 | lb/MMBtu | ERT |  | 3 | 3 | 1532 |  | 0.02308 | 0.02308 |  | 0.02308 |  | 12.5735 | 0.2902 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01
10771_10771-01 | coal | 545 |  | 10771 | Hopewell | 10771-01 | 1 & 2 | Conventional Boiler | Stoker - spreader | 34 | 433 | Filterable Particulate | 0.02308 | lb/MMBtu | ERT |  | 3 | 3 | 1532 |  | 0.02308 | 0.02308 |  | 0.02308 |  | 12.5735 | 0.2902 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01
3264_3 | coal | 546 |  | 3264 | W. S. Lee | 3 | 3 | Conventional Boiler | Tangential firing | 182.1 | 2252 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | UNIT3(2/20/07) | 3 | 0 |  |  | 0.0235 | 0.0235 |  | 0.0235 |  | 12.3668 | 0.29062
2843_9 | coal | 547 |  | 2843 | Picway | 9 | PI | Conventional Boiler | Wall firing - front firing | 106.2 | 1290 | Filterable Particulate | 0.024 | lb/MMBtu | Part II | Sept2009PM2 | 1 | 0 |  |  |  | 0.024 |  | 0.024 |  | 12.1469 | 0.29153
2527_6 | coal | 548 |  | 2527 | AES Greenidge | 6 | Unit 4 | Conventional Boiler | Tangential firing | 112 | 1117 | Filterable Particulate | 0.029267 | lb/MMBtu | Part II | 2009 PM and H2SO4 | 3 | 3 |  |  | 0.029267 | 0.029267 |  | 0.029267 |  | 9.9732 | 0.29188 | NOx control | Selective Catalytic Reduction | 2007-05-01 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | Other control | Activated carbon injection | 2007-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-05-01 | PM control | Fabric Filter, pulse | 2006-11-01
2364_2 | coal | 549 |  | 2364 | Merrimack Station | 2 | mk2 | Conventional Boiler | Cyclone firing | 337 | 3017 | Filterable Particulate | 0.03321 | lb/MMBtu | ERT |  | 3 | 3 | 1809 |  | 0.03321 | 0.03321 |  | 0.03321 |  | 8.9525 | 0.29732 | NOx control | Selective Catalytic Reduction | 1995-05-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1999-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-05-01
709_4 | coal | 550 |  | 709 | Harllee Branch | 4 | Unit 4 | Conventional Boiler | Cell burner | 520 | 4874.298 | Filterable Particulate | 0.031733 | lb/MMBtu | Part II | Unit 3&4 PM Emissions Test (May 22, 2008) | 3 | 0 |  |  | 0.031733 | 0.031733 |  | 0.031733 |  | 9.3737 | 0.29746
709_3 | coal | 551 |  | 709 | Harllee Branch | 3 | Unit 3 | Conventional Boiler | Cell burner | 513 | 4825.829 | Filterable Particulate | 0.031733 | lb/MMBtu | Part II | Unit 3&4 PM Emissions Test (May 22, 2008) | 3 | 0 |  |  | 0.031733 | 0.031733 |  | 0.031733 |  | 9.4071 | 0.29852
1733_2 | coal | 552 |  | 1733 | Monroe Power Plant | 2 | MN2-Config | Conventional Boiler | Wall firing - opposed firing | 815 | 7140 | Filterable Particulate | 0.0345 | lb/MMBtu | Part II | PM2006_Mar_2 | 2 | 0 |  |  | 0.0345 | 0.0345 |  | 0.0345 |  | 8.7607 | 0.30225
2403_U2 | coal | 553 |  | 2403 | PSEG Hudson Generating Station | U2 | HUDU2E2PT2OS1-Coal | Conventional Boiler | Wall firing - opposed firing | 659.7 | 6600 | Filterable Particulate | 0.030333 | lb/MMBtu | Part II | EG07044 | 3 | 3 |  |  | 0.030333 | 0.030333 |  | 0.030333 |  | 10.0045 | 0.30347 | NOx control | Selective Noncatalytic Reduction | 1999-03-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-12-01
2723_3 | coal | 554 |  | 2723 | Dan River | 3 | 3 | Conventional Boiler | Tangential firing | 151 | 1710 | Filterable Particulate | 0.026867 | lb/MMBtu | Part II | UNIT3(4/9/08) | 3 | 0 |  |  | 0.026867 | 0.026867 |  | 0.026867 |  | 11.3245 | 0.30425
2103_2 | coal | 555 |  | 2103 | Labadie | 2 | 002 | Conventional Boiler | Tangential firing | 623 | 6183 | Filterable Particulate | 0.0308 | lb/MMBtu | Part II | 4 | 1 | 0 |  |  |  | 0.0308 |  | 0.0308 |  | 9.9246 | 0.30568
50_8 | coal | 556 |  | 50 | Widows Creek | 8 | 8 | Conventional Boiler | Tangential firing | 550 | 5839 | Filterable Particulate | 0.029 | lb/MMBtu | Part II | WCF8 - 2006 | 3 | 3 |  |  | 0.029 | 0.029 |  | 0.029 |  | 10.6164 | 0.30787
7_2 | coal | 557 |  | 7 | Gadsden | 2 | Unit 2 | Conventional Boiler | Tangential firing | 70 | 847.8367 | Filterable Particulate | 0.025443 | lb/MMBtu | Part II | Unit 2 PM Emissions Test (August 13, 2008) | 3 | 0 |  |  | 0.025443 | 0.025443 |  | 0.025443 |  | 12.112 | 0.30817
3251_1 | coal | 558 |  | 3251 | HB Robinson / Darlington Electric Power Plant | 1 | Rob_Cfg_1 | Conventional Boiler | Tangential firing | 187 | 1733 | Filterable Particulate | 0.033333 | lb/MMBtu | Part II | Rob_Blr_1_Test_6e | 3 | 3 |  |  | 0.033333 | 0.033333 |  | 0.033333 |  | 9.2674 | 0.30891 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-07-01
2848_H-3 | coal | 559 |  | 2848 | O H Hutchings | H-3 | H-3 | Conventional Boiler | Tangential firing | 62.5 | 716 | Filterable Particulate | 0.027 | lb/MMBtu | Part II | 2005 H-3 | 3 | 3 |  |  | 0.027 | 0.027 |  | 0.027 |  | 11.456 | 0.30931
2848_H-2 | coal | 560 |  | 2848 | O H Hutchings | H-2 | H-2 | Conventional Boiler | Tangential firing | 53 | 574 | Filterable Particulate | 0.028667 | lb/MMBtu | Part II | 2006 H-2 | 3 | 3 |  |  | 0.028667 | 0.028667 |  | 0.028667 |  | 10.8302 | 0.31047
1047_4 | coal | 561 |  | 1047 | Lansing | 4 | Unit 4 | Conventional Boiler | Turbo | 264.2 | 2626 | Filterable Particulate | 0.0313 | lb/MMBtu | Part II | LANS4-PM-20060502 | 1 | 1 |  |  |  | 0.0313 |  | 0.0313 |  | 9.9394 | 0.3111 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-04-01
54634_1 | coal | 562 |  | 54634 | St. Nicholas Cogen Project | 1 | 1 | Fluidized bed firing | Fluidized bed firing | 99.2 | 1300 | Filterable Particulate | 0.02389 | lb/MMBtu | Part II | Particulate | 3 | 3 |  |  | 0.02389 | 0.02389 |  | 0.02389 |  | 13.1048 | 0.31308 | PM control | Fabric Filter, pulse | 1990-09-01
628_2 | coal | 563 |  | 628 | Crystal River Power Plant | 2 | CryR_Cfg_2 | Conventional Boiler | Tangential firing | 515 | 4161 | Filterable Particulate | 0.038883 | lb/MMBtu | Part II | CryR_Blr_2_Test_2 | 6 | 6 |  |  | 0.038883 | 0.038883 |  | 0.038883 |  | 8.0796 | 0.31416
2876_3 | coal | 564 |  | 2876 | Kyger Creek | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 213 | 2138.101 | Filterable Particulate | 0.0313 | lb/MMBtu | Part II | Unit3Particulate2007 | 1 | 1 |  |  |  | 0.0313 |  | 0.0313 |  | 10.038 | 0.31419
983_5 | coal | 565 |  | 983 | Clifty Creek | 5 | Unit 5 | Conventional Boiler | Wall firing - front firing | 215 | 2176.51 | Filterable Particulate | 0.0312 | lb/MMBtu | Part II | Stack2Particulate2007 | 1 | 1 |  |  |  | 0.0312 |  | 0.0312 |  | 10.1233 | 0.31585
68029_BLR2 | coal | 566 |  | 68029 | AES Puerto Rico Cogeneration Facility | BLR2 | Unit_2 | Fluidized bed firing | Fluidized bed firing | 255 | 2461.4 | Filterable Particulate | 0.033002 | lb/MMBtu | ERT |  | 6 | 6 | 2028 |  | 0.033002 | 0.033002 |  | 0.033002 |  | 9.6525 | 0.31856 | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Spray Dryer |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
983_6 | coal | 567 |  | 983 | Clifty Creek | 6 | Unit 6 | Conventional Boiler | Wall firing - front firing | 215 | 2206.022 | Filterable Particulate | 0.0312 | lb/MMBtu | Part II | Stack2Particulate2007 | 1 | 1 |  |  |  | 0.0312 |  | 0.0312 |  | 10.2606 | 0.32013
1743_7 | coal | 568 |  | 1743 | St Clair Power Plant | 7 | SC7-Config | Conventional Boiler | Tangential firing | 465 | 4547 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | PM2007_Oct7 | 2 | 0 |  |  | 0.033 | 0.033 |  | 0.033 |  | 9.7785 | 0.32269
983_4 | coal | 569 |  | 983 | Clifty Creek | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 215 | 2224.467 | Filterable Particulate | 0.0312 | lb/MMBtu | Part II | Stack2Particulate2007 | 1 | 1 |  |  |  | 0.0312 |  | 0.0312 |  | 10.3464 | 0.32281
2713_3 | coal | 570 |  | 2713 | L.V. Sutton Electric Plant | 3 | Sut_Cfg_3b | Conventional Boiler | Wall firing - rear firing | 420 | 3695 | Filterable Particulate | 0.037 | lb/MMBtu | Part II | Sut_Blr_3_Test_3 | 3 | 3 |  |  | 0.037 | 0.037 |  | 0.037 |  | 8.7976 | 0.32551
1356_1 | coal | 571 |  | 1356 | Ghent | 1 | GH1 | Conventional Boiler | Tangential firing | 520 | 6286 | Filterable Particulate | 0.027 | lb/MMBtu | Part II | GH1-PM-2009 | 1 | 1 |  |  |  | 0.027 |  | 0.027 |  | 12.0885 | 0.32639
6052_2 | coal | 572 |  | 6052 | Wansley | 2 | Unit 2 | Conventional Boiler | Tangential firing | 920 | 8554.28 | Filterable Particulate | 0.035764 | lb/MMBtu | Part II | Unit 2 PM Test, FGD Stack (May 20, 2009) | 3 | 0 |  |  | 0.035764 | 0.035764 |  | 0.035764 |  | 9.2981 | 0.33254
2713_2 | coal | 573 |  | 2713 | L.V. Sutton Electric Plant | 2 | Sut_Cfg_1 | Conventional Boiler | Tangential firing | 103 | 1081 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | Sut_Blr_2_Test_6 | 3 | 3 |  |  | 0.033 | 0.033 |  | 0.033 |  | 10.1502 | 0.33496
2713_1 | coal | 574 |  | 2713 | L.V. Sutton Electric Plant | 1 | Sut_Cfg_1 | Conventional Boiler | Tangential firing | 103 | 1081 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | Sut_Blr_2_Test_6 | 3 | 3 |  |  | 0.033 | 0.033 |  | 0.033 |  | 10.1502 | 0.33496
1046_5 | coal | 575 |  | 1046 | Dubuque | 5 | Unit 5 | Conventional Boiler | Wall firing - front firing | 29.2 | 337.3 | Filterable Particulate | 0.029 | lb/MMBtu | Part II | DBQ5-PM-20051028 | 1 | 1 |  |  |  | 0.029 |  | 0.029 |  | 11.5514 | 0.33499 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-08-01
1364_4 | coal | 576 |  | 1364 | Mill Creek | 4 | MC4 | Conventional Boiler | Wall firing - opposed firing | 517 | 5805 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | MC4-PM-2005 | 1 | 1 |  |  |  | 0.03 |  | 0.03 |  | 11.2282 | 0.33685
10671_2b | coal | 577 |  | 10671 | AES Shady Point,LLC | 2b | Unit 2 | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | Stack Test 2008 | 8 | 4 |  |  | 0.024571 | 0.024571 |  | 0.024571 |  | 13.8804 | 0.34105 | PM control | Fabric Filter, pulse | 1991-01-01
10671_2a | coal | 578 |  | 10671 | AES Shady Point,LLC | 2a | Unit 2 | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | Stack Test 2008 | 8 | 4 |  |  | 0.024571 | 0.024571 |  | 0.024571 |  | 13.8804 | 0.34105 | PM control | Fabric Filter, pulse | 1991-01-01
10671_1b | coal | 579 |  | 10671 | AES Shady Point,LLC | 1b | Unit 1 | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | Stack Test 2008 | 8 | 4 |  |  | 0.024571 | 0.024571 |  | 0.024571 |  | 13.8804 | 0.34105 | PM control | Fabric Filter, pulse | 1991-01-01
10671_1A | coal | 580 |  | 10671 | AES Shady Point,LLC | 1A | Unit 1 | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | Stack Test 2008 | 8 | 4 |  |  | 0.024571 | 0.024571 |  | 0.024571 |  | 13.8804 | 0.34105 | PM control | Fabric Filter, pulse | 1991-01-01
50611_031 | coal | 581 |  | 50611 | WPS Westwood Generation, LLC | 031 | 001 | Fluidized bed firing | Fluidized bed firing | 36 | 615 | Filterable Particulate | 0.02 | lb/MMBtu | Part II | 2009 PM Test | 3 | 3 |  |  | 0.02 | 0.02 |  | 0.02 |  | 17.0833 | 0.34167 | PM control | Fabric Filter, pulse | 1987-12-01
1745_19 | coal | 582 |  | 1745 | Trenton Channel Power Plant | 19 | TC16-Config | Conventional Boiler | Tangential firing | 58 | 603 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | PM2008_JunHPc | 1 | 0 |  |  | 0.033 | 0.033 |  | 0.033 |  | 10.3966 | 0.34309
1745_18 | coal | 583 |  | 1745 | Trenton Channel Power Plant | 18 | TC16-Config | Conventional Boiler | Tangential firing | 58 | 603 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | PM2008_JunHPc | 1 | 0 |  |  | 0.033 | 0.033 |  | 0.033 |  | 10.3966 | 0.34309
1745_17 | coal | 584 |  | 1745 | Trenton Channel Power Plant | 17 | TC16-Config | Conventional Boiler | Tangential firing | 58 | 603 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | PM2008_JunHPc | 1 | 0 |  |  | 0.033 | 0.033 |  | 0.033 |  | 10.3966 | 0.34309
1745_16 | coal | 585 |  | 1745 | Trenton Channel Power Plant | 16 | TC16-Config | Conventional Boiler | Tangential firing | 58 | 603 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | PM2008_JunHPc | 1 | 0 |  |  | 0.033 | 0.033 |  | 0.033 |  | 10.3966 | 0.34309
4140_B5 | coal | 586 |  | 4140 | Alma | B5 | B5 | Conventional Boiler | Wall firing - unspecified | 83.5 | 862.65 | Filterable Particulate | 0.034 | lb/MMBtu | Part II | 1 | 3 | 0 |  |  | 0.034 | 0.034 |  | 0.034 |  | 10.3311 | 0.35126 | NOx control | Selective Noncatalytic Reduction |  | PM control | Electrostatic precipitator, cold side, unspecified | 1974-06-01
1363_4 | coal | 587 |  | 1363 | Cane Run | 4 | CR4 | Conventional Boiler | Wall firing - front firing | 168 | 2310 | Filterable Particulate | 0.025678 | lb/MMBtu | ERT |  | 3 | 3 | 1826 |  | 0.025678 | 0.025678 |  | 0.025678 |  | 13.75 | 0.35308 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1963-06-01 | SO2 control | Wet FGD - Spray Type | 1976-12-01
2049_4 | coal | 588 |  | 2049 | Jack Watson | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 250 | 2226.86 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | PM Reports (2008) | 1 | 0 |  |  |  | 0.04 |  | 0.04 |  | 8.9074 | 0.3563
2104_1 | coal | 589 |  | 2104 | Meramec | 1 | 001 | Conventional Boiler | Tangential firing | 128 | 1566 | Filterable Particulate | 0.0292 | lb/MMBtu | Part II | 1 | 1 | 0 |  |  |  | 0.0292 |  | 0.0292 |  | 12.2344 | 0.35724
1356_3 | coal | 590 |  | 1356 | Ghent | 3 | GH3 | Conventional Boiler | Wall firing - opposed firing | 525 | 5868 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | GH23-PM-2009 | 1 | 1 |  |  |  | 0.032 |  | 0.032 |  | 11.1771 | 0.35767
1356_2 | coal | 591 |  | 1356 | Ghent | 2 | GH2 | Conventional Boiler | Tangential firing | 510 | 5705 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | GH23-PM-2009 | 1 | 1 |  |  |  | 0.032 |  | 0.032 |  | 11.1863 | 0.35796
3113_2 | coal | 592 |  | 3113 | Portland | 2 | POR-2 | Conventional Boiler | Tangential firing | 255 | 2542 | Filterable Particulate | 0.035933 | lb/MMBtu | Part II | P-92-U2 | 3 | 3 |  |  | 0.035933 | 0.035933 |  | 0.035933 |  | 9.9686 | 0.35821 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1987-05-01
2876_5 | coal | 593 |  | 2876 | Kyger Creek | 5 | Unit 5 | Conventional Boiler | Wall firing - front firing | 213 | 2129.638 | Filterable Particulate | 0.0361 | lb/MMBtu | Part II | Unit5Particulate2007 | 1 | 1 |  |  |  | 0.0361 |  | 0.0361 |  | 9.9983 | 0.36094
3776_52 | coal | 594 |  | 3776 | Glen Lyn | 52 | GL-5 | Conventional Boiler | Tangential firing | 50 | 572 | Filterable Particulate | 0.0316 | lb/MMBtu | Part II | June2007PM | 1 | 0 |  |  |  | 0.0316 |  | 0.0316 |  | 11.44 | 0.3615
3776_51 | coal | 595 |  | 3776 | Glen Lyn | 51 | GL-5 | Conventional Boiler | Tangential firing | 50 | 572 | Filterable Particulate | 0.0316 | lb/MMBtu | Part II | June2007PM | 1 | 0 |  |  |  | 0.0316 |  | 0.0316 |  | 11.44 | 0.3615
4078_2 | coal | 596 |  | 4078 | Weston | 2 | W2 | Conventional Boiler | Wall firing - front firing | 88.9 | 1000 | Filterable Particulate | 0.032667 | lb/MMBtu | Part II | W2 PM 2009 | 3 | 3 |  |  | 0.032667 | 0.032667 |  | 0.032667 |  | 11.2486 | 0.36745 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-01-01
1720_7 | coal | 597 |  | 1720 | J.C. Weadock | 7 | JCW7-Conf | Conventional Boiler | Tangential firing | 166 | 1560 | Filterable Particulate | 0.039133 | lb/MMBtu | Part II | JCW7-2005 PM Testing | 3 | 3 |  |  | 0.039133 | 0.039133 |  | 0.039133 |  | 9.3976 | 0.36776
2840_3 | coal | 598 |  | 2840 | Conesville | 3 | CV-3 | Conventional Boiler | Wall firing - front firing | 165 | 1862 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | Dec2005PM | 1 | 0 |  |  |  | 0.033 |  | 0.033 |  | 11.2848 | 0.3724 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-01-01
8_7 | coal | 599 |  | 8 | Gorgas | 7 | Unit 7 | Conventional Boiler | Wall firing - front firing | 110 | 1218.3294 | Filterable Particulate | 0.03397 | lb/MMBtu | Part II | Unit 7 Particulate Emissions Test (July 1, 2009) | 3 | 0 |  |  | 0.03397 | 0.03397 |  | 0.03397 |  | 11.0757 | 0.37625
50974_#2 CFB Boiler | coal | 600 |  | 50974 | Scrubgrass Generating Company L.P. | #2 CFB Boiler | Gen 1 | Fluidized bed firing | Fluidized bed firing | 48.5 | 650 | Filterable Particulate | 0.029396 | lb/MMBtu | ERT |  | 3 | 3 | 10000000 |  | 0.029396 | 0.029396 |  | 0.029396 |  | 12.8866 | 0.37882 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01
50974_#1 CFB boiler | coal | 601 |  | 50974 | Scrubgrass Generating Company L.P. | #1 CFB boiler | Gen 1 | Fluidized bed firing | Fluidized bed firing | 48.5 | 650 | Filterable Particulate | 0.029396 | lb/MMBtu | ERT |  | 3 | 3 | 10000000 |  | 0.029396 | 0.029396 |  | 0.029396 |  | 12.8866 | 0.37882 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01
1364_3 | coal | 602 |  | 1364 | Mill Creek | 3 | MC3 | Conventional Boiler | Wall firing - opposed firing | 422 | 4896 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | MC3-PM-2006 | 1 | 1 |  |  |  | 0.033 |  | 0.033 |  | 11.6019 | 0.38286
995_7 | coal | 603 |  | 995 | Bailly | 7 | 7 | Conventional Boiler | Cyclone firing | 176 | 1638 | Filterable Particulate | 0.041243 | lb/MMBtu | Part II | BGS U#7&8 M5 09/30/2008 | 1 | 1 |  |  |  | 0.041243 |  | 0.041243 |  | 9.3068 | 0.38384
1082_2 | coal | 604 |  | 1082 | Walter Scott Jr. Energy Center | 2 | 2 | Conventional Boiler | Tangential firing | 94 | 935 | Filterable Particulate | 0.039081 | lb/MMBtu | Part II | 6/2006 PM2 | 1 | 0 |  |  |  | 0.039081 |  | 0.039081 |  | 9.9468 | 0.38874
710_MB2 | coal | 605 | Retired | 710 | Jack McDonough | MB2 | MB2 | Conventional Boiler | Tangential firing | 270 | 2488.472 | Filterable Particulate | 0.042205 | lb/MMBtu | Part II | Units 1&2 PM Emissions Test (February 21, 2007) | 3 | 0 |  |  | 0.042205 | 0.042205 |  | 0.042205 |  | 9.2166 | 0.38898
710_MB1 | coal | 606 |  | 710 | Jack McDonough | MB1 | MB1 | Conventional Boiler | Tangential firing | 270 | 2490.99 | Filterable Particulate | 0.042205 | lb/MMBtu | Part II | Units 1&2 PM Emissions Test (February 21, 2007) | 3 | 0 |  |  | 0.042205 | 0.042205 |  | 0.042205 |  | 9.2259 | 0.38937
2723_2 | coal | 607 |  | 2723 | Dan River | 2 | 2 | Conventional Boiler | Tangential firing | 70.4 | 1140 | Filterable Particulate | 0.024052 | lb/MMBtu | Part II | UNIT2(7/28/05) | 3 | 0 |  |  | 0.023767 | 0.024052 | Corrected | 0.024338 | Corrected | 16.1932 | 0.38948
2708_6 | coal | 608 |  | 2708 | Cape Fear Steam Electric Plant | 6 | Cap_Cfg_6b | Conventional Boiler | Tangential firing | 184 | 1752 | Filterable Particulate | 0.041333 | lb/MMBtu | Part II | Cap_Blr_6_Test_6 | 3 | 3 |  |  | 0.041333 | 0.041333 |  | 0.041333 |  | 9.5217 | 0.39357
2291_NO5 | coal | 609 |  | 2291 | North Omaha | NO5 | NO5 | Conventional Boiler | Wall firing - front firing | 224 | 2348.64 | Filterable Particulate | 0.0376 | lb/MMBtu | Part II | PM Testing Unit 5 (NO5) | 1 | 0 |  |  |  | 0.0376 |  | 0.0376 |  | 10.485 | 0.39424
4140_B4 | coal | 610 |  | 4140 | Alma | B4 | B4 | Conventional Boiler | Wall firing - unspecified | 53.63 | 557.2 | Filterable Particulate | 0.038 | lb/MMBtu | Part II | 2 | 3 | 0 |  |  | 0.038 | 0.038 |  | 0.038 |  | 10.3897 | 0.39481 | NOx control | Selective Noncatalytic Reduction |  | PM control | Electrostatic precipitator, cold side, unspecified | 1974-06-01
1720_8 | coal | 611 |  | 1720 | J.C. Weadock | 8 | JCW8-Conf | Conventional Boiler | Tangential firing | 166.5 | 1475 | Filterable Particulate | 0.044733 | lb/MMBtu | Part II | 2005-JCW8 PM Testing | 3 | 3 |  |  | 0.044733 | 0.044733 |  | 0.044733 |  | 8.8589 | 0.39629
1048_2 | coal | 612 |  | 1048 | ML Kapp | 2 | Unit 2 | Conventional Boiler | Tangential firing | 229 | 2332 | Filterable Particulate | 0.0391 | lb/MMBtu | Part II | KAPP2-PM-20060608 | 1 | 1 |  |  |  | 0.0391 |  | 0.0391 |  | 10.1834 | 0.39817 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-07-01
1218_2 | coal | 613 |  | 1218 | Fair Station | 2 | U2 | Conventional Boiler | Wall firing - front firing | 44 | 465 | Filterable Particulate | 0.038 | lb/MMBtu | Part II | TITLEVU209 | 1 | 1 |  |  |  | 0.038 |  | 0.038 |  | 10.5682 | 0.40159 | Other control | Other (specify): Flue gas conditioning for opacity control | 2006-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-10-01
1004_7-1 | coal | 614 |  | 1004 | Edwardsport | 7-1 | 7-1 | Conventional Boiler | Wall firing - front firing | 42.75 | 510 | Filterable Particulate | 0.033667 | lb/MMBtu | Part II | UNIT7-1(4/10/08) | 3 | 0 |  |  | 0.033667 | 0.033667 |  | 0.033667 |  | 11.9298 | 0.40164
2103_1 | coal | 615 |  | 2103 | Labadie | 1 | 001 | Conventional Boiler | Tangential firing | 630 | 6183 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 3 | 1 | 0 |  |  |  | 0.041 |  | 0.041 |  | 9.8143 | 0.40239
981_4 | coal | 616 |  | 981 | State Line | 4 | Unit 4 | Conventional Boiler | Cyclone firing | 344 | 3478 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | Unit4_2008 | 1 | 0 |  |  |  | 0.04 |  | 0.04 |  | 10.1105 | 0.40442
2709_3 | coal | 617 |  | 2709 | H.F. Lee Plant | 3 | Lee_Cfg_3b | Conventional Boiler | Wall firing - opposed firing | 260 | 2412 | Filterable Particulate | 0.044 | lb/MMBtu | Part II | Lee_Blr_3_Test_9 | 3 | 3 |  |  | 0.044 | 0.044 |  | 0.044 |  | 9.2769 | 0.40818
3115_2 | coal | 618 |  | 3115 | Titus | 2 | TI-2 | Conventional Boiler | Tangential firing | 86.2 | 900 | Filterable Particulate | 0.039109 | lb/MMBtu | Part II | T-51 | 4 | 4 |  |  | 0.03885 | 0.039109 | Corrected | 0.039369 | Corrected | 10.4408 | 0.40833 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-02-01
3405_1 | coal | 619 |  | 3405 | John Sevier | 1 | 1 | Conventional Boiler | Tangential firing | 200 | 1967 | Filterable Particulate | 0.041667 | lb/MMBtu | Part II | JSF1-2 - 2008 | 3 | 3 |  |  | 0.041667 | 0.041667 |  | 0.041667 |  | 9.835 | 0.40979
527_1 | coal | 620 |  | 527 | Nucla | 1 | 001 | Fluidized bed firing | Fluidized bed firing | 110 | 1032 | Filterable Particulate | 0.043795 | lb/MMBtu | ERT |  | 6 | 6 | 1310 |  | 0.043795 | 0.043795 |  | 0.043795 |  | 9.3818 | 0.41088 | NOx control | Selective Noncatalytic Reduction | 2006-07-01 | PM control | Fabric Filter, shake and deflate | 1987-06-01
2850_B004 | coal | 621 |  | 2850 | J M Stuart | B004 | MS4W | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | Filterable Particulate | 0.0444 | lb/MMBtu | Part II | U4PM2009 | 3 | 3 |  |  | 0.0444 | 0.0444 |  | 0.0444 |  | 9.3098 | 0.41335
2721_1 | coal | 622 | Retired | 2721 | Cliffside | 1 | 1 | Conventional Boiler | Tangential firing | 40.5 | 647 | Filterable Particulate | 0.026367 | lb/MMBtu | Part II | UNIT1(4/22/08) | 3 | 0 |  |  | 0.026367 | 0.026367 |  | 0.026367 |  | 15.9753 | 0.42122
3178_1 | coal | 623 |  | 3178 | Armstrong Power Station | 1 | Unit 1 | Conventional Boiler | Wall firing - unspecified | 184 | 1749 | Filterable Particulate | 0.044333 | lb/MMBtu | Part II | 02052010 | 3 | 3 |  |  | 0.044333 | 0.044333 |  | 0.044333 |  | 9.5054 | 0.42141
728_Y5BR | coal | 624 |  | 728 | Yates | Y5BR | Y5BR | Conventional Boiler | Tangential firing | 145 | 1440.692 | Filterable Particulate | 0.042441 | lb/MMBtu | Part II | Units 4&5 PM Emissions Test (February 28, 2007) | 3 | 0 |  |  | 0.042441 | 0.042441 |  | 0.042441 |  | 9.9358 | 0.42169
889_Unit 2 | coal | 625 |  | 889 | Baldwin Energy Complex | Unit 2 | 002 | Conventional Boiler | Cyclone firing | 628 | 5996 | Filterable Particulate | 0.045 | lb/MMBtu | Part II | 14 | 1 | 0 |  |  |  | 0.045 |  | 0.045 |  | 9.5478 | 0.42965
1943_002 | coal | 626 |  | 1943 | Hoot Lake | 002 | 2 | Conventional Boiler | Tangential firing | 60.7 | 747.2 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | Particulate Performance Test - Unit 2 | 3 | 3 |  |  | 0.035 | 0.035 |  | 0.035 |  | 12.3097 | 0.43084 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-06-01
864_5 | coal | 627 |  | 864 | Meredosia | 5 | 005 | Conventional Boiler | Tangential firing | 204 | 2784 | Filterable Particulate | 0.031807 | lb/MMBtu | ERT |  | 3 | 3 | 1154 |  | 0.031807 | 0.031807 |  | 0.031807 |  | 13.6471 | 0.43407 | Other control | Activated carbon injection | 2009-08-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1992-11-01
728_Y4BR | coal | 628 |  | 728 | Yates | Y4BR | Y4BR | Conventional Boiler | Tangential firing | 138 | 1421.82 | Filterable Particulate | 0.042441 | lb/MMBtu | Part II | Units 4&5 PM Emissions Test (February 28, 2007) | 3 | 0 |  |  | 0.042441 | 0.042441 |  | 0.042441 |  | 10.303 | 0.43727
1378_2 | coal | 629 |  | 1378 | Paradise | 2 | 2 | Conventional Boiler | Cyclone firing | 704 | 6959 | Filterable Particulate | 0.044333 | lb/MMBtu | Part II | PAF2 - 05/23/2007 | 3 | 3 |  |  | 0.044333 | 0.044333 |  | 0.044333 |  | 9.8849 | 0.43823
2709_2 | coal | 630 |  | 2709 | H.F. Lee Plant | 2 | Lee_Cfg_1 | Conventional Boiler | Tangential firing | 80 | 704 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | Lee_Blr_1_Test_2 | 3 | 3 |  |  | 0.047 | 0.047 |  | 0.047 |  | 9.4877 | 0.44592
2709_1 | coal | 631 |  | 2709 | H.F. Lee Plant | 1 | Lee_Cfg_1 | Conventional Boiler | Tangential firing | 80 | 704 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | Lee_Blr_1_Test_2 | 3 | 3 |  |  | 0.047 | 0.047 |  | 0.047 |  | 9.4877 | 0.44592
1378_1 | coal | 632 |  | 1378 | Paradise | 1 | 1 | Conventional Boiler | Cyclone firing | 704 | 6959 | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | PAF1 - 05/24/2007 | 3 | 3 |  |  | 0.045333 | 0.045333 |  | 0.045333 |  | 9.8849 | 0.44812
2723_1 | coal | 633 |  | 2723 | Dan River | 1 | 1 | Conventional Boiler | Tangential firing | 71 | 1140 | Filterable Particulate | 0.027967 | lb/MMBtu | Part II | UNIT1(7/18/06) | 3 | 0 |  |  | 0.027967 | 0.027967 |  | 0.027967 |  | 16.0563 | 0.44904
2876_1 | coal | 634 |  | 2876 | Kyger Creek | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 214 | 2111.41 | Filterable Particulate | 0.0463 | lb/MMBtu | Part II | Unit1Particulate2007 | 1 | 1 |  |  |  | 0.0463 |  | 0.0463 |  | 9.8664 | 0.45681
2872_4 | coal | 635 |  | 2872 | Muskingum River | 4 | MR-4 | Conventional Boiler | Cyclone firing | 237.5 | 2150 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | Nov2009PM | 1 | 0 |  |  |  | 0.0506 |  | 0.0506 |  | 9.0526 | 0.45806
2872_3 | coal | 636 |  | 2872 | Muskingum River | 3 | MR-3 | Conventional Boiler | Cyclone firing | 237.5 | 2150 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | Nov2009PM | 1 | 0 |  |  |  | 0.0506 |  | 0.0506 |  | 9.0526 | 0.45806
54081_3B | coal | 637 |  | 54081 | Spruance Genco, LLC | 3B | GEN3 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.035662 | lb/MMBtu | ERT |  | 3 | 3 | 134611 |  | 0.035662 | 0.035662 |  | 0.035662 |  | 13.0662 | 0.46597 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_3A | coal | 638 |  | 54081 | Spruance Genco, LLC | 3A | GEN3 | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | Filterable Particulate | 0.035662 | lb/MMBtu | ERT |  | 3 | 3 | 134611 |  | 0.035662 | 0.035662 |  | 0.035662 |  | 13.0662 | 0.46597 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
2720_Boiler 5 | coal | 639 |  | 2720 | Buck | Boiler 5 | 5 | Conventional Boiler | Tangential firing | 40 | 619 | Filterable Particulate | 0.0303 | lb/MMBtu | Part II | BLR5(3/7/06) | 3 | 0 |  |  | 0.0303 | 0.0303 |  | 0.0303 |  | 15.475 | 0.46889
2872_2 | coal | 640 |  | 2872 | Muskingum River | 2 | MR-2 | Conventional Boiler | Wall firing - front firing | 219.6 | 2050 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | Nov2009PM | 1 | 0 |  |  |  | 0.0506 |  | 0.0506 |  | 9.3352 | 0.47236
2872_1 | coal | 641 |  | 2872 | Muskingum River | 1 | MR-1 | Conventional Boiler | Wall firing - front firing | 219.6 | 2050 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | Nov2009PM | 1 | 0 |  |  |  | 0.0506 |  | 0.0506 |  | 9.3352 | 0.47236
1733_1 | coal | 642 |  | 1733 | Monroe Power Plant | 1 | MN1-Config | Conventional Boiler | Wall firing - opposed firing | 810 | 7140 | Filterable Particulate | 0.055 | lb/MMBtu | Part II | PM2005_Apr_1 | 2 | 0 |  |  | 0.055 | 0.055 |  | 0.055 |  | 8.8148 | 0.48481
3775_1 | coal | 643 |  | 3775 | Clinch River | 1 | CR-1 | Conventional Boiler | Vertical firing | 230 | 2100.9 | Filterable Particulate | 0.05312 | lb/MMBtu | ERT |  | 6 | 6 | 10040002 |  | 0.05312 | 0.05312 |  | 0.05312 |  | 9.1343 | 0.48522 | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1975-02-01
2720_Boiler 7 | coal | 644 |  | 2720 | Buck | Boiler 7 | 7 | Conventional Boiler | Tangential firing | 40 | 619 | Filterable Particulate | 0.031367 | lb/MMBtu | Part II | BLR7(6/1/05) | 3 | 0 |  |  | 0.031367 | 0.031367 |  | 0.031367 |  | 15.475 | 0.4854
2049_5 | coal | 645 |  | 2049 | Jack Watson | 5 | Unit 5 | Conventional Boiler | Wall firing - front firing | 500 | 4752.86 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | PM Reports (2008) | 1 | 0 |  |  |  | 0.052 |  | 0.052 |  | 9.5057 | 0.4943
1364_1 | coal | 646 |  | 1364 | Mill Creek | 1 | MC1 | Conventional Boiler | Tangential firing | 330 | 3723 | Filterable Particulate | 0.044 | lb/MMBtu | Part II | MC1-PM-2006 | 1 | 1 |  |  |  | 0.044 |  | 0.044 |  | 11.2818 | 0.4964
889_Unit 1 | coal | 647 |  | 889 | Baldwin Energy Complex | Unit 1 | 001 | Conventional Boiler | Cyclone firing | 626 | 5892 | Filterable Particulate | 0.054 | lb/MMBtu | Part II | 13 | 1 | 0 |  |  |  | 0.054 |  | 0.054 |  | 9.4121 | 0.50826
1364_2 | coal | 648 |  | 1364 | Mill Creek | 2 | MC2 | Conventional Boiler | Tangential firing | 330 | 3788 | Filterable Particulate | 0.045 | lb/MMBtu | Part II | MC2-PM-2009 | 1 | 1 |  |  |  | 0.045 |  | 0.045 |  | 11.4788 | 0.51655
2712_3B | coal | 649 |  | 2712 | Roxboro Steam Electric Plant | 3B | Rox_Cfg_3b | Conventional Boiler | Wall firing - rear firing | 370.5 | 3460 | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | Rox_Unit_3_Test_5 | 3 | 3 |  |  | 0.055333 | 0.055333 |  | 0.055333 |  | 9.3387 | 0.51674
2712_3A | coal | 650 |  | 2712 | Roxboro Steam Electric Plant | 3A | Rox_Cfg_3b | Conventional Boiler | Wall firing - rear firing | 370.5 | 3460 | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | Rox_Unit_3_Test_5 | 3 | 3 |  |  | 0.055333 | 0.055333 |  | 0.055333 |  | 9.3387 | 0.51674
4078_1 | coal | 651 |  | 4078 | Weston | 1 | W1 | Conventional Boiler | Wall firing - front firing | 63.6 | 858 | Filterable Particulate | 0.038333 | lb/MMBtu | Part II | W1 PM 2009 | 3 | 3 |  |  | 0.038333 | 0.038333 |  | 0.038333 |  | 13.4906 | 0.51714 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-01-01
2721_2 | coal | 652 | Retired | 2721 | Cliffside | 2 | 2 | Conventional Boiler | Tangential firing | 40.8 | 647 | Filterable Particulate | 0.0328 | lb/MMBtu | Part II | UNIT2(4/24/08) | 3 | 0 |  |  | 0.0328 | 0.0328 |  | 0.0328 |  | 15.8578 | 0.52014
2790_B1 | coal | 653 |  | 2790 | R.M. Heskett Station | B1 | B1 | Conventional Boiler | Stoker - traveling grate | 22 | 320 | Filterable Particulate | 0.036 | lb/MMBtu | Part II | 2 | 1 | 0 |  |  |  | 0.036 |  | 0.036 |  | 14.5455 | 0.52364
1831_EUBoiler6 | coal | 654 |  | 1831 | Otto E. Eckert Station | EUBoiler6 | 006 | Conventional Boiler | Wall firing - front firing | 71 | 807 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | PM-6-9/05 | 3 | 0 |  |  | 0.047 | 0.047 |  | 0.047 |  | 11.3662 | 0.53421
883_8 | coal | 655 |  | 883 | Waukegan | 8 | WK8CONFIG | Conventional Boiler | Tangential firing | 383 | 3960.892 | Filterable Particulate | 0.051664 | lb/MMBtu | ERT |  | 6 | 6 | 2013 |  | 0.051664 | 0.051664 |  | 0.051664 |  | 10.3418 | 0.5343 | Other control | Activated carbon injection | 2008-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1962-07-01
6639_G2 | coal | 656 |  | 6639 | R D Green | G2 | 2 | Conventional Boiler | Wall firing - opposed firing | 239 | 2726.6 | Filterable Particulate | 0.046919 | lb/MMBtu | ERT |  | 6 | 6 | 1276 |  | 0.046919 | 0.046919 |  | 0.046919 |  | 11.4084 | 0.53527 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-01-01 | SO2 control | Wet FGD - Spray Type | 1981-01-01
997_12 | coal | 657 |  | 997 | Michigan City | 12 | 12 | Conventional Boiler | Cyclone firing | 495 | 4650 | Filterable Particulate | 0.057922 | lb/MMBtu | Part II | MCGS U#12 M5 06/03/08 | 1 | 1 |  |  |  | 0.057922 |  | 0.057922 |  | 9.3939 | 0.54412 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1992-05-01
2721_4 | coal | 658 | Retired | 2721 | Cliffside | 4 | 4 | Conventional Boiler | Tangential firing | 65.1 | 810 | Filterable Particulate | 0.0442 | lb/MMBtu | Part II | UNIT4(6/2/09) | 3 | 0 |  |  | 0.0442 | 0.0442 |  | 0.0442 |  | 12.4424 | 0.54995
8023_1 | coal | 659 |  | 8023 | Columbia | 1 | Unit 1 | Conventional Boiler | Tangential firing | 590.3 | 6090 | Filterable Particulate | 0.0539 | lb/MMBtu | Part II | COL1-PM-20070907 | 1 | 1 |  |  |  | 0.0539 |  | 0.0539 |  | 10.3168 | 0.55607 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1975-03-01
6147_2 | coal | 660 |  | 6147 | Monticello | 2 | 2 | Conventional Boiler | Tangential firing | 583 | 7000 | Filterable Particulate | 0.047418 | lb/MMBtu | ERT |  | 6 | 6 | 879456 |  | 0.047418 | 0.047418 |  | 0.047418 |  | 12.0069 | 0.56934
2716_3 | coal | 661 |  | 2716 | W.H. Weatherspoon Plant | 3 | Wea_Cfg_3 | Conventional Boiler | Tangential firing | 79 | 962 | Filterable Particulate | 0.047333 | lb/MMBtu | Part II | Wea_Blr_3_Test_6 | 3 | 3 |  |  | 0.047333 | 0.047333 |  | 0.047333 |  | 12.1772 | 0.57639
1353_BSU1 | coal | 662 |  | 1353 | Big Sandy | BSU1 | BSU-1 | Conventional Boiler | Wall firing - opposed firing | 280.5 | 2512 | Filterable Particulate | 0.0661 | lb/MMBtu | Part II | Dec2009PM | 1 | 0 |  |  |  | 0.0661 |  | 0.0661 |  | 8.9554 | 0.59195
1010_6 | coal | 663 |  | 1010 | Wabash River | 6 | 6 | Conventional Boiler | Tangential firing | 342 | 3059.0605 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | STACKA091509 | 3 | 3 |  |  | 0.067 | 0.067 |  | 0.067 |  | 8.9446 | 0.59929 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-05-01
1891_2 | coal | 664 |  | 1891 | Laskin Energy Center | 2 | LEC2 | Conventional Boiler | Tangential firing | 55 | 660 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | GE-PM_CO-7-2009 | 1 | 0 |  |  | 0.05 | 0.05 |  | 0.05 |  | 12 | 0.6
1891_1 | coal | 665 |  | 1891 | Laskin Energy Center | 1 | LEC1 | Conventional Boiler | Tangential firing | 60 | 725 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | GE-PM_CO-7-2009 | 1 | 0 |  |  | 0.05 | 0.05 |  | 0.05 |  | 12.0833 | 0.60417
1893_4 | coal | 666 |  | 1893 | Boswell Energy Center | 4 | BEC4 | Conventional Boiler | Tangential firing | 587.5 | 5947 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 1,2,3,4-May2007-PM | 1 | 0 |  |  |  | 0.06 |  | 0.06 |  | 10.1226 | 0.60735
728_Y2BR | coal | 667 |  | 728 | Yates | Y2BR | Y2BR | Conventional Boiler | Tangential firing | 105 | 1171.8 | Filterable Particulate | 0.056667 | lb/MMBtu | Part II | Units 2&3 PM Emissions Test (2/28/07) | 3 | 0 |  |  | 0.056667 | 0.056667 |  | 0.056667 |  | 11.16 | 0.63241
874_5 | coal | 668 |  | 874 | Joliet 9 | 5 | JOL5 CONFIG | Conventional Boiler | Cyclone firing | 326 | 3572.378 | Filterable Particulate | 0.058706 | lb/MMBtu | ERT |  | 6 | 6 | 2009 |  | 0.058706 | 0.058706 |  | 0.058706 |  | 10.9582 | 0.64332 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-03-01
1353_BSU2 | coal | 669 |  | 1353 | Big Sandy | BSU2 | BSU-2 | Conventional Boiler | Wall firing - opposed firing | 800 | 7914 | Filterable Particulate | 0.0661 | lb/MMBtu | Part II | Dec2009PM | 1 | 0 |  |  |  | 0.0661 |  | 0.0661 |  | 9.8925 | 0.65389
3992_9 | coal | 670 |  | 3992 | Blount Street | 9 | 9B7T | Conventional Boiler | Wall firing - front firing | 53.2 | 575 | Filterable Particulate | 0.0608 | lb/MMBtu | Part II | M083603 | 3 | 3 |  |  | 0.0608 | 0.0608 |  | 0.0608 |  | 10.8083 | 0.65714
2187_2 | coal | 671 |  | 2187 | JE Corette Plant | 2 | Corette1 | Conventional Boiler | Tangential firing | 163 | 1750 | Filterable Particulate | 0.061333 | lb/MMBtu | Part II | Dec2009_PM | 3 | 0 |  |  | 0.061333 | 0.061333 |  | 0.061333 |  | 10.7362 | 0.65849
3131_2 | coal | 672 |  | 3131 | Shawville | 2 | SHAW2-2 | Conventional Boiler | Wall firing - front firing | 125 | 1349 | Filterable Particulate | 0.0612 | lb/MMBtu | Part II | SH-184-U2 | 3 | 3 |  |  | 0.0612 | 0.0612 |  | 0.0612 |  | 10.792 | 0.66047
728_Y3BR | coal | 673 |  | 728 | Yates | Y3BR | Y3BR | Conventional Boiler | Tangential firing | 105 | 1250.704 | Filterable Particulate | 0.056667 | lb/MMBtu | Part II | Units 2&3 PM Emissions Test (2/28/07) | 3 | 0 |  |  | 0.056667 | 0.056667 |  | 0.056667 |  | 11.9115 | 0.67499
3942_1 | coal | 674 |  | 3942 | Albright Power Station | 1 | Unit_1 | Conventional Boiler | Wall firing - unspecified | 81 | 786 | Filterable Particulate | 0.069563 | lb/MMBtu | ERT |  | 3 | 3 | 1111 |  | 0.069563 | 0.069563 |  | 0.069563 |  | 9.7037 | 0.67502 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
2721_3 | coal | 675 | Retired | 2721 | Cliffside | 3 | 3 | Conventional Boiler | Tangential firing | 65.3 | 810 | Filterable Particulate | 0.054633 | lb/MMBtu | Part II | UNIT3(8/16/05) | 3 | 0 |  |  | 0.054633 | 0.054633 |  | 0.054633 |  | 12.4043 | 0.67769
1010_4 | coal | 676 |  | 1010 | Wabash River | 4 | 4 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | STACKA091509 | 3 | 3 |  |  | 0.067 | 0.067 |  | 0.067 |  | 10.2633 | 0.68764 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-10-01
1010_3 | coal | 677 |  | 1010 | Wabash River | 3 | 3 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | STACKA091509 | 3 | 3 |  |  | 0.067 | 0.067 |  | 0.067 |  | 10.2633 | 0.68764
1010_2 | coal | 678 |  | 1010 | Wabash River | 2 | 2 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | STACKA091509 | 3 | 3 |  |  | 0.067 | 0.067 |  | 0.067 |  | 10.2633 | 0.68764
1004_7-2 | coal | 679 |  | 1004 | Edwardsport | 7-2 | 7-2 | Conventional Boiler | Wall firing - front firing | 42.75 | 510 | Filterable Particulate | 0.058 | lb/MMBtu | Part II | UNIT7-2(12/7/06) | 3 | 0 |  |  | 0.058 | 0.058 |  | 0.058 |  | 11.9298 | 0.69193
1010_5 | coal | 680 |  | 1010 | Wabash River | 5 | 5 | Conventional Boiler | Wall firing - front firing | 103 | 1079.0931 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | STACKA091509 | 3 | 3 |  |  | 0.067 | 0.067 |  | 0.067 |  | 10.4766 | 0.70193
59_1 | coal | 681 |  | 59 | Platte | 1 | 1 | Conventional Boiler | Tangential firing | 110 | 1048 | Filterable Particulate | 0.076767 | lb/MMBtu | Part II | Particulate Emission Compliance Study 2006 | 3 | 3 |  |  | 0.076767 | 0.076767 |  | 0.076767 |  | 9.5273 | 0.73138
1058_5 | coal | 682 |  | 1058 | Sixth Street | 5 | Unit 5 | Conventional Boiler | Wall firing - front firing | 32.3 | 389 | Filterable Particulate | 0.0613 | lb/MMBtu | Part II | SXTH5-PM-20050419 | 1 | 1 |  |  |  | 0.0613 |  | 0.0613 |  | 12.0433 | 0.73826
1091_2 | coal | 683 |  | 1091 | George Neal North | 2 | 2 | Conventional Boiler | Wall firing - unspecified | 325 | 3081 | Filterable Particulate | 0.078311 | lb/MMBtu | Part II | 7/13/2006-PM | 1 | 0 |  |  |  | 0.078311 |  | 0.078311 |  | 9.48 | 0.74239
3295_URQ3 | coal | 684 |  | 3295 | Urquhart | URQ3 | URQ003 | Conventional Boiler | Tangential firing | 103 | 1048 | Filterable Particulate | 0.0761 | lb/MMBtu | Part II | PM-02/05 | 1 | 0 |  |  |  | 0.0761 |  | 0.0761 |  | 10.1748 | 0.7743 | PM control | Electrostatic precipitator, cold side, unspecified | 1969-11-01
3264_1 | coal | 685 |  | 3264 | W. S. Lee | 1 | 1 | Conventional Boiler | Tangential firing | 105.9 | 1215 | Filterable Particulate | 0.069233 | lb/MMBtu | Part II | UNIT1(3/10/09) | 3 | 0 |  |  | 0.069233 | 0.069233 |  | 0.069233 |  | 11.4731 | 0.79432
1361_5 | coal | 686 |  | 1361 | Tyrone | 5 | TY3 | Conventional Boiler | Wall firing - front firing | 75 | 995 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | TY3-PM-06272008 | 1 | 1 |  |  |  | 0.06 |  | 0.06 |  | 13.2667 | 0.796
3264_2 | coal | 687 |  | 3264 | W. S. Lee | 2 | 2 | Conventional Boiler | Tangential firing | 105.8 | 1215 | Filterable Particulate | 0.0714 | lb/MMBtu | Part II | UNIT2(4/19/05) | 3 | 0 |  |  | 0.0714 | 0.0714 |  | 0.0714 |  | 11.4839 | 0.81995
3122_2 | coal | 688 |  | 3122 | Homer City Station | 2 | HC2CONFIG | Conventional Boiler | Wall firing - opposed firing | 655 | 5690.552 | Filterable Particulate | 0.095333 | lb/MMBtu | Part II | HC2 Apr 2009 PM Test | 3 | 3 |  |  | 0.095333 | 0.095333 |  | 0.095333 |  | 8.6879 | 0.82824
1695_5 | coal | 689 |  | 1695 | B.C. Cobb | 5 | BCCobb5-Conf | Conventional Boiler | Tangential firing | 167.5 | 1623 | Filterable Particulate | 0.086633 | lb/MMBtu | Part II | BCC5 - 2009 PM Testing | 3 | 3 |  |  | 0.086633 | 0.086633 |  | 0.086633 |  | 9.6896 | 0.83944
1252_10 | coal | 690 |  | 1252 | Tecumseh Energy Center | 10 | 10 | Conventional Boiler | Tangential firing | 145 | 1423 | Filterable Particulate | 0.08577 | lb/MMBtu | Part II | CAM 0507/10 | 10 | 1 |  |  | 0.08577 | 0.08577 |  | 0.08577 |  | 9.8138 | 0.84173 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-08-01
1384_2 | coal | 691 |  | 1384 | Cooper Station. | 2 | Unit 02 | Conventional Boiler | Wall firing - front firing | 240 | 2418 | Filterable Particulate | 0.083667 | lb/MMBtu | Part II | U2_PM_05/22/07 | 3 | 3 |  |  | 0.083667 | 0.083667 |  | 0.083667 |  | 10.075 | 0.84294
1831_EUBoiler2 | coal | 692 |  | 1831 | Otto E. Eckert Station | EUBoiler2 | 002 | Conventional Boiler | Tangential firing | 38 | 522 | Filterable Particulate | 0.0617 | lb/MMBtu | Part II | PM-2-9/05 | 3 | 0 |  |  | 0.0617 | 0.0617 |  | 0.0617 |  | 13.7368 | 0.84756 | PM control | Electrostatic precipitator, unspecified | 1978-01-01
1004_8-1 | coal | 693 |  | 1004 | Edwardsport | 8-1 | 8-1 | Conventional Boiler | Wall firing - front firing | 42.75 | 510 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | UNIT8-1(4/9/08) | 3 | 0 |  |  | 0.071333 | 0.071333 |  | 0.071333 |  | 11.9298 | 0.85099
1357_4 | coal | 694 |  | 1357 | Green River | 4 | GR03 | Conventional Boiler | Wall firing - front firing | 72 | 1047 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | GR3-PM-2008 | 1 | 1 |  |  |  | 0.06 |  | 0.06 |  | 14.5417 | 0.8725
1046_1 | coal | 695 |  | 1046 | Dubuque | 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 37.6 | 605.8 | Filterable Particulate | 0.0558 | lb/MMBtu | Part II | DBQ1-PM-20051206 | 1 | 1 |  |  |  | 0.0558 |  | 0.0558 |  | 16.1117 | 0.89903 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01
1250_4 | coal | 696 |  | 1250 | Lawrence Energy Center | 4 | 4 | Conventional Boiler | Tangential firing | 126 | 1276 | Filterable Particulate | 0.089552 | lb/MMBtu | Part II | CAM 1007/4 | 58 | 4 |  |  | 0.089552 | 0.089552 |  | 0.089552 |  | 10.127 | 0.90689 | PM control | PM scrubber - Venturi | 1976-01-01 | PM control | PM scrubber - Venturi | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 1976-01-01
1897_3 | coal | 697 |  | 1897 | Hibbard Energy Center | 3 | HREC3 | Conventional Boiler | Stoker - spreader | 35 | 518 | Filterable Particulate | 0.061333 | lb/MMBtu | Part II | PM_CO-Boiler3 | 3 | 0 |  |  | 0.061333 | 0.061333 |  | 0.061333 |  | 14.8 | 0.90773
1058_4 | coal | 698 |  | 1058 | Sixth Street | 4 | Unit 4 | Conventional Boiler | Wall firing - front firing | 14.8 | 304 | Filterable Particulate | 0.0445 | lb/MMBtu | Part II | SXTH4-PM-20060623 | 1 | 1 |  |  |  | 0.0445 |  | 0.0445 |  | 20.5405 | 0.91405 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-08-01
963_33 | coal | 699 |  | 963 | Dallman | 33 | 33 | Conventional Boiler | Tangential firing | 208 | 2089.8 | Filterable Particulate | 0.096 | lb/MMBtu | Part II | Dallman 33 PM.CO Test | 1 | 1 |  |  |  | 0.096 |  | 0.096 |  | 10.0471 | 0.96452 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1980-01-01
3122_1 | coal | 700 |  | 3122 | Homer City Station | 1 | HC1CONFIG | Conventional Boiler | Wall firing - opposed firing | 655 | 5898.68 | Filterable Particulate | 0.108 | lb/MMBtu | Part II | HC1 Jan 2009 PM Test | 3 | 3 |  |  | 0.108 | 0.108 |  | 0.108 |  | 9.0056 | 0.97261
3319_3 | coal | 701 |  | 3319 | Jefferies | 3 | J3 | Conventional Boiler | Wall firing - front firing | 164 | 1780 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | J3PM2005 | 1 | 1 |  |  |  | 0.09 |  | 0.09 |  | 10.8537 | 0.97683 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-01-01
1058_3 | coal | 702 |  | 1058 | Sixth Street | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 13.9 | 304 | Filterable Particulate | 0.0449 | lb/MMBtu | Part II | SXTH3-PM-20060412 | 1 | 1 |  |  |  | 0.0449 |  | 0.0449 |  | 21.8705 | 0.98199 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-12-01
2169_2 | coal | 703 |  | 2169 | Chamois Power Plant | 2 | Unit 2 | Conventional Boiler | Cyclone firing | 50 | 563 | Filterable Particulate | 0.091667 | lb/MMBtu | Part II | PM052005 | 3 | 3 |  |  | 0.091667 | 0.091667 |  | 0.091667 |  | 11.26 | 1.0322 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-06-01
1357_5 | coal | 704 |  | 1357 | Green River | 5 | GR04 | Conventional Boiler | Wall firing - front firing | 102 | 1374 | Filterable Particulate | 0.08 | lb/MMBtu | Part II | GR4-PM-2008 | 1 | 1 |  |  |  | 0.08 |  | 0.08 |  | 13.4706 | 1.0776
1239_39 | coal | 705 |  | 1239 | Riverton | 39 | 039 | Conventional Boiler | Wall firing - unspecified | 40 | 426 | Filterable Particulate | 0.1012 | lb/MMBtu | Part II | 1 | 1 | 0 |  |  |  | 0.1012 |  | 0.1012 |  | 10.65 | 1.0778
1384_1 | coal | 706 |  | 1384 | Cooper Station. | 1 | Unit 01 | Conventional Boiler | Wall firing - front firing | 124 | 1381 | Filterable Particulate | 0.099 | lb/MMBtu | Part II | U1&2_PM_10/10/07 | 3 | 3 |  |  | 0.099 | 0.099 |  | 0.099 |  | 11.1371 | 1.1026
1831_EUBoiler3 | coal | 707 |  | 1831 | Otto E. Eckert Station | EUBoiler3 | 003 | Conventional Boiler | Tangential firing | 40 | 522 | Filterable Particulate | 0.0914 | lb/MMBtu | Part II | PM-3-9/05 | 3 | 0 |  |  | 0.0914 | 0.0914 |  | 0.0914 |  | 13.05 | 1.1928 | PM control | Electrostatic precipitator, unspecified | 1978-01-01
3317_2 | coal | 708 |  | 3317 | Dolphus M Grainger | 2 | G2 | Conventional Boiler | Wall firing - front firing | 87 | 972 | Filterable Particulate | 0.11 | lb/MMBtu | Part II | G2PM2007 | 1 | 1 |  |  |  | 0.11 |  | 0.11 |  | 11.1724 | 1.229 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-06-01
1385_2 | coal | 709 |  | 1385 | Dale Station | 2 | 02 | Conventional Boiler | Wall firing - front firing | 24 | 278 | Filterable Particulate | 0.109 | lb/MMBtu | Part II | U1_2_PM_12/20/06 | 3 | 3 |  |  | 0.109 | 0.109 |  | 0.109 |  | 11.5833 | 1.2626
1385_1 | coal | 710 |  | 1385 | Dale Station | 1 | 01 | Conventional Boiler | Wall firing - front firing | 24 | 278 | Filterable Particulate | 0.109 | lb/MMBtu | Part II | U1_2_PM_12/20/06 | 3 | 3 |  |  | 0.109 | 0.109 |  | 0.109 |  | 11.5833 | 1.2626
2098_6 | coal | 711 |  | 2098 | Lake Road | 6 | 6 | Conventional Boiler | Cyclone firing | 99 | 980 | Filterable Particulate | 0.12926 | lb/MMBtu | ERT |  | 3 | 3 | 892 |  | 0.12926 | 0.12926 |  | 0.12926 |  | 9.899 | 1.2795 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-07-01
3280_CAN1 | coal | 712 |  | 3280 | Canadys Steam | CAN1 | CAN001 | Conventional Boiler | Tangential firing | 121 | 1141.5 | Filterable Particulate | 0.1431 | lb/MMBtu | Part II | PM-02/06-CAN1 | 1 | 0 |  |  |  | 0.1431 |  | 0.1431 |  | 9.4339 | 1.35 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-06-01
3317_1 | coal | 713 |  | 3317 | Dolphus M Grainger | 1 | G1 | Conventional Boiler | Wall firing - front firing | 87 | 940 | Filterable Particulate | 0.13 | lb/MMBtu | Part II | G1PM2005 | 1 | 1 |  |  |  | 0.13 |  | 0.13 |  | 10.8046 | 1.4046 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-06-01
1043_2SG1 | coal | 714 |  | 1043 | Frank E. Ratts | 2SG1 | 2SG1conf1 | Conventional Boiler | Wall firing - front firing | 131 | 1142 | Filterable Particulate | 0.167 | lb/MMBtu | Part II | 2008R2PM | 3 | 3 |  |  | 0.167 | 0.167 |  | 0.167 |  | 8.7176 | 1.4558 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-12-01
3319_4 | coal | 715 |  | 3319 | Jefferies | 4 | J4 | Conventional Boiler | Wall firing - front firing | 162 | 1602 | Filterable Particulate | 0.15 | lb/MMBtu | Part II | J4PM2005 | 1 | 1 |  |  |  | 0.15 |  | 0.15 |  | 9.8889 | 1.4833 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-07-01
3992_8 | coal | 716 |  | 3992 | Blount Street | 8 | 8B6T | Conventional Boiler | Wall firing - front firing | 53.4 | 575 | Filterable Particulate | 0.14437 | lb/MMBtu | Part II | M083808 | 3 | 3 |  |  | 0.14437 | 0.14437 |  | 0.14437 |  | 10.7678 | 1.5545
1082_1 | coal | 717 |  | 1082 | Walter Scott Jr. Energy Center | 1 | 1 | Conventional Boiler | Wall firing - unspecified | 45 | 656 | Filterable Particulate | 0.10687 | lb/MMBtu | Part II | 6/2006 PM3 | 1 | 0 |  |  |  | 0.10687 |  | 0.10687 |  | 14.5778 | 1.5579
1943_003 | coal | 718 |  | 1943 | Hoot Lake | 003 | 3 | Conventional Boiler | Wall firing - front firing | 83.5 | 978.7 | Filterable Particulate | 0.13467 | lb/MMBtu | Part II | Particulate Engineering/Parametric Test | 3 | 3 |  |  | 0.13467 | 0.13467 |  | 0.13467 |  | 11.721 | 1.5784 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-05-01
1091_1 | coal | 719 |  | 1091 | George Neal North | 1 | 1 | Conventional Boiler | Cyclone firing | 145 | 1363 | Filterable Particulate | 0.17052 | lb/MMBtu | Part II | 7/17/2008 | 1 | 0 |  |  |  | 0.17052 |  | 0.17052 |  | 9.4 | 1.6029
1383_R1 | coal | 720 |  | 1383 | Robert A Reid | R1 | 1 | Conventional Boiler | Wall firing - front firing | 72 | 616.6 | Filterable Particulate | 0.195 | lb/MMBtu | Part II | R1 Compliance 2006 | 3 | 3 |  |  | 0.195 | 0.195 |  | 0.195 |  | 8.5639 | 1.67
2161_3 | coal | 721 |  | 2161 | James River Power Station | 3 | Unit_3_JRPS | Conventional Boiler | Wall firing - front firing | 44 | 496 | Filterable Particulate | 0.15331 | lb/MMBtu | Part II | PM Emissions\181-020 | 13 | 13 |  |  | 0.15331 | 0.15331 |  | 0.15331 |  | 11.2727 | 1.7282
1239_40 | coal | 722 |  | 1239 | Riverton | 40 | 040 | Conventional Boiler | Tangential firing | 58 | 600 | Filterable Particulate | 0.1827 | lb/MMBtu | Part II | 3 | 1 | 0 |  |  |  | 0.1827 |  | 0.1827 |  | 10.3448 | 1.89
1047_3 | coal | 723 |  | 1047 | Lansing | 3 | Unit 3 | Conventional Boiler | Wall firing - front firing | 31.9 | 452.9 | Filterable Particulate | 0.1461 | lb/MMBtu | Part II | LANS3-PM-20060427 | 1 | 1 |  |  |  | 0.1461 |  | 0.1461 |  | 14.1975 | 2.0743 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01
1218_1 | coal | 724 |  | 1218 | Fair Station | 1 | U1 | Conventional Boiler | Wall firing - front firing | 24.5 | 330 | Filterable Particulate | 0.17 | lb/MMBtu | Part II | TITLEV09U1 | 1 | 1 |  |  |  | 0.17 |  | 0.17 |  | 13.4694 | 2.2898 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
1058_2 | coal | 725 |  | 1058 | Sixth Street | 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 13.3 | 304 | Filterable Particulate | 0.1157 | lb/MMBtu | Part II | SXTH2-PM-20060406 | 1 | 1 |  |  |  | 0.1157 |  | 0.1157 |  | 22.8571 | 2.6446 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-06-01
1131_7 | coal | 726 |  | 1131 | Streeter Station | 7 | 7 | Conventional Boiler | Wall firing - front firing | 38.4 | 473 | Filterable Particulate | 0.219 | lb/MMBtu | Part II | 2006 Stack Test | 3 | 3 |  |  | 0.219 | 0.219 |  | 0.219 |  | 12.3177 | 2.6976
3982_5 | coal | 727 |  | 3982 | Bay Front | 5 | 5 | Conventional Boiler | Cyclone firing | 32 | 389 | Filterable Particulate | 0.225 | lb/MMBtu | Part II | PM Compliance 2006 | 1 | 1 |  |  |  | 0.225 |  | 0.225 |  | 12.1562 | 2.7352 | PM control | Multiple cyclone | 1976-08-01

## fPM_Variability
facility_ID_boiler_id | facility_name | Reason_for_Removal as top ranked unit for fPM new source floor | facility_ID | boiler_id | configuration_id | HAP Surrogate | Emission Rate (1mg = 1 x MDL) | Emission Rate Units | From | BDL | Report_id | Count of Runs | Submittal_ID_ERT | Config_heat_rate_MMBtu/MWh | fPM_Min_lb_per_MWh_Rank | lb fPM/MWh (1 Mg = 1 x MDL)
10566_Boil 2 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Boil 2 | Boil 2 | Filterable Particulate | 0.00023004 | lb/MMBtu | ERT | No |  | 3 | 1365 | 9.7333 | 1 | 0.002239
10566_Boil 2 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Boil 2 | Boil 2 | Filterable Particulate | 0.0012855 | lb/MMBtu | Part II | 0 | 2009 annual boil2 | 3 |  | 9.7333 | 1 | 0.012512
10566_Boil 2 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Boil 2 | Boil 2 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | 2005 annual boil2 | 3 |  | 9.7333 | 1 | 0.032444
10566_Boil 2 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Boil 2 | Boil 2 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | 2006 annual boil2 | 3 |  | 9.7333 | 1 | 0.032444
10566_Boil 2 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Boil 2 | Boil 2 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 2007 annual boil2 | 3 |  | 9.7333 | 1 | 0.0584
10566_Boil 2 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 2 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 33 of the lab data submitted with the Part III test report. | 10566 | Boil 2 | Boil 2 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | 2008 annual boil2 | 3 |  | 9.7333 | 1 | 0.0876
50976_AABO1 | INDIANTOWN COGENERATION L.P. | Indiantown Unit 1's ERT submittal includes a test where the facility entered grams as milligrams. This error was apparent because the tare weights of the filters as reported was 1000 times lower than the tare weights in other test reports. When the erronous "milligram" entries were corrected to "milligrams" Indian Town was not one of the top performers. It is also worth noting here that there was a second test reported for Indian Town under Part II with a very low emission rate (0.0004 lbs fPM/MMBtu). Per EPA guidance we estimated the volume of flue gas sampled to meet the minimum sample volume specified in the method (0.8 scm). Based on an estimated sample volume of one standard cubic meter we calcuated a detection limit for fPM on a lb fPM/MMBtu basis. The minimum detection limit for Indian Town based on this method (on a lb/MMBtu) was approximately 0.0007 lbs fPM/MMBtu. This value removed Indiantown from contention as the best performing EGU. | 50976 | AABO1 | 001 | Filterable Particulate | 0.0002424 | lb/MMBtu | ERT | No |  | 3 | 1336 | 9.4792 | 2 | 0.0022978
50976_AABO1 | INDIANTOWN COGENERATION L.P. | Indiantown Unit 1's ERT submittal includes a test where the facility entered grams as milligrams. This error was apparent because the tare weights of the filters as reported was 1000 times lower than the tare weights in other test reports. When the erronous "milligram" entries were corrected to "milligrams" Indian Town was not one of the top performers. It is also worth noting here that there was a second test reported for Indian Town under Part II with a very low emission rate (0.0004 lbs fPM/MMBtu). Per EPA guidance we estimated the volume of flue gas sampled to meet the minimum sample volume specified in the method (0.8 scm). Based on an estimated sample volume of one standard cubic meter we calcuated a detection limit for fPM on a lb fPM/MMBtu basis. The minimum detection limit for Indian Town based on this method (on a lb/MMBtu) was approximately 0.0007 lbs fPM/MMBtu. This value removed Indiantown from contention as the best performing EGU. | 50976 | AABO1 | 001 | Filterable Particulate | 0.0007959 | lb/MMBtu | Part II | 0 | 10396 | 3 |  | 9.4792 | 2 | 0.0075445
50976_AABO1 | INDIANTOWN COGENERATION L.P. | Indiantown Unit 1's ERT submittal includes a test where the facility entered grams as milligrams. This error was apparent because the tare weights of the filters as reported was 1000 times lower than the tare weights in other test reports. When the erronous "milligram" entries were corrected to "milligrams" Indian Town was not one of the top performers. It is also worth noting here that there was a second test reported for Indian Town under Part II with a very low emission rate (0.0004 lbs fPM/MMBtu). Per EPA guidance we estimated the volume of flue gas sampled to meet the minimum sample volume specified in the method (0.8 scm). Based on an estimated sample volume of one standard cubic meter we calcuated a detection limit for fPM on a lb fPM/MMBtu basis. The minimum detection limit for Indian Town based on this method (on a lb/MMBtu) was approximately 0.0007 lbs fPM/MMBtu. This value removed Indiantown from contention as the best performing EGU. | 50976 | AABO1 | 001 | Filterable Particulate | 0.00081797 | lb/MMBtu | Part II | 0 | 11350 | 3 |  | 9.4792 | 2 | 0.0077538
50976_AABO1 | INDIANTOWN COGENERATION L.P. | Indiantown Unit 1's ERT submittal includes a test where the facility entered grams as milligrams. This error was apparent because the tare weights of the filters as reported was 1000 times lower than the tare weights in other test reports. When the erronous "milligram" entries were corrected to "milligrams" Indian Town was not one of the top performers. It is also worth noting here that there was a second test reported for Indian Town under Part II with a very low emission rate (0.0004 lbs fPM/MMBtu). Per EPA guidance we estimated the volume of flue gas sampled to meet the minimum sample volume specified in the method (0.8 scm). Based on an estimated sample volume of one standard cubic meter we calcuated a detection limit for fPM on a lb fPM/MMBtu basis. The minimum detection limit for Indian Town based on this method (on a lb/MMBtu) was approximately 0.0007 lbs fPM/MMBtu. This value removed Indiantown from contention as the best performing EGU. | 50976 | AABO1 | 001 | Filterable Particulate | 0.0019333 | lb/MMBtu | Part II | 0 | I-9222 | 3 |  | 9.4792 | 2 | 0.018327
50976_AABO1 | INDIANTOWN COGENERATION L.P. | Indiantown Unit 1's ERT submittal includes a test where the facility entered grams as milligrams. This error was apparent because the tare weights of the filters as reported was 1000 times lower than the tare weights in other test reports. When the erronous "milligram" entries were corrected to "milligrams" Indian Town was not one of the top performers. It is also worth noting here that there was a second test reported for Indian Town under Part II with a very low emission rate (0.0004 lbs fPM/MMBtu). Per EPA guidance we estimated the volume of flue gas sampled to meet the minimum sample volume specified in the method (0.8 scm). Based on an estimated sample volume of one standard cubic meter we calcuated a detection limit for fPM on a lb fPM/MMBtu basis. The minimum detection limit for Indian Town based on this method (on a lb/MMBtu) was approximately 0.0007 lbs fPM/MMBtu. This value removed Indiantown from contention as the best performing EGU. | 50976 | AABO1 | 001 | Filterable Particulate | 24.4349 | lb/MMBtu | Part II | 0 | 10669-3 | 3 |  | 9.4792 | 2 | 231.6242
2554_1 | Dunkirk Generating Plant | The air pollution control technology in services at Dunkirk Unit 1 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 2554 | 1 | 1 | Filterable Particulate | 0.00029899 | lb/MMBtu | ERT | No |  | 6 | 535 | 10.8494 | 3 | 0.0032438
10566_Boil 1 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Boil 1 | Boil 1 | Filterable Particulate | 0.0005161 | lb/MMBtu | ERT | No |  | 3 | 1128 | 9.7333 | 4 | 0.0050234
10566_Boil 1 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Boil 1 | Boil 1 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | 0 | 2009 annual boil1 | 3 |  | 9.7333 | 4 | 0.025956
10566_Boil 1 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Boil 1 | Boil 1 | Filterable Particulate | 0.0032855 | lb/MMBtu | Part II | 0 | 2005 annual boil1 | 3 |  | 9.7333 | 4 | 0.031979
10566_Boil 1 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Boil 1 | Boil 1 | Filterable Particulate | 0.0046667 | lb/MMBtu | Part II | 0 | 2008 annual boil1 | 3 |  | 9.7333 | 4 | 0.045422
10566_Boil 1 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Boil 1 | Boil 1 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | 2006 Annual Boil1 | 3 |  | 9.7333 | 4 | 0.071378
10566_Boil 1 | Chambers Cogeneration LP | The OTM27 test used to establish Chambers Boiler 1 as the best performer did not include the recovery of the PM > 2.5 fraction. As reflected on pdf page 31 of the lab data submitted with the Part III test report. | 10566 | Boil 1 | Boil 1 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | 2007 annual boil1 | 3 |  | 9.7333 | 4 | 0.074622
492_5 | Martin Drake | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | 5 | Unit 5 - Coal | Filterable Particulate | 0.00049068 | lb/MMBtu | ERT | No |  | 3 | 1189 | 10.3636 | 5 | 0.0050853
492_5 | Martin Drake | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | 5 | Unit 5 - Coal | Filterable Particulate | 0.00091801 | lb/MMBtu | Part II | 0 | APT CSU5384 D | 3 |  | 10.3636 | 5 | 0.009514
492_5 | Martin Drake | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | 5 | Unit 5 - Coal | Filterable Particulate | 0.00784 | lb/MMBtu | Part II | 0 | Airtech 2693F | 3 |  | 10.3636 | 5 | 0.081251
492_5 | Martin Drake | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | 5 | Unit 5 - Coal | Filterable Particulate | 0.0284 | lb/MMBtu | Part II | 0 | Airtech 2383 | 2 |  | 10.3636 | 5 | 0.29433
492_5 | Martin Drake | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | 5 | Unit 5 - Coal | Filterable Particulate | 0.0338 | lb/MMBtu | Part II | 0 | Airtech 2693A-D-A | 3 |  | 10.3636 | 5 | 0.35029
492_5 | Martin Drake | The air pollution control technology in services at Martin Drake Unit 5 does not reflect current RACT/BACT/LAER levels of emissions control because the unit is not equipped with a flue gas desulfurization system that is capable of greater than 90% SO2 removal. | 492 | 5 | Unit 5 - Coal | Filterable Particulate | 0.0591 | lb/MMBtu | Part II | 0 | Airtech 2383A | 3 |  | 10.3636 | 5 | 0.61249
8223_3 | Springerville | New MACT Floor Unit | 8223 | 3 | 3 | Filterable Particulate | 0.00058211 | lb/MMBtu | ERT | No |  | 6 | 1133 | 9.3333 | 6 | 0.0054331
8223_3 | Springerville | New MACT Floor Unit | 8223 | 3 | 3 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | U3 PERF 08MAY07 | 1 |  | 9.3333 | 6 | 0.0093333
8223_3 | Springerville | New MACT Floor Unit | 8223 | 3 | 3 | Filterable Particulate | 0.00179 | lb/MMBtu | Part II | 0 | U3 PERF 09MAY18 | 1 |  | 9.3333 | 6 | 0.016707
8223_3 | Springerville | New MACT Floor Unit | 8223 | 3 | 3 | Filterable Particulate | 0.0018 | lb/MMBtu | Part II | 0 | U3 PERF 06NOV20 (PM RETEST) | 1 |  | 9.3333 | 6 | 0.0168
8223_3 | Springerville | New MACT Floor Unit | 8223 | 3 | 3 | Filterable Particulate | 0.0044 | lb/MMBtu | Part II | 0 | U3 PERF 07JUL09 | 1 |  | 9.3333 | 6 | 0.041067
2277_2 | Sheldon Station |  | 2277 | 2 | U2 | Filterable Particulate | 0.00051535 | lb/MMBtu | ERT | No |  | 6 | 1833 | 10.7376 | 7 | 0.0055336
10043_B01 | Logan Generating Plant |  | 10043 | B01 | Unit1 | Filterable Particulate | 0.00065396 | lb/MMBtu | ERT | No |  | 3 | 1266 | 8.7547 | 8 | 0.0057252
1626_1 | Salem Harbor |  | 1626 | 1 | Unit 1 | Filterable Particulate | 0.00049037 | lb/MMBtu | ERT | No |  | 3 | 2161 | 12.0488 | 9 | 0.0059084
1626_1 | Salem Harbor |  | 1626 | 1 | Unit 1 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | 2007Unit1PM | 1 |  | 12.0488 | 9 | 0.036146
1626_1 | Salem Harbor |  | 1626 | 1 | Unit 1 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | 2005Unit1PM | 1 |  | 12.0488 | 9 | 0.060244
1626_1 | Salem Harbor |  | 1626 | 1 | Unit 1 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 2008Unit1PM | 1 |  | 12.0488 | 9 | 0.072293
1626_1 | Salem Harbor |  | 1626 | 1 | Unit 1 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | 2009Unit1PM | 1 |  | 12.0488 | 9 | 0.10844
1626_1 | Salem Harbor |  | 1626 | 1 | Unit 1 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 2006Unit1PM | 1 |  | 12.0488 | 9 | 0.12049
8223_4 | Springerville |  | 8223 | 4 | 4 | Filterable Particulate | 0.00075428 | lb/MMBtu | ERT | No |  | 6 | 1129 | 9.3333 | 10 | 0.00704
8223_4 | Springerville |  | 8223 | 4 | 4 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | U4 INITIAL PERF 09DEC15 (PM, HF) | 1 |  | 9.3333 | 10 | 0.0093333
8223_4 | Springerville |  | 8223 | 4 | 4 | Filterable Particulate | 0.0019 | lb/MMBtu | Part II | 0 | U4 PERF DEC09 (ALT PM10) | 1 |  | 9.3333 | 10 | 0.017733
52071_5A | Sandow Station |  | 52071 | 5A | 5A | Filterable Particulate | 0.0006734 | lb/MMBtu | ERT | No |  | 6 | 834 | 10.4834 | 11 | 0.0070596
52071_5A | Sandow Station |  | 52071 | 5A | 5A | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | 2-Source Emissions Survey, Stacks | 1 |  | 10.4834 | 11 | 0.010483
52071_5A | Sandow Station |  | 52071 | 5A | 5A | Filterable Particulate | 0.001 | lb/MMBtu | Part II | -1 | 2-Source Emissions Survey, Stacks | 2 |  | 10.4834 | 11 | 0.010483
2408_E2 | PSEG Mercer Generating Station |  | 2408 | E2 | MERU2E2PT2OS1-Coal | Filterable Particulate | 0.00078255 | lb/MMBtu | ERT | No |  | 6 | 1585 | 9.0379 | 12 | 0.0070726
2408_E2 | PSEG Mercer Generating Station |  | 2408 | E2 | MERU2E2PT2OS1-Coal | Filterable Particulate | 0.0009115 | lb/MMBtu | Part II | 0 | MER 1-2 2009 ST Co NG PM | 2 |  | 9.0379 | 12 | 0.0082381
2408_E2 | PSEG Mercer Generating Station |  | 2408 | E2 | MERU2E2PT2OS1-Coal | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | MER2 2009 1YR ST Co NG | 3 |  | 9.0379 | 12 | 0.018076
2554_4 | Dunkirk Generating Plant |  | 2554 | 4 | 4 | Filterable Particulate | 0.00076382 | lb/MMBtu | ERT | No |  | 6 | 536 | 9.4154 | 13 | 0.0071917
2408_E1 | PSEG Mercer Generating Station |  | 2408 | E1 | MERU1E1PT1OS1-Coal | Filterable Particulate | 0.0008561 | lb/MMBtu | ERT | No |  | 6 | 1602 | 9.0379 | 14 | 0.0077374
2408_E1 | PSEG Mercer Generating Station |  | 2408 | E1 | MERU1E1PT1OS1-Coal | Filterable Particulate | 0.00088573 | lb/MMBtu | Part II | 0 | MER 1-2 2009 ST Co NG PM | 3 |  | 9.0379 | 14 | 0.0080052
2408_E1 | PSEG Mercer Generating Station |  | 2408 | E1 | MERU1E1PT1OS1-Coal | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | MER1 2009 1YR ST Co NG | 3 |  | 9.0379 | 14 | 0.0090379
6077_2 | Gerald Gentleman |  | 6077 | 2 | U2 | Filterable Particulate | 0.00080743 | lb/MMBtu | ERT | No |  | 6 | 1835 | 10.0507 | 15 | 0.0081152
568_BHB3 | Bridgeport Station |  | 568 | BHB3 | BHSEMU3OS2-Coal | Filterable Particulate | 0.00079892 | lb/MMBtu | ERT | No |  | 6 | 1618 | 10.1737 | 16 | 0.008128
6041_3 | H L Spurlock Station |  | 6041 | 3 | Unit 03 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | Acid Gas Emissions Test (1/9/07) | 2 |  | 8.3333 | 17 | 0.0083333
6041_3 | H L Spurlock Station |  | 6041 | 3 | Unit 03 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | U3PM_10/23/09 | 3 |  | 8.3333 | 17 | 0.016667
6041_3 | H L Spurlock Station |  | 6041 | 3 | Unit 03 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | PM Emissions Test (1/10/07) | 3 |  | 8.3333 | 17 | 0.041667
6041_3 | H L Spurlock Station |  | 6041 | 3 | Unit 03 | Filterable Particulate | 0.0065383 | lb/MMBtu | ERT | No |  | 3 | 1563 | 8.3333 | 17 | 0.054486
963_34 | Dallman |  | 963 | 34 | 34 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | Dallman 34 Test 2 | 1 |  | 8.391 | 18 | 0.008391
963_34 | Dallman |  | 963 | 34 | 34 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | Dallman 34 Test 1 | 1 |  | 8.391 | 18 | 0.092301
492_6 | Martin Drake |  | 492 | 6 | Unit 6 - Coal | Filterable Particulate | 0.00077373 | lb/MMBtu | Part II | 0 | Airtech 2693A-D-A | 3 |  | 10.9412 | 19 | 0.0084655
492_6 | Martin Drake |  | 492 | 6 | Unit 6 - Coal | Filterable Particulate | 0.00091204 | lb/MMBtu | Part II | 0 | APT CSU5384 D | 3 |  | 10.9412 | 19 | 0.0099788
3788_3 | Potomac River |  | 3788 | 3 | 3 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | C3 PM STK TronaOn 1206 | 1 |  | 8.8981 | 20 | 0.0088981
3788_3 | Potomac River |  | 3788 | 3 | 3 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | C3 PM STK TronaOff 1206 | 1 |  | 8.8981 | 20 | 0.017796
3788_3 | Potomac River |  | 3788 | 3 | 3 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | C3 PM STK 1206 | 6 |  | 8.8981 | 20 | 0.065253
3788_3 | Potomac River |  | 3788 | 3 | 3 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | CSC345 PM 0909 | 1 |  | 8.8981 | 20 | 0.19576
8219_1 | Ray D Nixon |  | 8219 | 1 | Unit 1 | Filterable Particulate | 0.00096371 | lb/MMBtu | Part II | 0 | APT CSU5384 N | 3 |  | 9.3111 | 21 | 0.0089732
8219_1 | Ray D Nixon |  | 8219 | 1 | Unit 1 | Filterable Particulate | 0.00208 | lb/MMBtu | Part II | 0 | Airtech 2693A-N-A | 3 |  | 9.3111 | 21 | 0.019367
8219_1 | Ray D Nixon |  | 8219 | 1 | Unit 1 | Filterable Particulate | 0.01289 | lb/MMBtu | Part II | 0 | Airtech 2341 | 4 |  | 9.3111 | 21 | 0.12002
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | Dec 2005 PM Compliance Test | 1 |  | 9.1803 | 23 | 0.0091803
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | Feb 2006 PM, HCL, and HF Testing | 1 |  | 9.1803 | 23 | 0.0091803
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.00133 | lb/MMBtu | Part II | 0 | Dec 2008 PM, HCL & HF Testing | 1 |  | 9.1803 | 23 | 0.01221
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | Nov 2009 PM, HCL & HF Testing | 1 |  | 9.1803 | 23 | 0.018361
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.002284 | lb/MMBtu | ERT | No |  | 3 | 947 | 9.1803 | 23 | 0.020968
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | Oct 2006 PM, HCL & HF Testing | 1 |  | 9.1803 | 23 | 0.036721
6761_101 | Rawhide |  | 6761 | 101 | Rawhide101 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | Nov 2007 PM, HCL & HF Testing | 1 |  | 9.1803 | 23 | 0.11934
492_7 | Martin Drake |  | 492 | 7 | Unit 7 - Coal | Filterable Particulate | 0.0009115 | lb/MMBtu | Part II | 0 | APT CSU5384 D | 2 |  | 10.461 | 26 | 0.0095352
492_7 | Martin Drake |  | 492 | 7 | Unit 7 - Coal | Filterable Particulate | 0.00369 | lb/MMBtu | Part II | 0 | Airtech 2693A-D-A | 3 |  | 10.461 | 26 | 0.038601
492_7 | Martin Drake |  | 492 | 7 | Unit 7 - Coal | Filterable Particulate | 0.0040894 | lb/MMBtu | ERT | No |  | 3 | 1190 | 10.461 | 26 | 0.042779
492_7 | Martin Drake |  | 492 | 7 | Unit 7 - Coal | Filterable Particulate | 0.026533 | lb/MMBtu | Part II | 0 | Airtech 2383A | 3 |  | 10.461 | 26 | 0.27757
492_7 | Martin Drake |  | 492 | 7 | Unit 7 - Coal | Filterable Particulate | 0.028667 | lb/MMBtu | Part II | 0 | Airtech 2383 | 3 |  | 10.461 | 26 | 0.29988
55479_3 | Wygen 1 |  | 55479 | 3 | WYG1Cfg | Filterable Particulate | 0.00082645 | lb/MMBtu | ERT | No |  | 4 | 1488 | 11.5714 | 27 | 0.0095632
897_Unit 2 | Vermilion |  | 897 | Unit 2 | 002 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | 8 | 1 |  | 9.7818 | 28 | 0.0097818
897_Unit 2 | Vermilion |  | 897 | Unit 2 | 002 | Filterable Particulate | 0.0013361 | lb/MMBtu | ERT | No |  | 3 | 1938 | 9.7818 | 28 | 0.013069
897_Unit 2 | Vermilion |  | 897 | Unit 2 | 002 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 9.7818 | 28 | 0.019564
10673_BLR A | AES Hawaii |  | 10673 | BLR A | 001 | Filterable Particulate | 0.0009892 | lb/MMBtu | ERT | No |  | 6 | 779 | 10.0631 | 29 | 0.0099544
2277_1 | Sheldon Station |  | 2277 | 1 | U1 | Filterable Particulate | 0.0009369 | lb/MMBtu | ERT | No |  | 6 | 1832 | 10.7344 | 30 | 0.010057
52071_5B | Sandow Station |  | 52071 | 5B | 5B | Filterable Particulate | 0.00098701 | lb/MMBtu | ERT | No |  | 6 | 830 | 10.4834 | 31 | 0.010347
52071_5B | Sandow Station |  | 52071 | 5B | 5B | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | 0 | 2-Source Emissions Survey, Stacks | 3 |  | 10.4834 | 31 | 0.059406
891_Boiler 9 | Havana |  | 891 | Boiler 9 | Boiler 9 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | 5 | 1 |  | 10.4574 | 32 | 0.010457
891_Boiler 9 | Havana |  | 891 | Boiler 9 | Boiler 9 | Filterable Particulate | 0.0027457 | lb/MMBtu | ERT | No |  | 6 | 1726 | 10.4574 | 32 | 0.028713
6180_1 | Oak Grove |  | 6180 | 1 | OG1 | Filterable Particulate | 0.0010178 | lb/MMBtu | Part II | 0 | 1-Compliance Test Report | 3 |  | 10.9792 | 33 | 0.011175
6180_1 | Oak Grove |  | 6180 | 1 | OG1 | Filterable Particulate | 0.0084305 | lb/MMBtu | ERT | No |  | 3 | 2025 | 10.9792 | 33 | 0.092561
470_2 | Comanche |  | 470 | 2 | Unit 2 | Filterable Particulate | 0.0012059 | lb/MMBtu | ERT | No |  | 3 | 1449 | 9.5397 | 34 | 0.011504
897_Unit 1 | Vermilion |  | 897 | Unit 1 | 001 | Filterable Particulate | 0.001 | lb/MMBtu | Part II | 0 | 8 | 1 |  | 11.5417 | 35 | 0.011542
897_Unit 1 | Vermilion |  | 897 | Unit 1 | 001 | Filterable Particulate | 0.0013361 | lb/MMBtu | ERT | No |  | 3 | 1938 | 11.5417 | 35 | 0.015421
897_Unit 1 | Vermilion |  | 897 | Unit 1 | 001 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 11.5417 | 35 | 0.023083
7504_2 | Neil Simpson II |  | 7504 | 2 | NS2Cfg | Filterable Particulate | 0.00092616 | lb/MMBtu | ERT | No |  | 6 | 1382 | 12.5 | 36 | 0.011577
6077_1 | Gerald Gentleman |  | 6077 | 1 | U1 | Filterable Particulate | 0.0011321 | lb/MMBtu | ERT | No |  | 6 | 2170 | 10.5427 | 37 | 0.011935
3845_BD22 | TransAlta Centralia Generation |  | 3845 | BD22 | BW22CONFIG | Filterable Particulate | 0.00088166 | lb/MMBtu | Part II | 0 | 2006 Compliance Unit 2 | 3 |  | 13.6561 | 38 | 0.01204
3845_BD22 | TransAlta Centralia Generation |  | 3845 | BD22 | BW22CONFIG | Filterable Particulate | 0.0014414 | lb/MMBtu | Part II | 0 | 2007 Compliance Unit 2 | 3 |  | 13.6561 | 38 | 0.019684
3845_BD22 | TransAlta Centralia Generation |  | 3845 | BD22 | BW22CONFIG | Filterable Particulate | 0.0016187 | lb/MMBtu | ERT | No |  | 3 | 1706 | 13.6561 | 38 | 0.022105
3845_BD22 | TransAlta Centralia Generation |  | 3845 | BD22 | BW22CONFIG | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | 2008 Compliance Unit 2 | 3 |  | 13.6561 | 38 | 0.04552
3845_BD22 | TransAlta Centralia Generation |  | 3845 | BD22 | BW22CONFIG | Filterable Particulate | 0.0042333 | lb/MMBtu | Part II | 0 | 2009 Compliance Unit 2 | 3 |  | 13.6561 | 38 | 0.057811
3845_BD22 | TransAlta Centralia Generation |  | 3845 | BD22 | BW22CONFIG | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | 2005 Compliance Unit 2 | 3 |  | 13.6561 | 38 | 0.086489
2079_5A | Hawthorn |  | 2079 | 5A | 5A | Filterable Particulate | 0.0011025 | lb/MMBtu | ERT | No |  | 6 | 1398 | 11.1111 | 39 | 0.01225
1626_3 | Salem Harbor |  | 1626 | 3 | Unit 3 | Filterable Particulate | 0.0010546 | lb/MMBtu | Part II | 0 | 2008Unit3PM | 1 |  | 11.7495 | 40 | 0.012391
1626_3 | Salem Harbor |  | 1626 | 3 | Unit 3 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | 2007Unit3PM | 1 |  | 11.7495 | 40 | 0.035249
1626_3 | Salem Harbor |  | 1626 | 3 | Unit 3 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 2009Unit3PM | 1 |  | 11.7495 | 40 | 0.070497
1626_3 | Salem Harbor |  | 1626 | 3 | Unit 3 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | 2006Unit3PM | 1 |  | 11.7495 | 40 | 0.10575
1626_3 | Salem Harbor |  | 1626 | 3 | Unit 3 | Filterable Particulate | 0.034 | lb/MMBtu | Part II | 0 | 2005Unit3PM | 1 |  | 11.7495 | 40 | 0.39948
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.00135 | lb/MMBtu | Part II | 0 | AWC/PC/PPR April 2006 | 3 |  | 9.4711 | 41 | 0.012786
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.00176 | lb/MMBtu | Part II | 0 | Compliance Stack Testing - April 2006 | 3 |  | 9.4711 | 41 | 0.016669
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.0020933 | lb/MMBtu | Part II | 0 | AWC/TDF Stack Test April 2006 | 3 |  | 9.4711 | 41 | 0.019826
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.0029167 | lb/MMBtu | Part II | 0 | AWC/HCA April 2006 | 3 |  | 9.4711 | 41 | 0.027624
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.0046 | lb/MMBtu | Part II | 0 | PM Testing May 2009 | 3 |  | 9.4711 | 41 | 0.043567
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.0066 | lb/MMBtu | Part II | 0 | TDF 2009 Stack Test - #226-013 | 3 |  | 9.4711 | 41 | 0.062509
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.0067667 | lb/MMBtu | Part II | 0 | TDF 2008 Stack Test - #226-007 | 3 |  | 9.4711 | 41 | 0.064088
50888_BLR1 | Northampton Generating Company, L.P. |  | 50888 | BLR1 | GEN1 | Filterable Particulate | 0.0088011 | lb/MMBtu | ERT | No |  | 3 | 5000 | 9.4711 | 41 | 0.083356
4041_7 | South Oak Creek |  | 4041 | 7 | OCPP-B7 | Filterable Particulate | 0.0015333 | lb/MMBtu | ERT | No |  | 6 | 1021 | 8.925 | 42 | 0.013684
4041_7 | South Oak Creek |  | 4041 | 7 | OCPP-B7 | Filterable Particulate | 0.0039 | lb/MMBtu | Part II | 0 | OCPP-PM-B7-6.2005 | 3 |  | 8.925 | 42 | 0.034807
4041_7 | South Oak Creek |  | 4041 | 7 | OCPP-B7 | Filterable Particulate | 0.0040333 | lb/MMBtu | Part II | 0 | OCPP-PM-B7-7.2007 | 3 |  | 8.925 | 42 | 0.035998
4041_7 | South Oak Creek |  | 4041 | 7 | OCPP-B7 | Filterable Particulate | 0.0072 | lb/MMBtu | Part II | 0 | OCPP-PM-B7-10.2009 | 3 |  | 8.925 | 42 | 0.06426
4041_7 | South Oak Creek |  | 4041 | 7 | OCPP-B7 | Filterable Particulate | 0.011719 | lb/MMBtu | ERT | No |  | 6 | 731 | 8.925 | 42 | 0.10459
4041_7 | South Oak Creek |  | 4041 | 7 | OCPP-B7 | Filterable Particulate | 15.2003 | lb/MMBtu | Part II | 0 | OCPP-PM-B7B8-6.2005 | 4 |  | 8.925 | 42 | 135.6631
10673_BLR B | AES Hawaii |  | 10673 | BLR B | 002 | Filterable Particulate | 0.0014764 | lb/MMBtu | ERT | No |  | 6 | 77922 | 9.3025 | 43 | 0.013734
2451_Unit 3 | San Juan |  | 2451 | Unit 3 | Unit 3 | Filterable Particulate | 0.0013557 | lb/MMBtu | ERT | No |  | 3 | 23152 | 10.5846 | 44 | 0.014349
1082_3 | Walter Scott Jr. Energy Center |  | 1082 | 3 | 3 | Filterable Particulate | 0.0014273 | lb/MMBtu | Part II | 0 | 6/2009 PM | 1 |  | 10.0654 | 45 | 0.014366
3845_BD21 | TransAlta Centralia Generation |  | 3845 | BD21 | BW21CONFIG | Filterable Particulate | 0.0011428 | lb/MMBtu | Part II | 0 | 2006 Compliance Unit 1 | 3 |  | 12.8408 | 46 | 0.014675
3845_BD21 | TransAlta Centralia Generation |  | 3845 | BD21 | BW21CONFIG | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | 0 | 2009 Compliance Unit 1 | 3 |  | 12.8408 | 46 | 0.034242
3845_BD21 | TransAlta Centralia Generation |  | 3845 | BD21 | BW21CONFIG | Filterable Particulate | 0.0031333 | lb/MMBtu | Part II | 0 | 2008 Compliance Unit 1 | 3 |  | 12.8408 | 46 | 0.040234
3845_BD21 | TransAlta Centralia Generation |  | 3845 | BD21 | BW21CONFIG | Filterable Particulate | 0.0032799 | lb/MMBtu | ERT | No |  | 3 | 1687 | 12.8408 | 46 | 0.042116
3845_BD21 | TransAlta Centralia Generation |  | 3845 | BD21 | BW21CONFIG | Filterable Particulate | 0.0033667 | lb/MMBtu | Part II | 0 | 2007 Compliance Unit 1 | 3 |  | 12.8408 | 46 | 0.043231
3845_BD21 | TransAlta Centralia Generation |  | 3845 | BD21 | BW21CONFIG | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | 0 | 2005 Compliance Unit 1 | 3 |  | 12.8408 | 46 | 0.072765
7210_COP1 | Cope |  | 7210 | COP1 | COP001 | Filterable Particulate | 0.0016 | lb/MMBtu | Part II | 0 | PM-10/09 | 1 |  | 9.2043 | 47 | 0.014727
7210_COP1 | Cope |  | 7210 | COP1 | COP001 | Filterable Particulate | 0.0036154 | lb/MMBtu | ERT | No |  | 3 | 1249 | 9.2043 | 47 | 0.033278
3944_2 | Harrison Power Station |  | 3944 | 2 | Boiler2 | Filterable Particulate | 0.0018667 | lb/MMBtu | Part II | 0 | 4 | 3 |  | 8.7312 | 48 | 0.016298
3944_2 | Harrison Power Station |  | 3944 | 2 | Boiler2 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 0 | 12 | 3 |  | 8.7312 | 48 | 0.14552
3944_2 | Harrison Power Station |  | 3944 | 2 | Boiler2 | Filterable Particulate | 0.019233 | lb/MMBtu | Part II | 0 | 1 | 3 |  | 8.7312 | 48 | 0.16793
3944_2 | Harrison Power Station |  | 3944 | 2 | Boiler2 | Filterable Particulate | 0.051333 | lb/MMBtu | Part II | 0 | 7 | 3 |  | 8.7312 | 48 | 0.4482
6002_4 | James H. Miller Jr. |  | 6002 | 4 | Unit 4 | Filterable Particulate | 0.0017209 | lb/MMBtu | ERT | No |  | 3 | 203612 | 9.6494 | 49 | 0.016606
1554_2 | Herbert A. Wagner |  | 1554 | 2 | 002 | Filterable Particulate | 0.0016609 | lb/MMBtu | ERT | No |  | 3 | 2195 | 10.2621 | 50 | 0.017045
1710_Unit 2 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 2 | JHC2-Conf | Filterable Particulate | 0.0019333 | lb/MMBtu | Part II | 0 | JHC12-PM 2008 Compliance Testing | 3 |  | 9.0695 | 51 | 0.017534
1710_Unit 2 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 2 | JHC2-Conf | Filterable Particulate | 0.01108 | lb/MMBtu | ERT | No |  | 3 | 1642 | 9.0695 | 51 | 0.10049
1710_Unit 2 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 2 | JHC2-Conf | Filterable Particulate | 0.011533 | lb/MMBtu | Part II | 0 | JHC12 - 2005 PM Compliance Testing | 3 |  | 9.0695 | 51 | 0.1046
3287_MCM1 | McMeekin |  | 3287 | MCM1 | MCM001 | Filterable Particulate | 0.0021 | lb/MMBtu | Part II | 0 | PM-01/07-MCM1 | 1 |  | 8.4704 | 52 | 0.017788
3287_MCM1 | McMeekin |  | 3287 | MCM1 | MCM001 | Filterable Particulate | 0.0029 | lb/MMBtu | Part II | 0 | PM-01/08-MCM1 | 1 |  | 8.4704 | 52 | 0.024564
3287_MCM1 | McMeekin |  | 3287 | MCM1 | MCM001 | Filterable Particulate | 0.0031 | lb/MMBtu | Part II | 0 | PM-01/05-MCM1 | 1 |  | 8.4704 | 52 | 0.026258
3287_MCM1 | McMeekin |  | 3287 | MCM1 | MCM001 | Filterable Particulate | 0.0052 | lb/MMBtu | Part II | 0 | PM-01/06-MCM1 | 1 |  | 8.4704 | 52 | 0.044046
3287_MCM1 | McMeekin |  | 3287 | MCM1 | MCM001 | Filterable Particulate | 0.0066473 | lb/MMBtu | ERT | No |  | 3 | 876 | 8.4704 | 52 | 0.056305
3287_MCM1 | McMeekin |  | 3287 | MCM1 | MCM001 | Filterable Particulate | 0.0092 | lb/MMBtu | Part II | 0 | PM-01/09-MCM1 | 1 |  | 8.4704 | 52 | 0.077927
87_1 | Escalante |  | 87 | 1 | 1 | Filterable Particulate | 0.0019708 | lb/MMBtu | Part II | 0 | 2007 PM Test | 3 |  | 9.1 | 53 | 0.017935
87_1 | Escalante |  | 87 | 1 | 1 | Filterable Particulate | 0.0025747 | lb/MMBtu | Part II | 0 | 2009 PM Test | 3 |  | 9.1 | 53 | 0.02343
87_1 | Escalante |  | 87 | 1 | 1 | Filterable Particulate | 0.0051528 | lb/MMBtu | Part II | 0 | 2006 PM Test | 3 |  | 9.1 | 53 | 0.04689
87_1 | Escalante |  | 87 | 1 | 1 | Filterable Particulate | 0.0053043 | lb/MMBtu | Part II | 0 | 2008 PM Test | 3 |  | 9.1 | 53 | 0.048269
87_1 | Escalante |  | 87 | 1 | 1 | Filterable Particulate | 0.0091475 | lb/MMBtu | Part II | 0 | 2009 Condensable PM | 3 |  | 9.1 | 53 | 0.083242
87_1 | Escalante |  | 87 | 1 | 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | 2005 PM Test | 3 |  | 9.1 | 53 | 0.1183
1710_Unit 1 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 1 | JHC1-Conf | Filterable Particulate | 0.0019333 | lb/MMBtu | Part II | 0 | JHC12-PM 2008 Compliance Testing | 3 |  | 9.3467 | 54 | 0.01807
1710_Unit 1 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 1 | JHC1-Conf | Filterable Particulate | 0.01108 | lb/MMBtu | ERT | No |  | 3 | 1642 | 9.3467 | 54 | 0.10356
1710_Unit 1 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 1 | JHC1-Conf | Filterable Particulate | 0.011533 | lb/MMBtu | Part II | 0 | JHC12 - 2005 PM Compliance Testing | 3 |  | 9.3467 | 54 | 0.1078
6181_2 | J T Deely |  | 6181 | 2 | 2 | Filterable Particulate | 0.0019178 | lb/MMBtu | ERT | No |  | 6 | 452145 | 9.4467 | 55 | 0.018116
6181_2 | J T Deely |  | 6181 | 2 | 2 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | JTD Units 1 & 2 June 2007 Test | 3 |  | 9.4467 | 55 | 0.031489
6181_1 | J T Deely |  | 6181 | 1 | 1 | Filterable Particulate | 0.0019178 | lb/MMBtu | ERT | No |  | 6 | 452145 | 9.4467 | 56 | 0.018116
6181_1 | J T Deely |  | 6181 | 1 | 1 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | JTD Units 1 & 2 June 2007 Test | 3 |  | 9.4467 | 56 | 0.031489
4078_4 | Weston |  | 4078 | 4 | W4 | Filterable Particulate | 0.0021071 | lb/MMBtu | ERT | No |  | 6 | 1611 | 9.0045 | 57 | 0.018973
26_3 | E. C. Gaston |  | 26 | 3 | Unit 3 | Filterable Particulate | 0.0021 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (April 15, 2005) | 3 |  | 9.1214 | 58 | 0.019155
26_3 | E. C. Gaston |  | 26 | 3 | Unit 3 | Filterable Particulate | 0.0073 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (April 26, 2006) | 3 |  | 9.1214 | 58 | 0.066586
26_3 | E. C. Gaston |  | 26 | 3 | Unit 3 | Filterable Particulate | 0.010133 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (May 28, 2008) | 3 |  | 9.1214 | 58 | 0.09243
26_3 | E. C. Gaston |  | 26 | 3 | Unit 3 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (June 2, 2009) | 3 |  | 9.1214 | 58 | 0.10034
26_3 | E. C. Gaston |  | 26 | 3 | Unit 3 | Filterable Particulate | 0.0195 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (February 13, 2007) | 3 |  | 9.1214 | 58 | 0.17787
2712_2 | Roxboro Steam Electric Plant |  | 2712 | 2 | Rox_Cfg_2c | Filterable Particulate | 0.0019832 | lb/MMBtu | ERT | No |  | 6 | 985 | 9.8051 | 59 | 0.019446
2712_2 | Roxboro Steam Electric Plant |  | 2712 | 2 | Rox_Cfg_2c | Filterable Particulate | 0.0046533 | lb/MMBtu | Part II | 0 | Rox_Blr_2_Test_7e | 3 |  | 9.8051 | 59 | 0.045626
2712_2 | Roxboro Steam Electric Plant |  | 2712 | 2 | Rox_Cfg_2c | Filterable Particulate | 0.017333 | lb/MMBtu | Part II | 0 | Rox_Blr_2_Test_10h | 6 |  | 9.8051 | 59 | 0.16996
2712_2 | Roxboro Steam Electric Plant |  | 2712 | 2 | Rox_Cfg_2c | Filterable Particulate | 0.022633 | lb/MMBtu | Part II | 0 | Rox_Blr_2_Test_8i | 3 |  | 9.8051 | 59 | 0.22192
2712_2 | Roxboro Steam Electric Plant |  | 2712 | 2 | Rox_Cfg_2c | Filterable Particulate | 0.068667 | lb/MMBtu | Part II | 0 | Rox_Blr_2_Test_9h | 3 |  | 9.8051 | 59 | 0.67328
2712_2 | Roxboro Steam Electric Plant |  | 2712 | 2 | Rox_Cfg_2c | Filterable Particulate | 0.070667 | lb/MMBtu | Part II | 0 | Rox_Blr_2_Test_5d | 3 |  | 9.8051 | 59 | 0.6929
6041_4 | H L Spurlock Station |  | 6041 | 4 | Unit 04 | Filterable Particulate | 0.0021333 | lb/MMBtu | Part II | 0 | Compliance_PM_05/27/09 | 3 |  | 9.3333 | 60 | 0.019911
6041_4 | H L Spurlock Station |  | 6041 | 4 | Unit 04 | Filterable Particulate | 0.0062127 | lb/MMBtu | ERT | No |  | 3 | 995 | 9.3333 | 60 | 0.057985
3287_MCM2 | McMeekin |  | 3287 | MCM2 | MCM002 | Filterable Particulate | 0.0024 | lb/MMBtu | Part II | 0 | PM-01/06-MCM2 | 1 |  | 8.3432 | 61 | 0.020024
3287_MCM2 | McMeekin |  | 3287 | MCM2 | MCM002 | Filterable Particulate | 0.0044836 | lb/MMBtu | ERT | No |  | 3 | 8761 | 8.3432 | 61 | 0.037408
3287_MCM2 | McMeekin |  | 3287 | MCM2 | MCM002 | Filterable Particulate | 0.0051 | lb/MMBtu | Part II | 0 | PM-1/07-MCM2 | 1 |  | 8.3432 | 61 | 0.04255
3287_MCM2 | McMeekin |  | 3287 | MCM2 | MCM002 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | PM-01/09-MCM2 | 1 |  | 8.3432 | 61 | 0.050059
3287_MCM2 | McMeekin |  | 3287 | MCM2 | MCM002 | Filterable Particulate | 0.0091 | lb/MMBtu | Part II | 0 | PM-01/05-MCM2 | 1 |  | 8.3432 | 61 | 0.075923
3287_MCM2 | McMeekin |  | 3287 | MCM2 | MCM002 | Filterable Particulate | 0.0095 | lb/MMBtu | Part II | 0 | PM-01/08-MCM2 | 1 |  | 8.3432 | 61 | 0.07926
2324_1 | Reid Gardner |  | 2324 | 1 | 1 | Filterable Particulate | 0.0019244 | lb/MMBtu | ERT | No |  | 3 | 1972 | 10.9459 | 62 | 0.021065
2324_1 | Reid Gardner |  | 2324 | 1 | 1 | Filterable Particulate | 0.009795 | lb/MMBtu | Part II | 0 | U1_2009_COMPLIANCE | 2 |  | 10.9459 | 62 | 0.10722
2324_1 | Reid Gardner |  | 2324 | 1 | 1 | Filterable Particulate | 0.028333 | lb/MMBtu | Part II | 0 | U1_2009_BAGHOUSE_STACK | 3 |  | 10.9459 | 62 | 0.31014
2324_1 | Reid Gardner |  | 2324 | 1 | 1 | Filterable Particulate | 0.028333 | lb/MMBtu | Part II | 0 | U2_2009_BAGHOUSE GUARANTEE STACK | 3 |  | 10.9459 | 62 | 0.31014
2706_1 | Asheville Steam Electric Plant |  | 2706 | 1 | Ash_Cfg_1d | Filterable Particulate | 0.0022867 | lb/MMBtu | Part II | 0 | Ash_Blr_1_Test_8p | 9 |  | 9.2464 | 63 | 0.021143
2706_1 | Asheville Steam Electric Plant |  | 2706 | 1 | Ash_Cfg_1d | Filterable Particulate | 0.0030191 | lb/MMBtu | ERT | No |  | 6 | 1738 | 9.2464 | 63 | 0.027916
2706_1 | Asheville Steam Electric Plant |  | 2706 | 1 | Ash_Cfg_1d | Filterable Particulate | 0.02 | lb/MMBtu | Part II | 0 | Ash_Blr_1_Test_11b | 3 |  | 9.2464 | 63 | 0.18493
2706_1 | Asheville Steam Electric Plant |  | 2706 | 1 | Ash_Cfg_1d | Filterable Particulate | 0.026 | lb/MMBtu | Part II | 0 | Ash_Blr_1_Test_10h | 3 |  | 9.2464 | 63 | 0.24041
2706_1 | Asheville Steam Electric Plant |  | 2706 | 1 | Ash_Cfg_1d | Filterable Particulate | 0.061 | lb/MMBtu | Part II | 0 | Ash_Blr_1_Test_9d | 3 |  | 9.2464 | 63 | 0.56403
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | C1PM2008 | 1 |  | 10.659 | 64 | 0.021318
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.0021898 | lb/MMBtu | ERT | No |  | 3 | 1117 | 10.659 | 64 | 0.023341
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | C1PM2009 | 1 |  | 10.659 | 64 | 0.031977
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | C1PM2005 | 1 |  | 10.659 | 64 | 0.11725
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | C1PM2006 | 1 |  | 10.659 | 64 | 0.14923
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | C1PM2007 | 1 |  | 10.659 | 64 | 0.14923
130_1 | Cross |  | 130 | 1 | C1 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | C1PM2007R | 1 |  | 10.659 | 64 | 0.15989
207_PPBoiler1 | St Johns River Power Park |  | 207 | PPBoiler1 | PPUnit1Configuration | Filterable Particulate | 0.0023333 | lb/MMBtu | Part II | 0 | S1_2009_PM | 3 |  | 9.3091 | 65 | 0.021721
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | 2006 Unit A | 3 |  | 11.4 | 66 | 0.0228
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.0021333 | lb/MMBtu | Part II | 0 | 2005 Unit A | 3 |  | 11.4 | 66 | 0.02432
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 2008 Unit B | 3 |  | 11.4 | 66 | 0.0456
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.0054 | lb/MMBtu | Part II | 0 | 2005 Unit B | 3 |  | 11.4 | 66 | 0.06156
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.0066 | lb/MMBtu | Part II | 0 | 2007 Unit A | 3 |  | 11.4 | 66 | 0.07524
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | 2008 Unit A | 3 |  | 11.4 | 66 | 0.0798
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | 2007 Unit B | 3 |  | 11.4 | 66 | 0.1482
54238_N64516 | Port of Stockton District Energy Facility |  | 54238 | N64516 | 1 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 0 | 2006 Unit B | 3 |  | 11.4 | 66 | 0.19
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | 2006 Unit A | 3 |  | 11.4 | 67 | 0.0228
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.0021333 | lb/MMBtu | Part II | 0 | 2005 Unit A | 3 |  | 11.4 | 67 | 0.02432
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 2008 Unit B | 3 |  | 11.4 | 67 | 0.0456
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.0054 | lb/MMBtu | Part II | 0 | 2005 Unit B | 3 |  | 11.4 | 67 | 0.06156
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.0066 | lb/MMBtu | Part II | 0 | 2007 Unit A | 3 |  | 11.4 | 67 | 0.07524
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | 2008 Unit A | 3 |  | 11.4 | 67 | 0.0798
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | 2007 Unit B | 3 |  | 11.4 | 67 | 0.1482
54238_N64514 | Port of Stockton District Energy Facility |  | 54238 | N64514 | 1 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 0 | 2006 Unit B | 3 |  | 11.4 | 67 | 0.19
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | 0 | PM2009_Sep_4b | 3 |  | 8.7607 | 68 | 0.023362
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | PM2009_Aug_4 | 3 |  | 8.7607 | 68 | 0.026282
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | PM2009_Nov_4a | 1 |  | 8.7607 | 68 | 0.035043
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | PM2009_Sep_4a | 3 |  | 8.7607 | 68 | 0.035043
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | PM2009_Nov_4b | 2 |  | 8.7607 | 68 | 0.043804
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | 0 | PM2010_Jan4_20 | 2 |  | 8.7607 | 68 | 0.048184
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | 0 | PM2010_Jan4_25 | 2 |  | 8.7607 | 68 | 0.048184
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.0065 | lb/MMBtu | Part II | 0 | PM2010_Jan4_30 | 2 |  | 8.7607 | 68 | 0.056945
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.0065 | lb/MMBtu | Part II | 0 | PM2010_Jan4_40 | 2 |  | 8.7607 | 68 | 0.056945
1733_4 | Monroe Power Plant |  | 1733 | 4 | MN4-Config | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | PM2010_Jan4_35 | 2 |  | 8.7607 | 68 | 0.061325
1379_10 | Shawnee |  | 1379 | 10 | 10 | Filterable Particulate | 0.0023333 | lb/MMBtu | Part II | 0 | SHF10 - 2006 | 3 |  | 10.2857 | 69 | 0.024
1379_10 | Shawnee |  | 1379 | 10 | 10 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | SHF10 - 2005 | 3 |  | 10.2857 | 69 | 0.034286
1379_10 | Shawnee |  | 1379 | 10 | 10 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | SHF10 - 2007 | 3 |  | 10.2857 | 69 | 0.078857
1379_10 | Shawnee |  | 1379 | 10 | 10 | Filterable Particulate | 0.051333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2005 | 3 |  | 10.2857 | 69 | 0.528
1379_10 | Shawnee |  | 1379 | 10 | 10 | Filterable Particulate | 0.088333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2009 | 3 |  | 10.2857 | 69 | 0.90857
8223_2 | Springerville |  | 8223 | 2 | 2 | Filterable Particulate | 0.0027 | lb/MMBtu | Part II | 0 | U2 PERF 06JUN05 | 1 |  | 8.907 | 70 | 0.024049
8223_2 | Springerville |  | 8223 | 2 | 2 | Filterable Particulate | 0.0069 | lb/MMBtu | Part II | 0 | U2 PERF 08MAY13 | 1 |  | 8.907 | 70 | 0.061458
8223_2 | Springerville |  | 8223 | 2 | 2 | Filterable Particulate | 0.0073 | lb/MMBtu | Part II | 0 | U2 PERF 07JUN5-8 | 1 |  | 8.907 | 70 | 0.065021
8223_2 | Springerville |  | 8223 | 2 | 2 | Filterable Particulate | 0.0083 | lb/MMBtu | Part II | 0 | U2 PERF 05JUN05 | 1 |  | 8.907 | 70 | 0.073928
8223_2 | Springerville |  | 8223 | 2 | 2 | Filterable Particulate | 0.0149 | lb/MMBtu | Part II | 0 | U2 PERF 09MAY19 | 1 |  | 8.907 | 70 | 0.13271
4041_8 | South Oak Creek |  | 4041 | 8 | OCPP-B8 | Filterable Particulate | 0.0027333 | lb/MMBtu | Part II | 0 | OCPP-PM-B8-6.2005 | 3 |  | 8.9554 | 71 | 0.024478
4041_8 | South Oak Creek |  | 4041 | 8 | OCPP-B8 | Filterable Particulate | 0.01235 | lb/MMBtu | Part II | 0 | OCPP-PM-B8-7.2007 | 4 |  | 8.9554 | 71 | 0.1106
4041_8 | South Oak Creek |  | 4041 | 8 | OCPP-B8 | Filterable Particulate | 8.6329 | lb/MMBtu | Part II | 0 | OCPP-PM-B7B8-6.2005 | 4 |  | 8.9554 | 71 | 77.3105
645_4 | Big Bend |  | 645 | 4 | BB04_SCR_iso | Filterable Particulate | 0.0026473 | lb/MMBtu | Part II | 0 | BB#4_ECOTHERM | 1 |  | 9.3118 | 72 | 0.024651
645_4 | Big Bend |  | 645 | 4 | BB04_SCR_iso | Filterable Particulate | 0.0077749 | lb/MMBtu | Part II | 0 | BB#4_FY2009 | 1 |  | 9.3118 | 72 | 0.072398
645_4 | Big Bend |  | 645 | 4 | BB04_SCR_iso | Filterable Particulate | 0.0079 | lb/MMBtu | Part II | 0 | BB#4_FY2008 | 1 |  | 9.3118 | 72 | 0.073563
4078_3 | Weston |  | 4078 | 3 | W3 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | 0 | W3 PM 2009 | 3 |  | 9.364 | 73 | 0.024971
4078_3 | Weston |  | 4078 | 3 | W3 | Filterable Particulate | 0.0066345 | lb/MMBtu | ERT | No |  | 6 | 1606 | 9.364 | 73 | 0.062125
4078_3 | Weston |  | 4078 | 3 | W3 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | W3 PM 2005 | 3 |  | 9.364 | 73 | 0.09364
3138_3 | New Castle Plant |  | 3138 | 3 | NC3-2 | Filterable Particulate | 0.0024 | lb/MMBtu | Part II | 0 | NC-50 | 4 |  | 10.4592 | 74 | 0.025102
3138_3 | New Castle Plant |  | 3138 | 3 | NC3-2 | Filterable Particulate | 0.0039867 | lb/MMBtu | Part II | 0 | NC-39B | 3 |  | 10.4592 | 74 | 0.041697
3138_3 | New Castle Plant |  | 3138 | 3 | NC3-2 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | NC-21 | 3 |  | 10.4592 | 74 | 0.090646
3138_3 | New Castle Plant |  | 3138 | 3 | NC3-2 | Filterable Particulate | 0.030667 | lb/MMBtu | Part II | 0 | NC-39A | 3 |  | 10.4592 | 74 | 0.32075
108_SGU1 | HOLCOMB |  | 108 | SGU1 | SGU1 | Filterable Particulate | 0.0028667 | lb/MMBtu | Part II | 0 | 2009-10150 | 3 |  | 8.7571 | 75 | 0.025104
108_SGU1 | HOLCOMB |  | 108 | SGU1 | SGU1 | Filterable Particulate | 0.0065333 | lb/MMBtu | Part II | 0 | M093106 | 3 |  | 8.7571 | 75 | 0.057213
2706_2 | Asheville Steam Electric Plant |  | 2706 | 2 | Ash_Cfg_2 | Filterable Particulate | 0.0027 | lb/MMBtu | Part II | 0 | Ash_Blr_2_Test_7t | 3 |  | 9.3235 | 76 | 0.025174
2706_2 | Asheville Steam Electric Plant |  | 2706 | 2 | Ash_Cfg_2 | Filterable Particulate | 0.00271 | lb/MMBtu | Part II | 0 | Ash_Blr_2_Test_7s | 3 |  | 9.3235 | 76 | 0.025267
2706_2 | Asheville Steam Electric Plant |  | 2706 | 2 | Ash_Cfg_2 | Filterable Particulate | 0.0035846 | lb/MMBtu | ERT | No |  | 6 | 1743 | 9.3235 | 76 | 0.033421
2706_2 | Asheville Steam Electric Plant |  | 2706 | 2 | Ash_Cfg_2 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | Ash_Blr_2_Test_3 | 6 |  | 9.3235 | 76 | 0.07148
2706_2 | Asheville Steam Electric Plant |  | 2706 | 2 | Ash_Cfg_2 | Filterable Particulate | 0.011333 | lb/MMBtu | Part II | 0 | Ash_Blr_2_Test_5d | 3 |  | 9.3235 | 76 | 0.10567
2706_2 | Asheville Steam Electric Plant |  | 2706 | 2 | Ash_Cfg_2 | Filterable Particulate | 0.02 | lb/MMBtu | Part II | 0 | Ash_Blr_2_Test_8h | 3 |  | 9.3235 | 76 | 0.18647
1626_2 | Salem Harbor |  | 1626 | 2 | Unit 2 | Filterable Particulate | 0.002 | lb/MMBtu | Part II | 0 | 2005Unit2PM | 1 |  | 12.8741 | 77 | 0.025748
1626_2 | Salem Harbor |  | 1626 | 2 | Unit 2 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 2006Unit2PM | 1 |  | 12.8741 | 77 | 0.077244
1626_2 | Salem Harbor |  | 1626 | 2 | Unit 2 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 2007Unit2PM | 1 |  | 12.8741 | 77 | 0.077244
1626_2 | Salem Harbor |  | 1626 | 2 | Unit 2 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 2009Unit2PM | 1 |  | 12.8741 | 77 | 0.12874
1626_2 | Salem Harbor |  | 1626 | 2 | Unit 2 | Filterable Particulate | 0.066 | lb/MMBtu | Part II | 0 | 2008Unit2PM | 1 |  | 12.8741 | 77 | 0.84969
8226_1 | Cheswick Power Plant |  | 8226 | 1 | CH2 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | 0 | CH-23B | 3 |  | 9.8039 | 78 | 0.026144
8226_1 | Cheswick Power Plant |  | 8226 | 1 | CH2 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | CH-31B | 3 |  | 9.8039 | 78 | 0.10784
8226_1 | Cheswick Power Plant |  | 8226 | 1 | CH2 | Filterable Particulate | 0.018667 | lb/MMBtu | Part II | 0 | CH-46 | 3 |  | 9.8039 | 78 | 0.18301
8226_1 | Cheswick Power Plant |  | 8226 | 1 | CH2 | Filterable Particulate | 0.033667 | lb/MMBtu | Part II | 0 | PRB20 | 3 |  | 9.8039 | 78 | 0.33007
8226_1 | Cheswick Power Plant |  | 8226 | 1 | CH2 | Filterable Particulate | 0.035667 | lb/MMBtu | Part II | 0 | CH-32A | 3 |  | 9.8039 | 78 | 0.34967
8226_1 | Cheswick Power Plant |  | 8226 | 1 | CH2 | Filterable Particulate | 0.0595 | lb/MMBtu | Part II | 0 | CH-31 | 4 |  | 9.8039 | 78 | 0.58333
50_6 | Widows Creek |  | 50 | 6 | 6 | Filterable Particulate | 0.0023333 | lb/MMBtu | Part II | 0 | WCF6 - 2007 | 3 |  | 11.3016 | 79 | 0.02637
50_6 | Widows Creek |  | 50 | 6 | 6 | Filterable Particulate | 0.0026667 | lb/MMBtu | Part II | 0 | WCF6 - 2008 | 3 |  | 11.3016 | 79 | 0.030138
50_6 | Widows Creek |  | 50 | 6 | 6 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | WCF6 - 2005 | 3 |  | 11.3016 | 79 | 0.037672
50_6 | Widows Creek |  | 50 | 6 | 6 | Filterable Particulate | 0.0046667 | lb/MMBtu | Part II | 0 | WCF6 - 2006 | 3 |  | 11.3016 | 79 | 0.052741
8224_1 | North Valmy |  | 8224 | 1 | 1 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | 0 | U1_2006_COMPLIANCE | 3 |  | 10.5133 | 80 | 0.026634
8224_1 | North Valmy |  | 8224 | 1 | 1 | Filterable Particulate | 0.0035333 | lb/MMBtu | Part II | 0 | U1_2008_COMPLIANCE | 3 |  | 10.5133 | 80 | 0.037147
8224_1 | North Valmy |  | 8224 | 1 | 1 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | U1_2007_COMPLIANCE | 1 |  | 10.5133 | 80 | 0.042053
8223_1 | Springerville |  | 8223 | 1 | 1 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | U1 PERF 06JUN01 (PM RETEST) | 1 |  | 8.9696 | 81 | 0.026909
8223_1 | Springerville |  | 8223 | 1 | 1 | Filterable Particulate | 0.0058 | lb/MMBtu | Part II | 0 | U1 PERF 08JUN09 | 1 |  | 8.9696 | 81 | 0.052023
8223_1 | Springerville |  | 8223 | 1 | 1 | Filterable Particulate | 0.0069 | lb/MMBtu | Part II | 0 | U1 PERF 09MAY20 | 1 |  | 8.9696 | 81 | 0.06189
8223_1 | Springerville |  | 8223 | 1 | 1 | Filterable Particulate | 0.0109 | lb/MMBtu | Part II | 0 | U1 PERF 05MAY01 | 1 |  | 8.9696 | 81 | 0.097768
8223_1 | Springerville |  | 8223 | 1 | 1 | Filterable Particulate | 0.075 | lb/MMBtu | Part II | 0 | U1 PERF 07JUN06 | 1 |  | 8.9696 | 81 | 0.67272
1082_4 | Walter Scott Jr. Energy Center |  | 1082 | 4 | 4 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | 5/2007 PM | 1 |  | 9.0294 | 82 | 0.027088
1082_4 | Walter Scott Jr. Energy Center |  | 1082 | 4 | 4 | Filterable Particulate | 0.0033765 | lb/MMBtu | ERT | No |  | 3 | 2207 | 9.0294 | 82 | 0.030488
1082_4 | Walter Scott Jr. Energy Center |  | 1082 | 4 | 4 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | 8/2007 PM | 1 |  | 9.0294 | 82 | 0.072235
2712_1 | Roxboro Steam Electric Plant |  | 2712 | 1 | Rox_Cfg_1b | Filterable Particulate | 0.0028093 | lb/MMBtu | ERT | No |  | 6 | 983 | 9.7532 | 83 | 0.027399
2712_1 | Roxboro Steam Electric Plant |  | 2712 | 1 | Rox_Cfg_1b | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | Rox_Blr_1_Test_7i | 3 |  | 9.7532 | 83 | 0.061771
2712_1 | Roxboro Steam Electric Plant |  | 2712 | 1 | Rox_Cfg_1b | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | 0 | Rox_Blr_1_Test_8h | 6 |  | 9.7532 | 83 | 0.072174
1740_3 | River Rouge Power Plant |  | 1740 | 3 | RR3-Config | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | 2009Dec_3 | 2 |  | 9.1433 | 84 | 0.02743
1740_3 | River Rouge Power Plant |  | 1740 | 3 | RR3-Config | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 2008Sep_3b | 3 |  | 9.1433 | 84 | 0.091433
1740_3 | River Rouge Power Plant |  | 1740 | 3 | RR3-Config | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | 2008Sep_3a | 2 |  | 9.1433 | 84 | 0.15544
981_3 | State Line |  | 981 | 3 | Unit 3 | Filterable Particulate | 0.0025 | lb/MMBtu | Part II | 0 | Unit3_2007 | 1 |  | 11.0185 | 85 | 0.027546
981_3 | State Line |  | 981 | 3 | Unit 3 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | Unit3_2005 | 1 |  | 11.0185 | 85 | 0.11019
981_3 | State Line |  | 981 | 3 | Unit 3 | Filterable Particulate | 0.024867 | lb/MMBtu | ERT | No |  | 3 | 1651 | 11.0185 | 85 | 0.274
3280_CAN3 | Canadys Steam |  | 3280 | CAN3 | CAN003 | Filterable Particulate | 0.0028 | lb/MMBtu | Part II | 0 | PM-02/06-CAN3 | 1 |  | 9.8622 | 86 | 0.027614
3280_CAN3 | Canadys Steam |  | 3280 | CAN3 | CAN003 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | PM-02/07-CAN3 | 1 |  | 9.8622 | 86 | 0.029586
3280_CAN3 | Canadys Steam |  | 3280 | CAN3 | CAN003 | Filterable Particulate | 0.0047 | lb/MMBtu | Part II | 0 | PM-01/09-CAN3 | 1 |  | 9.8622 | 86 | 0.046352
3280_CAN3 | Canadys Steam |  | 3280 | CAN3 | CAN003 | Filterable Particulate | 0.0053 | lb/MMBtu | Part II | 0 | PM-02/08-CAN3 | 1 |  | 9.8622 | 86 | 0.052269
3280_CAN3 | Canadys Steam |  | 3280 | CAN3 | CAN003 | Filterable Particulate | 0.014012 | lb/MMBtu | ERT | No |  | 3 | 63254 | 9.8622 | 86 | 0.13819
3280_CAN3 | Canadys Steam |  | 3280 | CAN3 | CAN003 | Filterable Particulate | 0.0152 | lb/MMBtu | Part II | 0 | PM-02/05-CAN3 | 1 |  | 9.8622 | 86 | 0.1499
10002_1 | ACE Cogeneration Company |  | 10002 | 1 | Config 1 | Filterable Particulate | 0.0031 | lb/MMBtu | Part II | 0 | 06212005 | 1 |  | 8.9915 | 87 | 0.027874
10002_1 | ACE Cogeneration Company |  | 10002 | 1 | Config 1 | Filterable Particulate | 0.0083 | lb/MMBtu | Part II | 0 | 2074.1011.rpt1 | 1 |  | 8.9915 | 87 | 0.074629
10002_1 | ACE Cogeneration Company |  | 10002 | 1 | Config 1 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | R017304 | 1 |  | 8.9915 | 87 | 0.1079
10002_1 | ACE Cogeneration Company |  | 10002 | 1 | Config 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | R016634 | 1 |  | 8.9915 | 87 | 0.11689
10002_1 | ACE Cogeneration Company |  | 10002 | 1 | Config 1 | Filterable Particulate | 0.0137 | lb/MMBtu | Part II | 0 | 2074.1012.rpt1 | 1 |  | 8.9915 | 87 | 0.12318
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.00275 | lb/MMBtu | Part II | 0 | 2009Sep_3 | 4 |  | 10.1437 | 88 | 0.027895
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.0036 | lb/MMBtu | Part II | 0 | 2009Jul_3d | 5 |  | 10.1437 | 88 | 0.036517
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.0038 | lb/MMBtu | Part II | 0 | 2009Jul_3c | 5 |  | 10.1437 | 88 | 0.038546
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 2009Jul_3b | 5 |  | 10.1437 | 88 | 0.040575
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | 0 | 2009Jul_3a | 6 |  | 10.1437 | 88 | 0.043956
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | 0 | PM2007_Oct3 | 3 |  | 10.1437 | 88 | 0.057481
1743_3 | St Clair Power Plant |  | 1743 | 3 | SC3-Config | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | PM2007_Sep3 | 3 |  | 10.1437 | 88 | 0.060862
113_3 | Cholla |  | 113 | 3 | 003 | Filterable Particulate | 0.002924 | lb/MMBtu | ERT | No |  | 3 | 1647 | 9.6033 | 89 | 0.02808
113_3 | Cholla |  | 113 | 3 | 003 | Filterable Particulate | 0.0045 | lb/MMBtu | Part II | 0 | 19 | 1 |  | 9.6033 | 89 | 0.043215
113_3 | Cholla |  | 113 | 3 | 003 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 22 | 1 |  | 9.6033 | 89 | 0.05762
113_3 | Cholla |  | 113 | 3 | 003 | Filterable Particulate | 9.21 | lb/MMBtu | Part II | 0 | 21 | 1 |  | 9.6033 | 89 | 88.4462
4042_3 | Valley |  | 4042 | 3 | VAPP-B3 | Filterable Particulate | 0.0023648 | lb/MMBtu | ERT | No |  | 6 | 735 | 12.0556 | 90 | 0.028509
4042_3 | Valley |  | 4042 | 3 | VAPP-B3 | Filterable Particulate | 0.0024019 | lb/MMBtu | ERT | No |  | 6 | 736 | 12.0556 | 90 | 0.028957
4042_3 | Valley |  | 4042 | 3 | VAPP-B3 | Filterable Particulate | 0.0049705 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2B3B4-8.2005 | 3 |  | 12.0556 | 90 | 0.059922
4042_3 | Valley |  | 4042 | 3 | VAPP-B3 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | 0 | VAPP-PM-B3-12.2009 | 3 |  | 12.0556 | 90 | 0.10046
4042_3 | Valley |  | 4042 | 3 | VAPP-B3 | Filterable Particulate | 0.011667 | lb/MMBtu | Part II | 0 | VAPP-PM-CO-THC-CH4-B3B4-8.2006 | 3 |  | 12.0556 | 90 | 0.14065
4042_3 | Valley |  | 4042 | 3 | VAPP-B3 | Filterable Particulate | 0.0135 | lb/MMBtu | Part II | 0 | VAPP-PM-B3B4-8.2007 | 3 |  | 12.0556 | 90 | 0.16275
564_1 | Stanton Energy Center |  | 564 | 1 | 1 coal | Filterable Particulate | 0.0031333 | lb/MMBtu | Part II | 0 | Unit 1 PM 2009 | 3 |  | 9.1581 | 91 | 0.028695
564_1 | Stanton Energy Center |  | 564 | 1 | 1 coal | Filterable Particulate | 0.0036667 | lb/MMBtu | Part II | 0 | Unit 1 PM 2007 | 3 |  | 9.1581 | 91 | 0.03358
564_1 | Stanton Energy Center |  | 564 | 1 | 1 coal | Filterable Particulate | 0.0043 | lb/MMBtu | Part II | 0 | Unit 1 PM 2005 | 3 |  | 9.1581 | 91 | 0.03938
564_1 | Stanton Energy Center |  | 564 | 1 | 1 coal | Filterable Particulate | 0.0089333 | lb/MMBtu | Part II | 0 | Unit 1 PM 2006 | 3 |  | 9.1581 | 91 | 0.081813
7213_2 | Clover |  | 7213 | 2 | Unit 2 | Filterable Particulate | 0.0025465 | lb/MMBtu | ERT | No |  | 3 | 1535 | 11.6152 | 92 | 0.029578
8_10 | Gorgas |  | 8 | 10 | Unit 10 | Filterable Particulate | 0.0032663 | lb/MMBtu | Part II | 0 | UNITS 8-10 FGD PERFORMANCE TESTING | 6 |  | 9.0608 | 93 | 0.029595
8_10 | Gorgas |  | 8 | 10 | Unit 10 | Filterable Particulate | 0.016514 | lb/MMBtu | Part II | 0 | Units 8, 9, and 10 PM Emissions Test (6/27/08) | 3 |  | 9.0608 | 93 | 0.14963
8_10 | Gorgas |  | 8 | 10 | Unit 10 | Filterable Particulate | 0.039141 | lb/MMBtu | Part II | 0 | Units 8, 9, and 10 PM Test (July 30, 2009) | 3 |  | 9.0608 | 93 | 0.35465
7097_BLR1 | J K Spruce |  | 7097 | BLR1 | 1 | Filterable Particulate | 0.0027209 | lb/MMBtu | ERT | No |  | 6 | 1515 | 10.9672 | 94 | 0.02984
7097_BLR1 | J K Spruce |  | 7097 | BLR1 | 1 | Filterable Particulate | 0.0028667 | lb/MMBtu | Part II | 0 | JKS Unit 1 Test Report June 2008 | 3 |  | 10.9672 | 94 | 0.031439
7097_BLR1 | J K Spruce |  | 7097 | BLR1 | 1 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | JKS Unit 1 Test Report May 2006 | 3 |  | 10.9672 | 94 | 0.084082
8_8 | Gorgas |  | 8 | 8 | Unit 8 | Filterable Particulate | 0.0032663 | lb/MMBtu | Part II | 0 | UNITS 8-10 FGD PERFORMANCE TESTING | 6 |  | 9.148 | 95 | 0.02988
8_8 | Gorgas |  | 8 | 8 | Unit 8 | Filterable Particulate | 0.016514 | lb/MMBtu | Part II | 0 | Units 8, 9, and 10 PM Emissions Test (6/27/08) | 3 |  | 9.148 | 95 | 0.15107
8_8 | Gorgas |  | 8 | 8 | Unit 8 | Filterable Particulate | 0.039141 | lb/MMBtu | Part II | 0 | Units 8, 9, and 10 PM Test (July 30, 2009) | 3 |  | 9.148 | 95 | 0.35806
4042_4 | Valley |  | 4042 | 4 | VAPP-B4 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2B3B4-8.2005 | 3 |  | 12.0556 | 96 | 0.030541
4042_4 | Valley |  | 4042 | 4 | VAPP-B4 | Filterable Particulate | 0.0093 | lb/MMBtu | Part II | 0 | VAPP-PM-CO-THC-CH4-B3B4-8.2006 | 3 |  | 12.0556 | 96 | 0.11212
4042_4 | Valley |  | 4042 | 4 | VAPP-B4 | Filterable Particulate | 0.010567 | lb/MMBtu | Part II | 0 | VAPP-PM-B3B4-8.2007 | 3 |  | 12.0556 | 96 | 0.12739
4042_4 | Valley |  | 4042 | 4 | VAPP-B4 | Filterable Particulate | 0.012033 | lb/MMBtu | Part II | 0 | VAPP-PM-B4-12.2009 | 3 |  | 12.0556 | 96 | 0.14507
1743_6 | St Clair Power Plant |  | 1743 | 6 | SC6-Config | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | PM2007_Oct6 | 3 |  | 9.1994 | 97 | 0.030665
8_9 | Gorgas |  | 8 | 9 | Unit 9 | Filterable Particulate | 0.0032663 | lb/MMBtu | Part II | 0 | UNITS 8-10 FGD PERFORMANCE TESTING | 6 |  | 9.398 | 98 | 0.030696
8_9 | Gorgas |  | 8 | 9 | Unit 9 | Filterable Particulate | 0.016514 | lb/MMBtu | Part II | 0 | Units 8, 9, and 10 PM Emissions Test (6/27/08) | 3 |  | 9.398 | 98 | 0.1552
8_9 | Gorgas |  | 8 | 9 | Unit 9 | Filterable Particulate | 0.039141 | lb/MMBtu | Part II | 0 | Units 8, 9, and 10 PM Test (July 30, 2009) | 3 |  | 9.398 | 98 | 0.36784
3403_4 | Gallatin |  | 3403 | 4 | 4 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | GAF3-4 - 2006 | 3 |  | 9.2552 | 99 | 0.030851
3403_4 | Gallatin |  | 3403 | 4 | 4 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | 0 | GAF3-4 -2008 | 3 |  | 9.2552 | 99 | 0.040106
3403_3 | Gallatin |  | 3403 | 3 | 3 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | GAF3-4 - 2006 | 3 |  | 9.2552 | 100 | 0.030851
3403_3 | Gallatin |  | 3403 | 3 | 3 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | 0 | GAF3-4 -2008 | 3 |  | 9.2552 | 100 | 0.040106
2107_2 | Sioux |  | 2107 | 2 | 002 | Filterable Particulate | 0.0033472 | lb/MMBtu | ERT | No |  | 3 | 1915 | 9.3893 | 101 | 0.031428
56224_BLR100 | TS Power Plant |  | 56224 | BLR100 | TSPower | Filterable Particulate | 0.0036333 | lb/MMBtu | Part II | 0 | TRC 04/2008 | 3 |  | 8.7273 | 102 | 0.031709
56224_BLR100 | TS Power Plant |  | 56224 | BLR100 | TSPower | Filterable Particulate | 0.0056066 | lb/MMBtu | ERT | No |  | 6 | 1568 | 8.7273 | 102 | 0.048931
56224_BLR100 | TS Power Plant |  | 56224 | BLR100 | TSPower | Filterable Particulate | 0.0149 | lb/MMBtu | Part II | 0 | Optimal 07/2009 | 6 |  | 8.7273 | 102 | 0.13004
3140_2 | PPL Brunner Island |  | 3140 | 2 | U2 | Filterable Particulate | 0.0033 | lb/MMBtu | Part II | 0 | BI12N09 | 1 |  | 9.6438 | 103 | 0.031824
3140_2 | PPL Brunner Island |  | 3140 | 2 | U2 | Filterable Particulate | 0.025519 | lb/MMBtu | ERT | No |  | 6 | 1176 | 9.6438 | 103 | 0.2461
708_2 | Hammond |  | 708 | 2 | Unit 2 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT | No |  | 6 | 1984 | 9.8959 | 104 | 0.032164
641_5 | Crist |  | 641 | 5 | Unit 5 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT | No |  | 6 | 1894 | 9.9735 | 105 | 0.032199
641_6 | Crist |  | 641 | 6 | Unit 6 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT | No |  | 6 | 1894 | 9.9792 | 106 | 0.032217
708_3 | Hammond |  | 708 | 3 | Unit 3 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT | No |  | 6 | 1984 | 9.9251 | 107 | 0.032259
602_2 | Brandon Shores |  | 602 | 2 | 002 | Filterable Particulate | 0.0033275 | lb/MMBtu | ERT | No |  | 3 | 2259 | 9.7101 | 108 | 0.032311
2837_3 | Eastlake |  | 2837 | 3 | Unit 3 | Filterable Particulate | 0.0038742 | lb/MMBtu | ERT | No |  | 6 | 22791 | 8.3681 | 109 | 0.032419
2718_ES-3 | G G Allen |  | 2718 | ES-3 | 3-2009 | Filterable Particulate | 0.0041114 | lb/MMBtu | ERT | No |  | 3 | 900 | 7.9147 | 110 | 0.032541
2718_ES-3 | G G Allen |  | 2718 | ES-3 | 3-2009 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | CS34(6/9/09) | 3 |  | 7.9147 | 110 | 0.094977
2727_Unit 1 | Marshall |  | 2727 | Unit 1 | U12007 | Filterable Particulate | 0.0035667 | lb/MMBtu | Part II | 0 | CS001020409 | 3 |  | 9.1455 | 111 | 0.032619
2727_Unit 1 | Marshall |  | 2727 | Unit 1 | U12007 | Filterable Particulate | 0.0042333 | lb/MMBtu | Part II | 0 | CS001083007 | 3 |  | 9.1455 | 111 | 0.038716
2727_Unit 1 | Marshall |  | 2727 | Unit 1 | U12007 | Filterable Particulate | 0.0223 | lb/MMBtu | Part II | 0 | CS001013008 | 3 |  | 9.1455 | 111 | 0.20394
2727_Unit 2 | Marshall |  | 2727 | Unit 2 | U22007 | Filterable Particulate | 0.0035667 | lb/MMBtu | Part II | 0 | CS001020409 | 3 |  | 9.158 | 112 | 0.032664
2727_Unit 2 | Marshall |  | 2727 | Unit 2 | U22007 | Filterable Particulate | 0.0042333 | lb/MMBtu | Part II | 0 | CS001083007 | 3 |  | 9.158 | 112 | 0.038769
2727_Unit 2 | Marshall |  | 2727 | Unit 2 | U22007 | Filterable Particulate | 0.0223 | lb/MMBtu | Part II | 0 | CS001013008 | 3 |  | 9.158 | 112 | 0.20422
708_1 | Hammond |  | 708 | 1 | Unit 1 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT | No |  | 6 | 1984 | 10.0761 | 113 | 0.03275
2718_ES-4 | G G Allen |  | 2718 | ES-4 | 4-2009 | Filterable Particulate | 0.0041114 | lb/MMBtu | ERT | No |  | 3 | 900 | 8.0054 | 114 | 0.032913
2718_ES-4 | G G Allen |  | 2718 | ES-4 | 4-2009 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | CS34(6/9/09) | 3 |  | 8.0054 | 114 | 0.096065
2727_Unit 4 | Marshall |  | 2727 | Unit 4 | U4 | Filterable Particulate | 0.0038333 | lb/MMBtu | Part II | 0 | U4020509 | 3 |  | 8.614 | 115 | 0.03302
2727_Unit 4 | Marshall |  | 2727 | Unit 4 | U4 | Filterable Particulate | 0.0050667 | lb/MMBtu | Part II | 0 | U4020108 | 3 |  | 8.614 | 115 | 0.043644
2727_Unit 4 | Marshall |  | 2727 | Unit 4 | U4 | Filterable Particulate | 0.0051333 | lb/MMBtu | Part II | 0 | U4082907 | 3 |  | 8.614 | 115 | 0.044219
2451_Unit 4 | San Juan |  | 2451 | Unit 4 | Unit 4 | Filterable Particulate | 0.0031961 | lb/MMBtu | ERT | No |  | 3 | 23153 | 10.3842 | 116 | 0.033189
3140_1 | PPL Brunner Island |  | 3140 | 1 | U1 | Filterable Particulate | 0.0033 | lb/MMBtu | Part II | 0 | BI12N09 | 1 |  | 10.1364 | 117 | 0.03345
3140_1 | PPL Brunner Island |  | 3140 | 1 | U1 | Filterable Particulate | 0.025519 | lb/MMBtu | ERT | No |  | 6 | 1176 | 10.1364 | 117 | 0.25867
56068_1 | Elm Road Generating Station |  | 56068 | 1 | ERGS-B1 | Filterable Particulate | 0.0035045 | lb/MMBtu | ERT | No |  | 3 | 2319 | 9.6233 | 118 | 0.033725
7213_1 | Clover |  | 7213 | 1 | Unit 1 | Filterable Particulate | 0.0029671 | lb/MMBtu | ERT | No |  | 3 | 1534 | 11.4223 | 119 | 0.033891
50_5 | Widows Creek |  | 50 | 5 | 5 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | WCF5 - 10/25/2006 | 3 |  | 11.3016 | 120 | 0.033905
50_5 | Widows Creek |  | 50 | 5 | 5 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | WCF5 - 2005 | 3 |  | 11.3016 | 120 | 0.097947
50_5 | Widows Creek |  | 50 | 5 | 5 | Filterable Particulate | 0.0093333 | lb/MMBtu | Part II | 0 | WCF5 - 2008 | 3 |  | 11.3016 | 120 | 0.10548
50_5 | Widows Creek |  | 50 | 5 | 5 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | 0 | WCF5 - 12/08/2006 | 3 |  | 11.3016 | 120 | 0.275
1710_Unit 3 | Consumers Energy - J.H. Campbell |  | 1710 | Unit 3 | JHC3-Conf | Filterable Particulate | 0.0036 | lb/MMBtu | Part II | 0 | JHC3 - 2008 Particulate Test | 3 |  | 9.435 | 121 | 0.033966
641_7 | Crist |  | 641 | 7 | Unit 7 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT | No |  | 6 | 1894 | 10.5596 | 122 | 0.034091
708_4 | Hammond |  | 708 | 4 | Unit 4 | Filterable Particulate | 0.0032502 | lb/MMBtu | ERT | No |  | 6 | 1984 | 10.4972 | 123 | 0.034118
641_4 | Crist |  | 641 | 4 | Unit 4 | Filterable Particulate | 0.0032284 | lb/MMBtu | ERT | No |  | 6 | 1894 | 10.5956 | 124 | 0.034207
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | CBB2009pm | 1 |  | 11.5543 | 125 | 0.034663
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.0036667 | lb/MMBtu | Part II | 0 | CBB2006pm | 3 |  | 11.5543 | 125 | 0.042366
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | CBB2007pm10 | 1 |  | 11.5543 | 125 | 0.057772
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.0050763 | lb/MMBtu | ERT | No |  | 3 | 2199 | 11.5543 | 125 | 0.058653
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | 0 | CBB2007pm | 3 |  | 11.5543 | 125 | 0.096286
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.010667 | lb/MMBtu | Part II | 0 | CBB2008pm | 3 |  | 11.5543 | 125 | 0.12325
10672_CBB | Cedar Bay Generating Company L.P. |  | 10672 | CBB | CBB1 | Filterable Particulate | 0.016 | lb/MMBtu | Part II | 0 | CBB2005pm | 3 |  | 11.5543 | 125 | 0.18487
47_1 | Colbert |  | 47 | 1 | 1 | Filterable Particulate | 0.0033333 | lb/MMBtu | Part II | 0 | COF1 - 2006 | 3 |  | 10.605 | 126 | 0.03535
47_1 | Colbert |  | 47 | 1 | 1 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | COF1 - 2009 | 3 |  | 10.605 | 126 | 0.08484
47_1 | Colbert |  | 47 | 1 | 1 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | COF1 - 2005 | 3 |  | 10.605 | 126 | 0.09191
47_1 | Colbert |  | 47 | 1 | 1 | Filterable Particulate | 0.014333 | lb/MMBtu | Part II | 0 | COF1 - 2007 | 3 |  | 10.605 | 126 | 0.15201
47_1 | Colbert |  | 47 | 1 | 1 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | COF1 - 2008 | 3 |  | 10.605 | 126 | 0.16261
6016_1 | Duck Creek |  | 6016 | 1 | 001 | Filterable Particulate | 0.0032 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 11.25 | 127 | 0.036
6016_1 | Duck Creek |  | 6016 | 1 | 001 | Filterable Particulate | 0.003267 | lb/MMBtu | ERT | No |  | 3 | 2239 | 11.25 | 127 | 0.036754
6016_1 | Duck Creek |  | 6016 | 1 | 001 | Filterable Particulate | 0.0077 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 11.25 | 127 | 0.086625
10151_BLR1B | Grant Town Power Plant |  | 10151 | BLR1B | GEN1 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | 0 | 3 | 3 |  | 14.2105 | 128 | 0.036
10151_BLR1B | Grant Town Power Plant |  | 10151 | BLR1B | GEN1 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 14.2105 | 128 | 0.10895
10151_BLR1B | Grant Town Power Plant |  | 10151 | BLR1B | GEN1 | Filterable Particulate | 0.018665 | lb/MMBtu | ERT | No |  | 3 | 1974 | 14.2105 | 128 | 0.26523
10151_BLR1A | Grant Town Power Plant |  | 10151 | BLR1A | GEN1 | Filterable Particulate | 0.0025333 | lb/MMBtu | Part II | 0 | 3 | 3 |  | 14.2105 | 129 | 0.036
10151_BLR1A | Grant Town Power Plant |  | 10151 | BLR1A | GEN1 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 14.2105 | 129 | 0.10895
10151_BLR1A | Grant Town Power Plant |  | 10151 | BLR1A | GEN1 | Filterable Particulate | 0.018665 | lb/MMBtu | ERT | No |  | 3 | 1974 | 14.2105 | 129 | 0.26523
2442_5 | Four Corners |  | 2442 | 5 | 005 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 6 | 1 |  | 9.1152 | 130 | 0.036461
2442_5 | Four Corners |  | 2442 | 5 | 005 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | 17 | 1 |  | 9.1152 | 130 | 0.063806
2442_5 | Four Corners |  | 2442 | 5 | 005 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | 12 | 1 |  | 9.1152 | 130 | 0.072921
6021_C1 | Craig |  | 6021 | C1 | C1 | Filterable Particulate | 0.0041381 | lb/MMBtu | ERT | No |  | 2 | 1307 | 8.8333 | 131 | 0.036553
113_4 | Cholla |  | 113 | 4 | 004 | Filterable Particulate | 0.0036504 | lb/MMBtu | ERT | No |  | 3 | 1648 | 10.0424 | 132 | 0.036659
113_4 | Cholla |  | 113 | 4 | 004 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | 20 | 1 |  | 10.0424 | 132 | 0.090381
113_4 | Cholla |  | 113 | 4 | 004 | Filterable Particulate | 0.0132 | lb/MMBtu | Part II | 0 | 16 | 1 |  | 10.0424 | 132 | 0.13256
3403_2 | Gallatin |  | 3403 | 2 | 2 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | GAF1-2 - 2006 | 3 |  | 9.1667 | 133 | 0.036667
3403_2 | Gallatin |  | 3403 | 2 | 2 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | GAF1-2 -2008 | 3 |  | 9.1667 | 133 | 0.073333
3403_2 | Gallatin |  | 3403 | 2 | 2 | Filterable Particulate | 0.039282 | lb/MMBtu | ERT | No |  | 3 | 2278 | 9.1667 | 133 | 0.36009
3403_1 | Gallatin |  | 3403 | 1 | 1 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | GAF1-2 - 2006 | 3 |  | 9.1667 | 134 | 0.036667
3403_1 | Gallatin |  | 3403 | 1 | 1 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | GAF1-2 -2008 | 3 |  | 9.1667 | 134 | 0.073333
207_PPBoiler2 | St Johns River Power Park |  | 207 | PPBoiler2 | PPUnit2Configuration | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | S2_2009_PM | 3 |  | 9.3091 | 135 | 0.037236
6113_2 | Gibson |  | 6113 | 2 | 2-2007-FGDIN | Filterable Particulate | 0.0038317 | lb/MMBtu | ERT | No |  | 3 | 1638 | 9.7489 | 136 | 0.037355
54304_1A | Birchwood Power Facility |  | 54304 | 1A | 1A | Filterable Particulate | 0.0036333 | lb/MMBtu | Part II | 0 | 5/3/06 Stack Test | 3 |  | 10.3604 | 137 | 0.037643
54304_1A | Birchwood Power Facility |  | 54304 | 1A | 1A | Filterable Particulate | 0.010965 | lb/MMBtu | ERT | No |  | 3 | 1052 | 10.3604 | 137 | 0.1136
525_1 | Hayden |  | 525 | 1 | Unit 1 | Filterable Particulate | 0.0038751 | lb/MMBtu | ERT | No |  | 3 | 560 | 9.7178 | 138 | 0.037658
2451_Unit 1 | San Juan |  | 2451 | Unit 1 | Unit 1 | Filterable Particulate | 0.0037689 | lb/MMBtu | ERT | No |  | 3 | 2315 | 10.0189 | 139 | 0.03776
8042_Unit 2 | Belews Creek Steam Station |  | 8042 | Unit 2 | 2-2008 | Filterable Particulate | 0.0041667 | lb/MMBtu | Part II | 0 | UNIT2(2/18/09) | 3 |  | 9.1293 | 140 | 0.038039
8042_Unit 2 | Belews Creek Steam Station |  | 8042 | Unit 2 | 2-2008 | Filterable Particulate | 0.0239 | lb/MMBtu | Part II | 0 | UNIT2(6/3/08) | 3 |  | 9.1293 | 140 | 0.21819
2837_1 | Eastlake |  | 2837 | 1 | Unit 1 | Filterable Particulate | 0.0045984 | lb/MMBtu | ERT | No |  | 6 | 2279 | 8.3681 | 141 | 0.03848
3149_1 | PPL Montour |  | 3149 | 1 | U1 | Filterable Particulate | 0.00426 | lb/MMBtu | Part II | 0 | M1PM509 | 1 |  | 9.0828 | 142 | 0.038693
3149_1 | PPL Montour |  | 3149 | 1 | U1 | Filterable Particulate | 0.010703 | lb/MMBtu | ERT | No |  | 6 | 1185 | 9.0828 | 142 | 0.09721
3149_1 | PPL Montour |  | 3149 | 1 | U1 | Filterable Particulate | 0.0118 | lb/MMBtu | Part II | 0 | M1PM608 | 1 |  | 9.0828 | 142 | 0.10718
2836_12 | Avon Lake |  | 2836 | 12 | AL12-2 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | AL-16 | 3 |  | 9.6779 | 143 | 0.038712
2836_12 | Avon Lake |  | 2836 | 12 | AL12-2 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | AL-17 | 3 |  | 9.6779 | 143 | 0.16452
2836_12 | Avon Lake |  | 2836 | 12 | AL12-2 | Filterable Particulate | 0.024667 | lb/MMBtu | Part II | 0 | AL-22A | 3 |  | 9.6779 | 143 | 0.23872
6041_1 | H L Spurlock Station |  | 6041 | 1 | Unit 01 | Filterable Particulate | 0.0036839 | lb/MMBtu | ERT | No |  | 3 | 994 | 10.5843 | 144 | 0.038991
6041_1 | H L Spurlock Station |  | 6041 | 1 | Unit 01 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | U1PM_10/07/09 | 3 |  | 10.5843 | 144 | 0.19052
1252_9 | Tecumseh Energy Center |  | 1252 | 9 | 9 | Filterable Particulate | 0.0038 | lb/MMBtu | Part II | 0 | PREC 0708/9 | 3 |  | 10.3171 | 145 | 0.039205
1252_9 | Tecumseh Energy Center |  | 1252 | 9 | 9 | Filterable Particulate | 0.069967 | lb/MMBtu | Part II | 0 | CAM 0808/9 | 9 |  | 10.3171 | 145 | 0.72185
6249_1 | Winyah |  | 6249 | 1 | W1 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | W1PM2009 | 1 |  | 9.8441 | 146 | 0.039376
6249_1 | Winyah |  | 6249 | 1 | W1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | W1PM2007 | 1 |  | 9.8441 | 146 | 0.12797
6249_1 | Winyah |  | 6249 | 1 | W1 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | W1PM2008 | 1 |  | 9.8441 | 146 | 0.14766
6098_001 | Big Stone |  | 6098 | 001 | 001 | Filterable Particulate | 0.0037255 | lb/MMBtu | ERT | No |  | 6 | 1151 | 10.7253 | 147 | 0.039956
6098_001 | Big Stone |  | 6098 | 001 | 001 | Filterable Particulate | 0.011333 | lb/MMBtu | Part II | 0 | Particulate Emissions Test | 3 |  | 10.7253 | 147 | 0.12155
3944_1 | Harrison Power Station |  | 3944 | 1 | Boiler1 | Filterable Particulate | 0.0048 | lb/MMBtu | Part II | 0 | 3 | 3 |  | 8.3391 | 148 | 0.040028
3944_1 | Harrison Power Station |  | 3944 | 1 | Boiler1 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | 11 | 3 |  | 8.3391 | 148 | 0.12787
3944_1 | Harrison Power Station |  | 3944 | 1 | Boiler1 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | 5 | 3 |  | 8.3391 | 148 | 0.15844
3944_1 | Harrison Power Station |  | 3944 | 1 | Boiler1 | Filterable Particulate | 0.053 | lb/MMBtu | Part II | 0 | 8 | 3 |  | 8.3391 | 148 | 0.44197
3944_1 | Harrison Power Station |  | 3944 | 1 | Boiler1 | Filterable Particulate | 97.6 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 8.3391 | 148 | 813.8967
130_2 | Cross |  | 130 | 2 | C2 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | C2PM2009 | 1 |  | 10.1025 | 149 | 0.04041
130_2 | Cross |  | 130 | 2 | C2 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | C2PM2008 | 1 |  | 10.1025 | 149 | 0.050513
130_2 | Cross |  | 130 | 2 | C2 | Filterable Particulate | 0.0066 | lb/MMBtu | Part II | 0 | C2PM2005 | 1 |  | 10.1025 | 149 | 0.066677
130_2 | Cross |  | 130 | 2 | C2 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | C2PM2007 | 1 |  | 10.1025 | 149 | 0.090923
130_2 | Cross |  | 130 | 2 | C2 | Filterable Particulate | 0.016 | lb/MMBtu | Part II | 0 | C2PM2006 | 1 |  | 10.1025 | 149 | 0.16164
130_2 | Cross |  | 130 | 2 | C2 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | C2PM2005R | 1 |  | 10.1025 | 149 | 0.17174
26_2 | E. C. Gaston |  | 26 | 2 | Unit 2 | Filterable Particulate | 0.0043667 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (May 11, 2005) | 3 |  | 9.3031 | 150 | 0.040624
26_2 | E. C. Gaston |  | 26 | 2 | Unit 2 | Filterable Particulate | 0.0076333 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (June 9, 2006) | 3 |  | 9.3031 | 150 | 0.071014
26_2 | E. C. Gaston |  | 26 | 2 | Unit 2 | Filterable Particulate | 0.0103 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (August 23, 2007) | 3 |  | 9.3031 | 150 | 0.095822
26_2 | E. C. Gaston |  | 26 | 2 | Unit 2 | Filterable Particulate | 0.0234 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (March 25, 2009) | 3 |  | 9.3031 | 150 | 0.21769
26_2 | E. C. Gaston |  | 26 | 2 | Unit 2 | Filterable Particulate | 0.0575 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (July 9, 2008) | 3 |  | 9.3031 | 150 | 0.53493
2848_H-5 | O H Hutchings |  | 2848 | H-5 | H-5 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 2009 H-5 EF trail baseline metals | 2 |  | 10.1746 | 151 | 0.040698
2848_H-5 | O H Hutchings |  | 2848 | H-5 | H-5 | Filterable Particulate | 0.021 | lb/MMBtu | Part II | 0 | 2007 H-5 | 3 |  | 10.1746 | 151 | 0.21367
2848_H-5 | O H Hutchings |  | 2848 | H-5 | H-5 | Filterable Particulate | 0.022567 | lb/MMBtu | Part II | 0 | 2009 H-5 | 3 |  | 10.1746 | 151 | 0.22961
2848_H-5 | O H Hutchings |  | 2848 | H-5 | H-5 | Filterable Particulate | 0.024 | lb/MMBtu | Part II | 0 | 2005 H-5 | 3 |  | 10.1746 | 151 | 0.24419
2848_H-5 | O H Hutchings |  | 2848 | H-5 | H-5 | Filterable Particulate | 0.053 | lb/MMBtu | Part II | 0 | 2006 H-5 | 3 |  | 10.1746 | 151 | 0.53925
2848_H-5 | O H Hutchings |  | 2848 | H-5 | H-5 | Filterable Particulate | 0.069933 | lb/MMBtu | Part II | 0 | 2008 H-5 | 3 |  | 10.1746 | 151 | 0.71154
50951_1 | Sunnyside Cogen Associates |  | 50951 | 1 | Config 1 | Filterable Particulate | 0.0035593 | lb/MMBtu | ERT | No |  | 6 | 1942 | 11.6667 | 152 | 0.041525
6257_3 | Scherer |  | 6257 | 3 | Unit 3 | Filterable Particulate | 0.003917 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (January 5, 2010) | 3 |  | 10.6392 | 153 | 0.041674
2727_Unit 3 | Marshall |  | 2727 | Unit 3 | U3 | Filterable Particulate | 0.0048 | lb/MMBtu | Part II | 0 | U3020309 | 3 |  | 8.7187 | 154 | 0.04185
60_1 | Whelan Energy Center Unit 1 (WEC1) |  | 60 | 1 | 1 | Filterable Particulate | 0.0041454 | lb/MMBtu | ERT | No |  | 6 | 3197 | 10.1089 | 155 | 0.041906
1893_3 | Boswell Energy Center |  | 1893 | 3 | BEC3 | Filterable Particulate | 0.0038 | lb/MMBtu | Part II | 0 | 3-Feb2010-PM | 1 |  | 11.0827 | 156 | 0.042114
1040_2 | Whitewater Valley |  | 1040 | 2 | 002 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 10.5797 | 157 | 0.042319
1040_2 | Whitewater Valley |  | 1040 | 2 | 002 | Filterable Particulate | 0.096 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 10.5797 | 157 | 1.0157
1040_2 | Whitewater Valley |  | 1040 | 2 | 002 | Filterable Particulate | 0.14 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 10.5797 | 157 | 1.4812
1040_2 | Whitewater Valley |  | 1040 | 2 | 002 | Filterable Particulate | 0.201 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 10.5797 | 157 | 2.1265
564_2 | Stanton Energy Center |  | 564 | 2 | 2 coal | Filterable Particulate | 0.0046667 | lb/MMBtu | Part II | 0 | Unit 2 PM 2009 | 3 |  | 9.1581 | 158 | 0.042738
564_2 | Stanton Energy Center |  | 564 | 2 | 2 coal | Filterable Particulate | 0.0050667 | lb/MMBtu | Part II | 0 | Unit 2 PM 2005 | 3 |  | 9.1581 | 158 | 0.046401
564_2 | Stanton Energy Center |  | 564 | 2 | 2 coal | Filterable Particulate | 0.0057333 | lb/MMBtu | Part II | 0 | Unit 2 PM 2006 | 3 |  | 9.1581 | 158 | 0.052507
564_2 | Stanton Energy Center |  | 564 | 2 | 2 coal | Filterable Particulate | 0.023447 | lb/MMBtu | ERT | No |  | 6 | 2081 | 9.1581 | 158 | 0.21473
6021_C2 | Craig |  | 6021 | C2 | C2 | Filterable Particulate | 0.0045678 | lb/MMBtu | ERT | No |  | 3 | 1327 | 9.3618 | 159 | 0.042763
1040_1 | Whitewater Valley |  | 1040 | 1 | 001 | Filterable Particulate | 0.004 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 10.6944 | 160 | 0.042778
1040_1 | Whitewater Valley |  | 1040 | 1 | 001 | Filterable Particulate | 0.096 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 10.6944 | 160 | 1.0267
1040_1 | Whitewater Valley |  | 1040 | 1 | 001 | Filterable Particulate | 0.14 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 10.6944 | 160 | 1.4972
1040_1 | Whitewater Valley |  | 1040 | 1 | 001 | Filterable Particulate | 0.201 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 10.6944 | 160 | 2.1496
2823_B1 | Milton R. Young Station |  | 2823 | B1 | 1 | Filterable Particulate | 0.0034635 | lb/MMBtu | Part II | 0 | Sept2005 PM emissions compliance study | 1 |  | 12.8 | 161 | 0.044333
2823_B1 | Milton R. Young Station |  | 2823 | B1 | 1 | Filterable Particulate | 0.0044883 | lb/MMBtu | Part II | 0 | AUG2006 PM Emissions Compliance Study | 1 |  | 12.8 | 161 | 0.05745
6170_1 | Pleasant Prairie |  | 6170 | 1 | PPPPB1 | Filterable Particulate | 0.0045134 | lb/MMBtu | Part II | 0 | PPPP-PM-U1-1.2009 | 3 |  | 9.8458 | 162 | 0.044438
6170_1 | Pleasant Prairie |  | 6170 | 1 | PPPPB1 | Filterable Particulate | 0.0061851 | lb/MMBtu | Part II | 0 | PPPP-PM-U1-4.2009 | 3 |  | 9.8458 | 162 | 0.060897
6019_1 | W H Zimmer |  | 6019 | 1 | 1 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | U1072809 | 3 |  | 8.9886 | 163 | 0.044943
6019_1 | W H Zimmer |  | 6019 | 1 | 1 | Filterable Particulate | 0.0093973 | lb/MMBtu | ERT | No |  | 3 | 908 | 8.9886 | 163 | 0.084469
6019_1 | W H Zimmer |  | 6019 | 1 | 1 | Filterable Particulate | 0.019667 | lb/MMBtu | Part II | 0 | U1041205 | 3 |  | 8.9886 | 163 | 0.17678
6019_1 | W H Zimmer |  | 6019 | 1 | 1 | Filterable Particulate | 0.020667 | lb/MMBtu | Part II | 0 | U1 112007 | 3 |  | 8.9886 | 163 | 0.18577
1825_3 | Grand Haven City of J.B. Sims |  | 1825 | 3 | 001 | Filterable Particulate | 0.0048 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 9.473 | 164 | 0.045471
2442_4 | Four Corners |  | 2442 | 4 | 004 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | 16 | 1 |  | 9.1152 | 165 | 0.045576
2442_4 | Four Corners |  | 2442 | 4 | 004 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | 5 | 1 |  | 9.1152 | 165 | 0.072921
2442_4 | Four Corners |  | 2442 | 4 | 004 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 11 | 1 |  | 9.1152 | 165 | 0.091152
4072_8 | Pulliam |  | 4072 | 8 | 8 | Filterable Particulate | 0.0041887 | lb/MMBtu | ERT | No |  | 6 | 1597 | 10.95 | 166 | 0.045866
4072_8 | Pulliam |  | 4072 | 8 | 8 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | P8 PM 2008 | 3 |  | 10.95 | 166 | 0.1533
6204_1 | Laramie River Station |  | 6204 | 1 | 1 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | 0 | Unit 1 Particulate 2005 | 3 |  | 10.6116 | 167 | 0.045983
6204_1 | Laramie River Station |  | 6204 | 1 | 1 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | 0 | Unit 1 Particulate 2009 | 3 |  | 10.6116 | 167 | 0.045983
6204_1 | Laramie River Station |  | 6204 | 1 | 1 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | Unit 1 Particulate 2007 | 3 |  | 10.6116 | 167 | 0.067207
6204_1 | Laramie River Station |  | 6204 | 1 | 1 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | Unit 1 Particulate 2008 | 3 |  | 10.6116 | 167 | 0.095504
6204_1 | Laramie River Station |  | 6204 | 1 | 1 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | Unit 1 Particulate 2006 | 3 |  | 10.6116 | 167 | 0.095504
3122_3 | Homer City Station |  | 3122 | 3 | HC3CONFIG | Filterable Particulate | 0.0051333 | lb/MMBtu | Part II | 0 | HC 3 Jan 2009 PM Test | 3 |  | 9.0809 | 169 | 0.046615
2451_Unit 2 | San Juan |  | 2451 | Unit 2 | Unit 2 | Filterable Particulate | 0.0046789 | lb/MMBtu | ERT | No |  | 3 | 23151 | 9.9676 | 170 | 0.046637
10743_CFB2 | Morgantown Energy Facility |  | 10743 | CFB2 | Unit 1&2 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | 3/5/2005PM | 1 |  | 15.6897 | 171 | 0.047069
10743_CFB2 | Morgantown Energy Facility |  | 10743 | CFB2 | Unit 1&2 | Filterable Particulate | 0.0091026 | lb/MMBtu | ERT | No |  | 3 | 1654 | 15.6897 | 171 | 0.14282
10743_CFB2 | Morgantown Energy Facility |  | 10743 | CFB2 | Unit 1&2 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | 3/20/2008PM | 1 |  | 15.6897 | 171 | 0.21966
10743_CFB1 | Morgantown Energy Facility |  | 10743 | CFB1 | Unit 1&2 | Filterable Particulate | 0.003 | lb/MMBtu | Part II | 0 | 3/5/2005PM | 1 |  | 15.6897 | 172 | 0.047069
10743_CFB1 | Morgantown Energy Facility |  | 10743 | CFB1 | Unit 1&2 | Filterable Particulate | 0.0091026 | lb/MMBtu | ERT | No |  | 3 | 1654 | 15.6897 | 172 | 0.14282
10743_CFB1 | Morgantown Energy Facility |  | 10743 | CFB1 | Unit 1&2 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | 3/20/2008PM | 1 |  | 15.6897 | 172 | 0.21966
3399_2 | Cumberland |  | 3399 | 2 | 2 | Filterable Particulate | 0.0043333 | lb/MMBtu | Part II | 0 | CUF2 - 2007 | 3 |  | 10.8692 | 173 | 0.0471
3399_2 | Cumberland |  | 3399 | 2 | 2 | Filterable Particulate | 0.0066667 | lb/MMBtu | Part II | 0 | CUF2 - 2009 | 3 |  | 10.8692 | 173 | 0.072462
4271_B1 | John P. Madgett |  | 4271 | B1 | 001 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 9.4649 | 174 | 0.047325
4271_B1 | John P. Madgett |  | 4271 | B1 | 001 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | 3 | 3 |  | 9.4649 | 174 | 0.047325
4271_B1 | John P. Madgett |  | 4271 | B1 | 001 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | 4 | 3 |  | 9.4649 | 174 | 0.082029
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.0040071 | lb/MMBtu | ERT | No |  | 3 | 2179 | 11.859 | 176 | 0.04752
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.0092211 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Steady State Test (8/16/05) | 3 |  | 11.859 | 176 | 0.10935
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.01108 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Steady State Test (8/14/07) | 3 |  | 11.859 | 176 | 0.1314
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.016916 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Soot Blow Test (8/15/05) | 3 |  | 11.859 | 176 | 0.2006
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.017629 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Soot Blow Test (8/17/05) | 3 |  | 11.859 | 176 | 0.20907
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.017652 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Soot Blow Test (8/14/07) | 3 |  | 11.859 | 176 | 0.20933
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.017834 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Steady State Test (8/18/05) | 3 |  | 11.859 | 176 | 0.2115
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.01854 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Steady State Test (8/12/08) | 3 |  | 11.859 | 176 | 0.21986
642_1 | Scholz |  | 642 | 1 | Unit 1 | Filterable Particulate | 0.018667 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Soot Blow Test (8/12/08) | 3 |  | 11.859 | 176 | 0.22137
6249_2 | Winyah |  | 6249 | 2 | W2 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | W2PM2009 | 1 |  | 9.5344 | 177 | 0.047672
6249_2 | Winyah |  | 6249 | 2 | W2 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | W2PM2008 | 1 |  | 9.5344 | 177 | 0.066741
6249_2 | Winyah |  | 6249 | 2 | W2 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | W2PM2007 | 1 |  | 9.5344 | 177 | 0.12395
50879_50879 | Wheelabrator Frackville Energy Co. |  | 50879 | 50879 | 1 | Filterable Particulate | 0.0036667 | lb/MMBtu | Part II | 0 | StackTest-3 | 3 |  | 13.1111 | 178 | 0.048074
6664_101 | Louisa |  | 6664 | 101 | 101 | Filterable Particulate | 0.004512 | lb/MMBtu | ERT | No |  | 3 | 2206 | 10.713 | 179 | 0.048337
113_1 | Cholla |  | 113 | 1 | 001 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | 17 | 1 |  | 9.6947 | 180 | 0.048473
113_1 | Cholla |  | 113 | 1 | 001 | Filterable Particulate | 0.0134 | lb/MMBtu | Part II | 0 | 13 | 1 |  | 9.6947 | 180 | 0.12991
113_1 | Cholla |  | 113 | 1 | 001 | Filterable Particulate | 0.0166 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 9.6947 | 180 | 0.16093
54144_BRBR1 | Piney Creek Project |  | 54144 | BRBR1 | BRBRI | Filterable Particulate | 0.0039147 | lb/MMBtu | ERT | No |  | 3 | 2088 | 12.5 | 181 | 0.048934
54144_BRBR1 | Piney Creek Project |  | 54144 | BRBR1 | BRBRI | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | 16-00127 Condition 4 & 12 | 2 |  | 12.5 | 181 | 0.15
643_1 | Lansing Smith |  | 643 | 1 | Unit 1 | Filterable Particulate | 0.0049442 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Steady State Test (8/19/09) | 3 |  | 10.0478 | 182 | 0.049678
6204_2 | Laramie River Station |  | 6204 | 2 | 2 | Filterable Particulate | 0.0046667 | lb/MMBtu | Part II | 0 | Unit 2 Particulate 2007 | 3 |  | 10.6645 | 183 | 0.049767
6204_2 | Laramie River Station |  | 6204 | 2 | 2 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | Unit 2 Particulate 2006 | 3 |  | 10.6645 | 183 | 0.067542
6204_2 | Laramie River Station |  | 6204 | 2 | 2 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | Unit 2 Particulate 2009 | 3 |  | 10.6645 | 183 | 0.067542
6204_2 | Laramie River Station |  | 6204 | 2 | 2 | Filterable Particulate | 0.0075 | lb/MMBtu | Part II | 0 | Unit 2 Particulate 2005 | 2 |  | 10.6645 | 183 | 0.079983
6204_2 | Laramie River Station |  | 6204 | 2 | 2 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | 0 | Unit 2 Particulate 2008 | 3 |  | 10.6645 | 183 | 0.08887
6170_2 | Pleasant Prairie |  | 6170 | 2 | PPPPB2 | Filterable Particulate | 0.0049645 | lb/MMBtu | Part II | 0 | PPPP-PM-U2-1.2009 | 3 |  | 10.0295 | 184 | 0.049792
6170_2 | Pleasant Prairie |  | 6170 | 2 | PPPPB2 | Filterable Particulate | 0.0087138 | lb/MMBtu | Part II | 0 | PPPP-PMNH3SO3-U2-5.2007 | 3 |  | 10.0295 | 184 | 0.087395
6170_2 | Pleasant Prairie |  | 6170 | 2 | PPPPB2 | Filterable Particulate | 0.0087377 | lb/MMBtu | Part II | 0 | PPPP-PM-U2-8.2009 | 3 |  | 10.0295 | 184 | 0.087636
884_1 | Will County |  | 884 | 1 | WC1CONFIG | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | WillCo1 PM | 3 |  | 10.1197 | 185 | 0.050599
3788_2 | Potomac River |  | 3788 | 2 | 2 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | C2 PM STK 1206 | 1 |  | 10.4301 | 186 | 0.052151
3788_2 | Potomac River |  | 3788 | 2 | 2 | Filterable Particulate | 0.016367 | lb/MMBtu | Part II | 0 | C2 PM Stack 1206 | 3 |  | 10.4301 | 186 | 0.17071
3788_2 | Potomac River |  | 3788 | 2 | 2 | Filterable Particulate | 0.027 | lb/MMBtu | Part II | 0 | CSC12 PM 0909 | 1 |  | 10.4301 | 186 | 0.28161
988_4 | Tanners Creek |  | 988 | 4 | TC-4 | Filterable Particulate | 0.0060958 | lb/MMBtu | ERT | No |  | 6 | 12861 | 8.6079 | 187 | 0.052472
988_4 | Tanners Creek |  | 988 | 4 | TC-4 | Filterable Particulate | 0.0079 | lb/MMBtu | Part II | 0 | Mar2007PM | 1 |  | 8.6079 | 187 | 0.068002
988_4 | Tanners Creek |  | 988 | 4 | TC-4 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | July2005PM | 1 |  | 8.6079 | 187 | 0.068863
988_4 | Tanners Creek |  | 988 | 4 | TC-4 | Filterable Particulate | 0.0164 | lb/MMBtu | Part II | 0 | Aug2009PM2 | 1 |  | 8.6079 | 187 | 0.14117
1606_1 | Mount Tom |  | 1606 | 1 | 1 current | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | 0 | Turbosorp - initial compliance test | 1 |  | 9.5484 | 188 | 0.052516
642_2 | Scholz |  | 642 | 2 | Unit 2 | Filterable Particulate | 0.0040071 | lb/MMBtu | ERT | No |  | 3 | 2179 | 13.158 | 189 | 0.052725
642_2 | Scholz |  | 642 | 2 | Unit 2 | Filterable Particulate | 0.0081178 | lb/MMBtu | Part II | 0 | Unit 2 Particulate Steady State Test (8/12/08) | 3 |  | 13.158 | 189 | 0.10681
642_2 | Scholz |  | 642 | 2 | Unit 2 | Filterable Particulate | 0.011657 | lb/MMBtu | Part II | 0 | Unit 2 Particulate Soot Blow Test (8/11/08) | 3 |  | 13.158 | 189 | 0.15339
1091_3 | George Neal North |  | 1091 | 3 | 3 | Filterable Particulate | 0.0057227 | lb/MMBtu | Part II | 0 | 7/15/2008-PM | 1 |  | 9.4557 | 190 | 0.054112
1091_3 | George Neal North |  | 1091 | 3 | 3 | Filterable Particulate | 0.009556 | lb/MMBtu | Part II | 0 | 7/11/2006-PM | 1 |  | 9.4557 | 190 | 0.090359
6034_1 | Belle River |  | 6034 | 1 | BR1-Config | Filterable Particulate | 0.005375 | lb/MMBtu | Part II | 0 | PM2009_1 | 8 |  | 10.1098 | 191 | 0.05434
6034_1 | Belle River |  | 6034 | 1 | BR1-Config | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | PM2007_1 | 3 |  | 10.1098 | 191 | 0.070769
3138_4 | New Castle Plant |  | 3138 | 4 | NC4-2 | Filterable Particulate | 0.00607 | lb/MMBtu | Part II | 0 | NC-39B | 3 |  | 8.9912 | 192 | 0.054577
3138_4 | New Castle Plant |  | 3138 | 4 | NC4-2 | Filterable Particulate | 0.0083 | lb/MMBtu | Part II | 0 | NC-19A | 3 |  | 8.9912 | 192 | 0.074627
3138_4 | New Castle Plant |  | 3138 | 4 | NC4-2 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | 0 | NC-21A | 3 |  | 8.9912 | 192 | 0.074927
3138_4 | New Castle Plant |  | 3138 | 4 | NC4-2 | Filterable Particulate | 0.0086633 | lb/MMBtu | Part II | 0 | NC-39C | 3 |  | 8.9912 | 192 | 0.077894
1008_4 | R. Gallagher |  | 1008 | 4 | 4-2008 | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | 0 | STACKB052908 | 3 |  | 9.7333 | 193 | 0.055156
1008_3 | R. Gallagher |  | 1008 | 3 | 3-2008 | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | 0 | STACKB052908 | 3 |  | 9.7333 | 194 | 0.055156
3788_1 | Potomac River |  | 3788 | 1 | 1 | Filterable Particulate | 0.0053 | lb/MMBtu | Part II | 0 | C1 PM SBC60 0508 | 1 |  | 10.4301 | 195 | 0.05528
3788_1 | Potomac River |  | 3788 | 1 | 1 | Filterable Particulate | 0.0078 | lb/MMBtu | Part II | 0 | C1 PM SBC30 0508 | 1 |  | 10.4301 | 195 | 0.081355
3788_1 | Potomac River |  | 3788 | 1 | 1 | Filterable Particulate | 0.0172 | lb/MMBtu | Part II | 0 | C1 PM SBC50 0508 | 1 |  | 10.4301 | 195 | 0.1794
3788_1 | Potomac River |  | 3788 | 1 | 1 | Filterable Particulate | 0.0181 | lb/MMBtu | Part II | 0 | C1 PM SBC20 0508 | 1 |  | 10.4301 | 195 | 0.18878
3788_1 | Potomac River |  | 3788 | 1 | 1 | Filterable Particulate | 0.027 | lb/MMBtu | Part II | 0 | CSC12 PM 0909 | 1 |  | 10.4301 | 195 | 0.28161
2712_4B | Roxboro Steam Electric Plant |  | 2712 | 4B | Rox_Cfg_4c | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | Rox_Unit_4_Test_7d | 4 |  | 9.3128 | 196 | 0.055877
2712_4B | Roxboro Steam Electric Plant |  | 2712 | 4B | Rox_Cfg_4c | Filterable Particulate | 0.012917 | lb/MMBtu | Part II | 0 | Rox_Unit_4_Test_8k | 12 |  | 9.3128 | 196 | 0.12029
2712_4B | Roxboro Steam Electric Plant |  | 2712 | 4B | Rox_Cfg_4c | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | Rox_Unit_4_Test_12h | 3 |  | 9.3128 | 196 | 0.13969
2712_4A | Roxboro Steam Electric Plant |  | 2712 | 4A | Rox_Cfg_4c | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | Rox_Unit_4_Test_7d | 4 |  | 9.3128 | 197 | 0.055877
2712_4A | Roxboro Steam Electric Plant |  | 2712 | 4A | Rox_Cfg_4c | Filterable Particulate | 0.012917 | lb/MMBtu | Part II | 0 | Rox_Unit_4_Test_8k | 12 |  | 9.3128 | 197 | 0.12029
2712_4A | Roxboro Steam Electric Plant |  | 2712 | 4A | Rox_Cfg_4c | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | Rox_Unit_4_Test_12h | 3 |  | 9.3128 | 197 | 0.13969
6113_1 | Gibson |  | 6113 | 1 | 1-2007-FGDIN | Filterable Particulate | 0.0058648 | lb/MMBtu | ERT | No |  | 3 | 1637 | 9.6339 | 198 | 0.0565
47_4 | Colbert |  | 47 | 4 | 4 | Filterable Particulate | 0.0053333 | lb/MMBtu | Part II | 0 | COF4 - 2006 | 3 |  | 10.605 | 199 | 0.05656
47_4 | Colbert |  | 47 | 4 | 4 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | COF4 - 2009 | 3 |  | 10.605 | 199 | 0.06363
47_4 | Colbert |  | 47 | 4 | 4 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | COF4 - 2007 | 3 |  | 10.605 | 199 | 0.095445
47_4 | Colbert |  | 47 | 4 | 4 | Filterable Particulate | 0.011333 | lb/MMBtu | Part II | 0 | COF4 - 2005 | 3 |  | 10.605 | 199 | 0.12019
47_4 | Colbert |  | 47 | 4 | 4 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | COF4 - 2008 | 3 |  | 10.605 | 199 | 0.19089
47_4 | Colbert |  | 47 | 4 | 4 | Filterable Particulate | 0.024005 | lb/MMBtu | ERT | No |  | 6 | 2276 | 10.605 | 199 | 0.25457
47_2 | Colbert |  | 47 | 2 | 2 | Filterable Particulate | 0.0053333 | lb/MMBtu | Part II | 0 | COF2 - 2008 | 3 |  | 10.605 | 200 | 0.05656
47_2 | Colbert |  | 47 | 2 | 2 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | COF2 - 2009 | 3 |  | 10.605 | 200 | 0.095445
47_2 | Colbert |  | 47 | 2 | 2 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | COF2 - 2006 | 3 |  | 10.605 | 200 | 0.11666
47_2 | Colbert |  | 47 | 2 | 2 | Filterable Particulate | 0.011333 | lb/MMBtu | Part II | 0 | COF2 - 2007 | 3 |  | 10.605 | 200 | 0.12019
47_2 | Colbert |  | 47 | 2 | 2 | Filterable Particulate | 0.049 | lb/MMBtu | Part II | 0 | COF2 - 2005 | 3 |  | 10.605 | 200 | 0.51964
508_4 | Lamar Plant |  | 508 | 4 | 001 | Filterable Particulate | 0.0049078 | lb/MMBtu | Part II | 0 | 1 | 2 |  | 11.5864 | 201 | 0.056864
1743_4 | St Clair Power Plant |  | 1743 | 4 | SC4-Config | Filterable Particulate | 0.0053333 | lb/MMBtu | Part II | 0 | PM2007_Sep4 | 3 |  | 10.7771 | 202 | 0.057478
1743_4 | St Clair Power Plant |  | 1743 | 4 | SC4-Config | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | PM2007_Oct4 | 3 |  | 10.7771 | 202 | 0.093401
10672_CBA | Cedar Bay Generating Company L.P. |  | 10672 | CBA | CBA1 | Filterable Particulate | 0.005 | lb/MMBtu | Part II | 0 | CBA2006pm | 3 |  | 11.5543 | 203 | 0.057772
10672_CBA | Cedar Bay Generating Company L.P. |  | 10672 | CBA | CBA1 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | CBA2009pm | 1 |  | 11.5543 | 203 | 0.069326
10672_CBA | Cedar Bay Generating Company L.P. |  | 10672 | CBA | CBA1 | Filterable Particulate | 0.0063127 | lb/MMBtu | ERT | No |  | 3 | 2198 | 11.5543 | 203 | 0.072939
10672_CBA | Cedar Bay Generating Company L.P. |  | 10672 | CBA | CBA1 | Filterable Particulate | 0.0093333 | lb/MMBtu | Part II | 0 | CBA2005pm | 3 |  | 11.5543 | 203 | 0.10784
10672_CBA | Cedar Bay Generating Company L.P. |  | 10672 | CBA | CBA1 | Filterable Particulate | 0.013333 | lb/MMBtu | Part II | 0 | CBA2007pm | 3 |  | 11.5543 | 203 | 0.15406
10672_CBA | Cedar Bay Generating Company L.P. |  | 10672 | CBA | CBA1 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | CBA2008pm | 3 |  | 11.5543 | 203 | 0.16946
1915_Boiler 1 | Allen S King |  | 1915 | Boiler 1 | Unit 1 | Filterable Particulate | 0.0071 | lb/MMBtu | Part II | 0 | King PM 05-2009 | 1 |  | 8.1552 | 204 | 0.057902
1915_Boiler 1 | Allen S King |  | 1915 | Boiler 1 | Unit 1 | Filterable Particulate | 0.0076 | lb/MMBtu | Part II | 0 | King PM 05-2008 | 1 |  | 8.1552 | 204 | 0.061979
130_3 | Cross |  | 130 | 3 | C3 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | C3PM2007 | 1 |  | 9.6928 | 205 | 0.058157
130_3 | Cross |  | 130 | 3 | C3 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | C3PM2009 | 1 |  | 9.6928 | 205 | 0.077542
130_3 | Cross |  | 130 | 3 | C3 | Filterable Particulate | 0.009083 | lb/MMBtu | ERT | No |  | 3 | 1118 | 9.6928 | 205 | 0.08804
130_3 | Cross |  | 130 | 3 | C3 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | C3PM2008 | 1 |  | 9.6928 | 205 | 0.096928
3138_5 | New Castle Plant |  | 3138 | 5 | NC5-2 | Filterable Particulate | 0.0058 | lb/MMBtu | Part II | 0 | NC-48 | 3 |  | 10.0558 | 206 | 0.058324
3138_5 | New Castle Plant |  | 3138 | 5 | NC5-2 | Filterable Particulate | 0.040767 | lb/MMBtu | Part II | 0 | NC-39C | 3 |  | 10.0558 | 206 | 0.40994
3138_5 | New Castle Plant |  | 3138 | 5 | NC5-2 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | 0 | NC-21B | 3 |  | 10.0558 | 206 | 0.47262
3138_5 | New Castle Plant |  | 3138 | 5 | NC5-2 | Filterable Particulate | 0.0484 | lb/MMBtu | Part II | 0 | NC-39B | 3 |  | 10.0558 | 206 | 0.4867
2823_B2 | Milton R. Young Station |  | 2823 | B2 | 2 | Filterable Particulate | 0.0044195 | lb/MMBtu | Part II | 0 | Sept2005 PM emissions compliance study | 1 |  | 13.2075 | 207 | 0.058371
2823_B2 | Milton R. Young Station |  | 2823 | B2 | 2 | Filterable Particulate | 0.0062038 | lb/MMBtu | Part II | 0 | AUG2006 PM Emissions Compliance Study | 1 |  | 13.2075 | 207 | 0.081938
2324_4 | Reid Gardner |  | 2324 | 4 | 4 | Filterable Particulate | 0.0056433 | lb/MMBtu | Part II | 0 | U4_2005_COMPLIANCE ALT | 3 |  | 10.5196 | 208 | 0.059365
2324_4 | Reid Gardner |  | 2324 | 4 | 4 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | U4_2006_COMPLIANCE | 1 |  | 10.5196 | 208 | 0.063117
2324_4 | Reid Gardner |  | 2324 | 4 | 4 | Filterable Particulate | 0.00629 | lb/MMBtu | Part II | 0 | U4_2005_COMPLIANCE | 3 |  | 10.5196 | 208 | 0.066168
2324_4 | Reid Gardner |  | 2324 | 4 | 4 | Filterable Particulate | 0.0093333 | lb/MMBtu | Part II | 0 | U4_2007_COMPLIANCE | 3 |  | 10.5196 | 208 | 0.098183
2324_4 | Reid Gardner |  | 2324 | 4 | 4 | Filterable Particulate | 0.0096667 | lb/MMBtu | Part II | 0 | U4_2008_COMPLIANCE | 3 |  | 10.5196 | 208 | 0.10169
2324_4 | Reid Gardner |  | 2324 | 4 | 4 | Filterable Particulate | 0.0097933 | lb/MMBtu | Part II | 0 | U4_2009_COMPLIANCE | 3 |  | 10.5196 | 208 | 0.10302
892_Unit 1 | Hennepin Power Station |  | 892 | Unit 1 | 001 | Filterable Particulate | 0.0058037 | lb/MMBtu | ERT | No |  | 3 | 1884 | 10.3467 | 209 | 0.060049
628_4 | Crystal River Power Plant |  | 628 | 4 | CryR_Cfg_4 | Filterable Particulate | 0.0060667 | lb/MMBtu | Part II | 0 | CryR_Blr_4_Test_4 | 3 |  | 9.8999 | 210 | 0.060059
628_4 | Crystal River Power Plant |  | 628 | 4 | CryR_Cfg_4 | Filterable Particulate | 0.013333 | lb/MMBtu | Part II | 0 | CryR_Blr_4_Test_1 | 3 |  | 9.8999 | 210 | 0.132
628_4 | Crystal River Power Plant |  | 628 | 4 | CryR_Cfg_4 | Filterable Particulate | 0.0192 | lb/MMBtu | Part II | 0 | CryR_Blr_4_Test_3 | 3 |  | 9.8999 | 210 | 0.19008
628_4 | Crystal River Power Plant |  | 628 | 4 | CryR_Cfg_4 | Filterable Particulate | 0.02 | lb/MMBtu | Part II | 0 | CryR_Blr_4_Test_2 | 3 |  | 9.8999 | 210 | 0.198
628_4 | Crystal River Power Plant |  | 628 | 4 | CryR_Cfg_4 | Filterable Particulate | 0.038033 | lb/MMBtu | Part II | 0 | CryR_Blr_4_Test_5 | 3 |  | 9.8999 | 210 | 0.37653
628_4 | Crystal River Power Plant |  | 628 | 4 | CryR_Cfg_4 | Filterable Particulate | 0.052067 | lb/MMBtu | Part II | 0 | CryR_Blr_4_Test_6 | 3 |  | 9.8999 | 210 | 0.51545
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.0056667 | lb/MMBtu | Part II | 0 | COF3 - 2009 | 3 |  | 10.605 | 211 | 0.060095
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | 0 | COF3 - 10/24/2008 | 3 |  | 10.605 | 211 | 0.088375
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.011365 | lb/MMBtu | ERT | No |  | 6 | 2274 | 10.605 | 211 | 0.12053
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.012333 | lb/MMBtu | Part II | 0 | COF3 - 2005 | 3 |  | 10.605 | 211 | 0.13079
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.015667 | lb/MMBtu | Part II | 0 | COF3 - 2006 | 3 |  | 10.605 | 211 | 0.16614
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 0 | COF3 - 2007 | 3 |  | 10.605 | 211 | 0.17675
47_3 | Colbert |  | 47 | 3 | 3 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | COF3 - 09/16/2008 | 3 |  | 10.605 | 211 | 0.26866
1241_2 | La Cygne |  | 1241 | 2 | 2 | Filterable Particulate | 0.0053594 | lb/MMBtu | ERT | No |  | 6 | 1372 | 11.2409 | 212 | 0.060244
4143_1 | Genoa |  | 4143 | 1 | 001 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | 3 | 3 |  | 9.7127 | 213 | 0.061514
4143_1 | Genoa |  | 4143 | 1 | 001 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 9.7127 | 213 | 0.061514
4143_1 | Genoa |  | 4143 | 1 | 001 | Filterable Particulate | 0.013667 | lb/MMBtu | Part II | 0 | 4 | 3 |  | 9.7127 | 213 | 0.13274
10641_B1 | Cambria Cogen |  | 10641 | B1 | 001 | Filterable Particulate | 0.0054023 | lb/MMBtu | ERT | No |  | 3 | 2226 | 11.4286 | 214 | 0.06174
892_Unit 2 | Hennepin Power Station |  | 892 | Unit 2 | 002 | Filterable Particulate | 0.0058037 | lb/MMBtu | ERT | No |  | 3 | 1884 | 10.6838 | 215 | 0.062005
1250_3 | Lawrence Energy Center |  | 1250 | 3 | 3 | Filterable Particulate | 0.0055865 | lb/MMBtu | ERT | No |  | 3 | 1854 | 11.1207 | 216 | 0.062126
1250_3 | Lawrence Energy Center |  | 1250 | 3 | 3 | Filterable Particulate | 0.089856 | lb/MMBtu | Part II | 0 | CAM 0507/3 | 9 |  | 11.1207 | 216 | 0.99926
50_7 | Widows Creek |  | 50 | 7 | 7 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | WCF7 - 10/30/2008 | 3 |  | 9.88 | 217 | 0.062573
50_7 | Widows Creek |  | 50 | 7 | 7 | Filterable Particulate | 0.010667 | lb/MMBtu | Part II | 0 | WCF7 - 2009 | 3 |  | 9.88 | 217 | 0.10539
50_7 | Widows Creek |  | 50 | 7 | 7 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | WCF7 - 12/23/2008 | 3 |  | 9.88 | 217 | 0.13832
50_7 | Widows Creek |  | 50 | 7 | 7 | Filterable Particulate | 0.014333 | lb/MMBtu | Part II | 0 | WCF7 - 2007 | 3 |  | 9.88 | 217 | 0.14161
50_7 | Widows Creek |  | 50 | 7 | 7 | Filterable Particulate | 0.021 | lb/MMBtu | Part II | 0 | WCF7 - 2006 | 3 |  | 9.88 | 217 | 0.20748
10075_2 | Taconite Harbor Energy Center |  | 10075 | 2 | THEC2 | Filterable Particulate | 0.0054656 | lb/MMBtu | ERT | No |  | 6 | 1734 | 11.5278 | 218 | 0.063006
10075_2 | Taconite Harbor Energy Center |  | 10075 | 2 | THEC2 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | 0 | 2-July2008-PM/PM10 | 3 |  | 11.5278 | 218 | 0.28051
10075_2 | Taconite Harbor Energy Center |  | 10075 | 2 | THEC2 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | 0 | 2-Dec-PM | 3 |  | 11.5278 | 218 | 0.32278
3118_1 | Conemaugh |  | 3118 | 1 | CON-1 | Filterable Particulate | 0.0065667 | lb/MMBtu | Part II | 0 | C-190 | 3 |  | 9.5994 | 219 | 0.063036
983_3 | Clifty Creek |  | 983 | 3 | Unit 3 | Filterable Particulate | 0.0061 | lb/MMBtu | Part II | 0 | Stack1Particulate2007 | 1 |  | 10.3898 | 220 | 0.063378
983_3 | Clifty Creek |  | 983 | 3 | Unit 3 | Filterable Particulate | 0.0124 | lb/MMBtu | Part II | 0 | Stack1Particulate2005 | 1 |  | 10.3898 | 220 | 0.12883
983_3 | Clifty Creek |  | 983 | 3 | Unit 3 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | Stack1Particulate2009 | 1 |  | 10.3898 | 220 | 0.13507
4041_6 | South Oak Creek |  | 4041 | 6 | OCPP-B6 | Filterable Particulate | 0.0070333 | lb/MMBtu | Part II | 0 | OCPP-PM.Hg-B6-6.2005 | 3 |  | 9.0504 | 221 | 0.063654
4041_6 | South Oak Creek |  | 4041 | 6 | OCPP-B6 | Filterable Particulate | 0.0097667 | lb/MMBtu | Part II | 0 | OCPP-PM-B6-3.2007 | 3 |  | 9.0504 | 221 | 0.088392
4041_6 | South Oak Creek |  | 4041 | 6 | OCPP-B6 | Filterable Particulate | 0.019567 | lb/MMBtu | Part II | 0 | OCPP-PM-B6-7.22.2008 | 3 |  | 9.0504 | 221 | 0.17709
4041_6 | South Oak Creek |  | 4041 | 6 | OCPP-B6 | Filterable Particulate | 0.033967 | lb/MMBtu | Part II | 0 | OCPP-PM-B6-7.8.2008 | 3 |  | 9.0504 | 221 | 0.30741
983_2 | Clifty Creek |  | 983 | 2 | Unit 2 | Filterable Particulate | 0.0061 | lb/MMBtu | Part II | 0 | Stack1Particulate2007 | 1 |  | 10.4523 | 222 | 0.063759
983_2 | Clifty Creek |  | 983 | 2 | Unit 2 | Filterable Particulate | 0.0124 | lb/MMBtu | Part II | 0 | Stack1Particulate2005 | 1 |  | 10.4523 | 222 | 0.12961
983_2 | Clifty Creek |  | 983 | 2 | Unit 2 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | Stack1Particulate2009 | 1 |  | 10.4523 | 222 | 0.13588
3297_WAT1 | Wateree |  | 3297 | WAT1 | WAT001 | Filterable Particulate | 0.00734 | lb/MMBtu | Part II | 0 | PM-HCL-HF-HG-07/06-WAT1 | 1 |  | 8.6937 | 223 | 0.063812
3297_WAT1 | Wateree |  | 3297 | WAT1 | WAT001 | Filterable Particulate | 0.0096 | lb/MMBtu | Part II | 0 | PM-05/06-WAT1 | 1 |  | 8.6937 | 223 | 0.08346
3297_WAT1 | Wateree |  | 3297 | WAT1 | WAT001 | Filterable Particulate | 0.0116 | lb/MMBtu | Part II | 0 | PM-05/07-WAT1 | 1 |  | 8.6937 | 223 | 0.10085
3297_WAT1 | Wateree |  | 3297 | WAT1 | WAT001 | Filterable Particulate | 0.0118 | lb/MMBtu | Part II | 0 | PM-05.05-WAT1 | 1 |  | 8.6937 | 223 | 0.10259
3297_WAT1 | Wateree |  | 3297 | WAT1 | WAT001 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | 0 | PM-05/08-WAT1 | 1 |  | 8.6937 | 223 | 0.10606
3297_WAT1 | Wateree |  | 3297 | WAT1 | WAT001 | Filterable Particulate | 0.0533 | lb/MMBtu | Part II | 0 | PM-05/09-WAT1 | 1 |  | 8.6937 | 223 | 0.46338
6639_G1 | R D Green |  | 6639 | G1 | 1 | Filterable Particulate | 0.0059367 | lb/MMBtu | Part II | 0 | G1 compliance test 2008 | 3 |  | 10.8168 | 224 | 0.064216
7343_4 | George Neal South |  | 7343 | 4 | 4 | Filterable Particulate | 0.0064393 | lb/MMBtu | Part II | 0 | PM-July 2008 | 1 |  | 10.1173 | 225 | 0.065148
7343_4 | George Neal South |  | 7343 | 4 | 4 | Filterable Particulate | 0.018579 | lb/MMBtu | Part II | 0 | PM-Sept 2008 | 1 |  | 10.1173 | 225 | 0.18797
983_1 | Clifty Creek |  | 983 | 1 | Unit 1 | Filterable Particulate | 0.0061 | lb/MMBtu | Part II | 0 | Stack1Particulate2007 | 1 |  | 10.7248 | 226 | 0.065422
983_1 | Clifty Creek |  | 983 | 1 | Unit 1 | Filterable Particulate | 0.0124 | lb/MMBtu | Part II | 0 | Stack1Particulate2005 | 1 |  | 10.7248 | 226 | 0.13299
983_1 | Clifty Creek |  | 983 | 1 | Unit 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | Stack1Particulate2009 | 1 |  | 10.7248 | 226 | 0.13942
4041_5 | South Oak Creek |  | 4041 | 5 | OCPP-B5 | Filterable Particulate | 0.0072 | lb/MMBtu | Part II | 0 | OCPP-PM-B5-3.2007 | 3 |  | 9.1136 | 227 | 0.065618
4041_5 | South Oak Creek |  | 4041 | 5 | OCPP-B5 | Filterable Particulate | 0.0076 | lb/MMBtu | Part II | 0 | OCPP-PM.Hg-B5-7.2005 | 3 |  | 9.1136 | 227 | 0.069263
4041_5 | South Oak Creek |  | 4041 | 5 | OCPP-B5 | Filterable Particulate | 0.0126 | lb/MMBtu | Part II | 0 | OCPP-PM-B5-7.23.2008 | 3 |  | 9.1136 | 227 | 0.11483
4042_1 | Valley |  | 4042 | 1 | VAPP-B1 | Filterable Particulate | 0.005443 | lb/MMBtu | ERT | No |  | 6 | 1244 | 12.0556 | 228 | 0.065618
4042_1 | Valley |  | 4042 | 1 | VAPP-B1 | Filterable Particulate | 0.0083256 | lb/MMBtu | ERT | No |  | 6 | 734 | 12.0556 | 228 | 0.10037
4042_1 | Valley |  | 4042 | 1 | VAPP-B1 | Filterable Particulate | 0.0087667 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2-8.2005 | 3 |  | 12.0556 | 228 | 0.10569
4042_1 | Valley |  | 4042 | 1 | VAPP-B1 | Filterable Particulate | 0.0087667 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2B3B4-8.2005 | 3 |  | 12.0556 | 228 | 0.10569
4042_1 | Valley |  | 4042 | 1 | VAPP-B1 | Filterable Particulate | 0.010767 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2-8.2009 | 3 |  | 12.0556 | 228 | 0.1298
3788_5 | Potomac River |  | 3788 | 5 | 5 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | 0 | C5 PM 0908 | 1 |  | 8.8981 | 229 | 0.065846
3788_5 | Potomac River |  | 3788 | 5 | 5 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | CSC345 PM 0909 | 1 |  | 8.8981 | 229 | 0.19576
4042_2 | Valley |  | 4042 | 2 | VAPP-B2 | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2-8.2005 | 3 |  | 12.0556 | 230 | 0.066306
4042_2 | Valley |  | 4042 | 2 | VAPP-B2 | Filterable Particulate | 0.0055 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2B3B4-8.2005 | 3 |  | 12.0556 | 230 | 0.066306
4042_2 | Valley |  | 4042 | 2 | VAPP-B2 | Filterable Particulate | 0.013233 | lb/MMBtu | Part II | 0 | VAPP-PM-B1B2-8.2009 | 3 |  | 12.0556 | 230 | 0.15954
1378_3 | Paradise |  | 1378 | 3 | 3 | Filterable Particulate | 0.0066667 | lb/MMBtu | Part II | 0 | PAF3 - 2007 | 3 |  | 9.9609 | 232 | 0.066406
1378_3 | Paradise |  | 1378 | 3 | 3 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | PAF3 - 2008 | 3 |  | 9.9609 | 232 | 0.099609
1378_3 | Paradise |  | 1378 | 3 | 3 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | PAF3 - 2009 | 3 |  | 9.9609 | 232 | 0.21914
3947_3 | Kammer |  | 3947 | 3 | K-3 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | 0 | July2009PM | 1 |  | 9.0779 | 233 | 0.067176
3947_3 | Kammer |  | 3947 | 3 | K-3 | Filterable Particulate | 0.0089 | lb/MMBtu | Part II | 0 | July2006PM | 1 |  | 9.0779 | 233 | 0.080793
3947_2 | Kammer |  | 3947 | 2 | K-2 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | 0 | July2009PM | 1 |  | 9.0779 | 234 | 0.067176
3947_2 | Kammer |  | 3947 | 2 | K-2 | Filterable Particulate | 0.0089 | lb/MMBtu | Part II | 0 | July2006PM | 1 |  | 9.0779 | 234 | 0.080793
3947_1 | Kammer |  | 3947 | 1 | K-1 | Filterable Particulate | 0.0074 | lb/MMBtu | Part II | 0 | July2009PM | 1 |  | 9.0779 | 235 | 0.067176
3947_1 | Kammer |  | 3947 | 1 | K-1 | Filterable Particulate | 0.0089 | lb/MMBtu | Part II | 0 | July2006PM | 1 |  | 9.0779 | 235 | 0.080793
1379_5 | Shawnee |  | 1379 | 5 | 5 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | SHF1-5 - 2007 | 3 |  | 9.6629 | 236 | 0.06764
1379_5 | Shawnee |  | 1379 | 5 | 5 | Filterable Particulate | 0.036333 | lb/MMBtu | Part II | 0 | SHF1-5 - 2005 | 3 |  | 9.6629 | 236 | 0.35108
1379_4 | Shawnee |  | 1379 | 4 | 4 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | SHF1-5 - 2007 | 3 |  | 9.6629 | 237 | 0.06764
1379_4 | Shawnee |  | 1379 | 4 | 4 | Filterable Particulate | 0.036333 | lb/MMBtu | Part II | 0 | SHF1-5 - 2005 | 3 |  | 9.6629 | 237 | 0.35108
1379_3 | Shawnee |  | 1379 | 3 | 3 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | SHF1-5 - 2007 | 3 |  | 9.6629 | 238 | 0.06764
1379_3 | Shawnee |  | 1379 | 3 | 3 | Filterable Particulate | 0.036333 | lb/MMBtu | Part II | 0 | SHF1-5 - 2005 | 3 |  | 9.6629 | 238 | 0.35108
1379_2 | Shawnee |  | 1379 | 2 | 2 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | SHF1-5 - 2007 | 3 |  | 9.6629 | 239 | 0.06764
1379_2 | Shawnee |  | 1379 | 2 | 2 | Filterable Particulate | 0.036333 | lb/MMBtu | Part II | 0 | SHF1-5 - 2005 | 3 |  | 9.6629 | 239 | 0.35108
1379_1 | Shawnee |  | 1379 | 1 | 1 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | SHF1-5 - 2007 | 3 |  | 9.6629 | 240 | 0.06764
1379_1 | Shawnee |  | 1379 | 1 | 1 | Filterable Particulate | 0.036333 | lb/MMBtu | Part II | 0 | SHF1-5 - 2005 | 3 |  | 9.6629 | 240 | 0.35108
3131_1 | Shawville |  | 3131 | 1 | SHAW1-2 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | SH-185B | 3 |  | 10.792 | 241 | 0.068349
3131_1 | Shawville |  | 3131 | 1 | SHAW1-2 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | SH-186 | 4 |  | 10.792 | 241 | 0.43168
3131_1 | Shawville |  | 3131 | 1 | SHAW1-2 | Filterable Particulate | 0.21223 | lb/MMBtu | Part II | 0 | SH-184-U1 | 3 |  | 10.792 | 241 | 2.2904
3131_1 | Shawville |  | 3131 | 1 | SHAW1-2 | Filterable Particulate | 0.399 | lb/MMBtu | Part II | 0 | Sh-185A | 3 |  | 10.792 | 241 | 4.306
10641_B2 | Cambria Cogen |  | 10641 | B2 | 002 | Filterable Particulate | 0.0059818 | lb/MMBtu | ERT | No |  | 3 | 22261 | 11.4286 | 242 | 0.068363
4054_2 | Nelson Dewey |  | 4054 | 2 | Unit 2 | Filterable Particulate | 0.0069 | lb/MMBtu | Part II | 0 | ND2-PM-20091013 | 1 |  | 9.9146 | 243 | 0.068411
3407_4 | Kingston |  | 3407 | 4 | 4 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | KIF1-5 - 2005 | 3 |  | 9.3771 | 244 | 0.068766
3407_4 | Kingston |  | 3407 | 4 | 4 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | KIF1-5 - 2007 | 3 |  | 9.3771 | 244 | 0.1219
3407_3 | Kingston |  | 3407 | 3 | 3 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | KIF1-5 - 2005 | 3 |  | 9.3771 | 245 | 0.068766
3407_3 | Kingston |  | 3407 | 3 | 3 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | KIF1-5 - 2007 | 3 |  | 9.3771 | 245 | 0.1219
3407_2 | Kingston |  | 3407 | 2 | 2 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | KIF1-5 - 2005 | 3 |  | 9.3771 | 246 | 0.068766
3407_2 | Kingston |  | 3407 | 2 | 2 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | KIF1-5 - 2007 | 3 |  | 9.3771 | 246 | 0.1219
3407_1 | Kingston |  | 3407 | 1 | 1 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | KIF1-5 - 2005 | 3 |  | 9.3771 | 247 | 0.068766
3407_1 | Kingston |  | 3407 | 1 | 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | KIF1-5 - 2007 | 3 |  | 9.3771 | 247 | 0.1219
50_2 | Widows Creek |  | 50 | 2 | 2 | Filterable Particulate | 0.0063333 | lb/MMBtu | Part II | 0 | WCF2 - 2007 | 3 |  | 10.8677 | 248 | 0.068829
50_2 | Widows Creek |  | 50 | 2 | 2 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | WCF2 - 2006 | 3 |  | 10.8677 | 248 | 0.086942
50_2 | Widows Creek |  | 50 | 2 | 2 | Filterable Particulate | 0.012667 | lb/MMBtu | Part II | 0 | WCF2 - 2005 | 3 |  | 10.8677 | 248 | 0.13766
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.006 | lb/MMBtu | Part II | 0 | 7 | 1 |  | 11.5385 | 249 | 0.069231
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0064 | lb/MMBtu | Part II | 0 | 8 | 1 |  | 11.5385 | 249 | 0.073846
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0065 | lb/MMBtu | Part II | 0 | 5 | 1 |  | 11.5385 | 249 | 0.075
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0068 | lb/MMBtu | Part II | 0 | 10 | 1 |  | 11.5385 | 249 | 0.078462
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | 12 | 1 |  | 11.5385 | 249 | 0.080769
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0075 | lb/MMBtu | Part II | 0 | 6 | 1 |  | 11.5385 | 249 | 0.086538
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0075 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 11.5385 | 249 | 0.086538
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0086 | lb/MMBtu | Part II | 0 | 13 | 1 |  | 11.5385 | 249 | 0.099231
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0096 | lb/MMBtu | Part II | 0 | 11 | 1 |  | 11.5385 | 249 | 0.11077
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0107 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 11.5385 | 249 | 0.12346
2790_B2 | R.M. Heskett Station |  | 2790 | B2 | B2 | Filterable Particulate | 0.0214 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 11.5385 | 249 | 0.24692
8224_2 | North Valmy |  | 8224 | 2 | 2 | Filterable Particulate | 0.0065 | lb/MMBtu | Part II | 0 | U2_2008_COMPLIANCE | 3 |  | 10.6625 | 250 | 0.069306
8224_2 | North Valmy |  | 8224 | 2 | 2 | Filterable Particulate | 0.013867 | lb/MMBtu | Part II | 0 | U2_2006_COMPLIANCE | 3 |  | 10.6625 | 250 | 0.14785
8224_2 | North Valmy |  | 8224 | 2 | 2 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | U2_2007_COMPLIANCE | 1 |  | 10.6625 | 250 | 0.31987
6249_4 | Winyah |  | 6249 | 4 | W4 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | W4PM2009 | 1 |  | 10.0033 | 251 | 0.070023
6249_4 | Winyah |  | 6249 | 4 | W4 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | W4PM2007 | 1 |  | 10.0033 | 251 | 0.18006
6249_4 | Winyah |  | 6249 | 4 | W4 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 0 | W4PM2005 | 1 |  | 10.0033 | 251 | 0.25008
6249_4 | Winyah |  | 6249 | 4 | W4 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 0 | W4PM2008 | 1 |  | 10.0033 | 251 | 0.25008
6249_4 | Winyah |  | 6249 | 4 | W4 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | W4PM2006 | 1 |  | 10.0033 | 251 | 0.67022
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.0077 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (May 15, 2007) | 3 |  | 9.2032 | 252 | 0.070864
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.0090448 | lb/MMBtu | Part II | 0 | Units 1 and 2 PM Emissions Test (June 11, 2008) | 3 |  | 9.2032 | 252 | 0.083241
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.014033 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (June 4, 2009) | 3 |  | 9.2032 | 252 | 0.12915
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.016133 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (June 10, 2005) | 3 |  | 9.2032 | 252 | 0.14848
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.020067 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (February 14, 2006) | 3 |  | 9.2032 | 252 | 0.18468
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.027733 | lb/MMBtu | Part II | 0 | Unit 2 Engineering PMTest during Wood Chips Test | 3 |  | 9.2032 | 252 | 0.25523
10_2 | Greene County |  | 10 | 2 | Unit 2 | Filterable Particulate | 0.0781 | lb/MMBtu | Part II | 0 | Unit 2 CAM Test (February 16, 2006) | 3 |  | 9.2032 | 252 | 0.71877
6177_U2B | Coronado Generating Station |  | 6177 | U2B | U2B | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | 7 | 1 |  | 10.3351 | 253 | 0.072346
6177_U2B | Coronado Generating Station |  | 6177 | U2B | U2B | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 6 | 1 |  | 10.3351 | 253 | 0.10335
6177_U2B | Coronado Generating Station |  | 6177 | U2B | U2B | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 10.3351 | 253 | 0.11369
6177_U2B | Coronado Generating Station |  | 6177 | U2B | U2B | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | 10 | 1 |  | 10.3351 | 253 | 0.19637
6177_U2B | Coronado Generating Station |  | 6177 | U2B | U2B | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | 8 | 1 |  | 10.3351 | 253 | 0.19637
6009_2 | White Bluff |  | 6009 | 2 | 002 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 9.8751 | 254 | 0.072418
1832_EU001 | Erickson Station |  | 1832 | EU001 | 001 | Filterable Particulate | 0.0071836 | lb/MMBtu | ERT | No |  | 6 | 942 | 10.1091 | 255 | 0.07262
1832_EU001 | Erickson Station |  | 1832 | EU001 | 001 | Filterable Particulate | 0.010033 | lb/MMBtu | Part II | 0 | PM-9/05 | 3 |  | 10.1091 | 255 | 0.10143
1381_C3 | Kenneth C Coleman |  | 1381 | C3 | 4 | Filterable Particulate | 0.00693 | lb/MMBtu | Part II | 0 | Coleman compliance test 2009 | 3 |  | 10.4887 | 256 | 0.072687
1381_C3 | Kenneth C Coleman |  | 1381 | C3 | 4 | Filterable Particulate | 0.0089333 | lb/MMBtu | Part II | 0 | Coleman compliance test 2006 | 3 |  | 10.4887 | 256 | 0.093699
1381_C2 | Kenneth C Coleman |  | 1381 | C2 | 4 | Filterable Particulate | 0.00693 | lb/MMBtu | Part II | 0 | Coleman compliance test 2009 | 3 |  | 10.4887 | 257 | 0.072687
1381_C2 | Kenneth C Coleman |  | 1381 | C2 | 4 | Filterable Particulate | 0.0089333 | lb/MMBtu | Part II | 0 | Coleman compliance test 2006 | 3 |  | 10.4887 | 257 | 0.093699
1381_C1 | Kenneth C Coleman |  | 1381 | C1 | 4 | Filterable Particulate | 0.00693 | lb/MMBtu | Part II | 0 | Coleman compliance test 2009 | 3 |  | 10.4887 | 258 | 0.072687
1381_C1 | Kenneth C Coleman |  | 1381 | C1 | 4 | Filterable Particulate | 0.0089333 | lb/MMBtu | Part II | 0 | Coleman compliance test 2006 | 3 |  | 10.4887 | 258 | 0.093699
47_5 | Colbert |  | 47 | 5 | 5 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | COF5 - 2009 | 3 |  | 10.0855 | 259 | 0.07396
47_5 | Colbert |  | 47 | 5 | 5 | Filterable Particulate | 0.011333 | lb/MMBtu | Part II | 0 | COF5 - 2008 | 3 |  | 10.0855 | 259 | 0.1143
47_5 | Colbert |  | 47 | 5 | 5 | Filterable Particulate | 0.0175 | lb/MMBtu | Part II | 0 | COF5 - 2005 | 2 |  | 10.0855 | 259 | 0.1765
47_5 | Colbert |  | 47 | 5 | 5 | Filterable Particulate | 0.042667 | lb/MMBtu | Part II | 0 | COF5 - 2006 | 3 |  | 10.0855 | 259 | 0.43031
47_5 | Colbert |  | 47 | 5 | 5 | Filterable Particulate | 0.073 | lb/MMBtu | Part II | 0 | COF5 - 2007 | 3 |  | 10.0855 | 259 | 0.73624
6096_NC2 | Nebraska City |  | 6096 | NC2 | NC2 | Filterable Particulate | 0.0073 | lb/MMBtu | Part II | 0 | PM NC Unit 2 | 1 |  | 10.147 | 260 | 0.074073
6096_NC2 | Nebraska City |  | 6096 | NC2 | NC2 | Filterable Particulate | 0.0094911 | lb/MMBtu | ERT | No |  | 6 | 1997 | 10.147 | 260 | 0.096307
3130_2 | Seward |  | 3130 | 2 | SEW-1 | Filterable Particulate | 0.0070333 | lb/MMBtu | Part II | 0 | SE-116 | 3 |  | 10.5983 | 261 | 0.074541
3130_2 | Seward |  | 3130 | 2 | SEW-1 | Filterable Particulate | 0.010822 | lb/MMBtu | ERT | No |  | 3 | 524 | 10.5983 | 261 | 0.1147
3130_1 | Seward |  | 3130 | 1 | SEW-1 | Filterable Particulate | 0.0070333 | lb/MMBtu | Part II | 0 | SE-116 | 3 |  | 10.5983 | 262 | 0.074541
3130_1 | Seward |  | 3130 | 1 | SEW-1 | Filterable Particulate | 0.010822 | lb/MMBtu | ERT | No |  | 3 | 524 | 10.5983 | 262 | 0.1147
1008_2 | R. Gallagher |  | 1008 | 2 | 2-2007 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | STACKA052808 | 3 |  | 9.7333 | 263 | 0.074622
1008_1 | R. Gallagher |  | 1008 | 1 | 1-2007 | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | STACKA052808 | 3 |  | 9.7333 | 264 | 0.074622
3788_4 | Potomac River |  | 3788 | 4 | 4 | Filterable Particulate | 0.0084 | lb/MMBtu | Part II | 0 | C4 PM 0108 | 1 |  | 8.8981 | 265 | 0.074744
3788_4 | Potomac River |  | 3788 | 4 | 4 | Filterable Particulate | 0.0144 | lb/MMBtu | Part II | 0 | C4 PM 1208 | 1 |  | 8.8981 | 265 | 0.12813
3788_4 | Potomac River |  | 3788 | 4 | 4 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | CSC345 PM 0909 | 1 |  | 8.8981 | 265 | 0.19576
3407_5 | Kingston |  | 3407 | 5 | 5 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | KIF1-5 - 2005 | 3 |  | 10.28 | 266 | 0.075387
3407_5 | Kingston |  | 3407 | 5 | 5 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | KIF1-5 - 2007 | 3 |  | 10.28 | 266 | 0.13364
6204_3 | Laramie River Station |  | 6204 | 3 | 3 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | Unit 3 Particulate 2005 | 3 |  | 10.8197 | 267 | 0.075738
6204_3 | Laramie River Station |  | 6204 | 3 | 3 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | Unit 3 Particulate 2009 | 3 |  | 10.8197 | 267 | 0.09377
6204_3 | Laramie River Station |  | 6204 | 3 | 3 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | Unit 3 Particulate 2008 | 3 |  | 10.8197 | 267 | 0.097377
6204_3 | Laramie River Station |  | 6204 | 3 | 3 | Filterable Particulate | 0.010667 | lb/MMBtu | Part II | 0 | Unit 3 Particulate 2006 | 3 |  | 10.8197 | 267 | 0.11541
6204_3 | Laramie River Station |  | 6204 | 3 | 3 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | Unit 3 Particulate 2007 | 3 |  | 10.8197 | 267 | 0.1623
3399_1 | Cumberland |  | 3399 | 1 | 1 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | CUF1 - 2007 | 3 |  | 10.8692 | 268 | 0.076085
3399_1 | Cumberland |  | 3399 | 1 | 1 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | CUF1 - 2009 | 3 |  | 10.8692 | 268 | 0.0942
130_4 | Cross |  | 130 | 4 | C4 | Filterable Particulate | 0.007 | lb/MMBtu | Part II | 0 | C4PM2008 | 1 |  | 10.8768 | 269 | 0.076138
130_4 | Cross |  | 130 | 4 | C4 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | C4PM2009 | 1 |  | 10.8768 | 269 | 0.087014
130_4 | Cross |  | 130 | 4 | C4 | Filterable Particulate | 0.012875 | lb/MMBtu | ERT | No |  | 3 | 1119 | 10.8768 | 269 | 0.14004
113_2 | Cholla |  | 113 | 2 | 002 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 9.6328 | 270 | 0.077062
113_2 | Cholla |  | 113 | 2 | 002 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | 6 | 1 |  | 9.6328 | 270 | 0.12523
113_2 | Cholla |  | 113 | 2 | 002 | Filterable Particulate | 0.0165 | lb/MMBtu | Part II | 0 | 10 | 1 |  | 9.6328 | 270 | 0.15894
113_2 | Cholla |  | 113 | 2 | 002 | Filterable Particulate | 0.0176 | lb/MMBtu | Part II | 0 | 14 | 1 |  | 9.6328 | 270 | 0.16954
113_2 | Cholla |  | 113 | 2 | 002 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | 0 | 18 | 1 |  | 9.6328 | 270 | 0.26972
6034_2 | Belle River |  | 6034 | 2 | BR2-Config | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | PM2007_Aug_2 | 3 |  | 10.0635 | 271 | 0.077154
6034_2 | Belle River |  | 6034 | 2 | BR2-Config | Filterable Particulate | 0.048 | lb/MMBtu | Part II | 0 | PM2007_Feb_2 | 2 |  | 10.0635 | 271 | 0.48305
3_4 | Barry |  | 3 | 4 | Unit 4 | Filterable Particulate | 0.0083 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (June 3, 2009) | 3 |  | 9.3422 | 272 | 0.07754
3_4 | Barry |  | 3 | 4 | Unit 4 | Filterable Particulate | 0.017933 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (April 9, 2008) | 3 |  | 9.3422 | 272 | 0.16754
3_4 | Barry |  | 3 | 4 | Unit 4 | Filterable Particulate | 0.023067 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (February 22, 2007) | 3 |  | 9.3422 | 272 | 0.21549
10343_SG-101 | Foster Wheeler Mt Carmel Cogen |  | 10343 | SG-101 | SG-101 | Filterable Particulate | 0.0066667 | lb/MMBtu | Part II | 0 | PM 2007 | 3 |  | 11.7442 | 273 | 0.078295
10343_SG-101 | Foster Wheeler Mt Carmel Cogen |  | 10343 | SG-101 | SG-101 | Filterable Particulate | 0.0086667 | lb/MMBtu | Part II | 0 | PM 2009 | 3 |  | 11.7442 | 273 | 0.10178
10343_SG-101 | Foster Wheeler Mt Carmel Cogen |  | 10343 | SG-101 | SG-101 | Filterable Particulate | 0.0093333 | lb/MMBtu | Part II | 0 | PM 2005 | 3 |  | 11.7442 | 273 | 0.10961
6021_C3 | Craig |  | 6021 | C3 | C3 | Filterable Particulate | 0.0091333 | lb/MMBtu | Part II | 0 | C3 2009 PM test | 3 |  | 8.6276 | 274 | 0.078799
6002_1 | James H. Miller Jr. |  | 6002 | 1 | Unit 1 | Filterable Particulate | 0.0081507 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (April 16, 2008) | 3 |  | 9.6772 | 275 | 0.078876
6002_1 | James H. Miller Jr. |  | 6002 | 1 | Unit 1 | Filterable Particulate | 0.010471 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Emissions Test (May 2, 2006) | 3 |  | 9.6772 | 275 | 0.10133
6002_1 | James H. Miller Jr. |  | 6002 | 1 | Unit 1 | Filterable Particulate | 0.025999 | lb/MMBtu | Part II | 0 | Unit 1 CAM Test (May 3, 2006) | 3 |  | 9.6772 | 275 | 0.2516
55749_PC1 | Hardin Generator Project |  | 55749 | PC1 | PC1 | Filterable Particulate | 0.0072 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 10.958 | 276 | 0.078897
55749_PC1 | Hardin Generator Project |  | 55749 | PC1 | PC1 | Filterable Particulate | 0.012426 | lb/MMBtu | ERT | No |  | 6 | 2112 | 10.958 | 276 | 0.13616
3942_2 | Albright Power Station |  | 3942 | 2 | Unit_2 | Filterable Particulate | 0.0099574 | lb/MMBtu | ERT | No |  | 3 | 1113 | 7.9383 | 277 | 0.079045
50_3 | Widows Creek |  | 50 | 3 | 3 | Filterable Particulate | 0.0073333 | lb/MMBtu | Part II | 0 | WCF3 - 2006 | 3 |  | 10.8677 | 278 | 0.079697
50_3 | Widows Creek |  | 50 | 3 | 3 | Filterable Particulate | 0.025667 | lb/MMBtu | Part II | 0 | WCF3 - 2008 | 3 |  | 10.8677 | 278 | 0.27894
50_3 | Widows Creek |  | 50 | 3 | 3 | Filterable Particulate | 0.032333 | lb/MMBtu | Part II | 0 | WCF3 - 2005 | 3 |  | 10.8677 | 278 | 0.35139
50_3 | Widows Creek |  | 50 | 3 | 3 | Filterable Particulate | 0.092333 | lb/MMBtu | Part II | 0 | WCF3 - 2007 | 3 |  | 10.8677 | 278 | 1.0035
3118_2 | Conemaugh |  | 3118 | 2 | CON-2 | Filterable Particulate | 0.008362 | lb/MMBtu | Part II | 0 | C-193 | 3 |  | 9.5994 | 279 | 0.08027
6017_2 | Newton |  | 6017 | 2 | 002 | Filterable Particulate | 0.0091158 | lb/MMBtu | ERT | No |  | 3 | 1902 | 8.871 | 280 | 0.080866
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.0090448 | lb/MMBtu | Part II | 0 | Units 1 and 2 PM Emissions Test (June 11, 2008) | 3 |  | 9.017 | 281 | 0.081557
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.0095 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (June 19, 2007) | 3 |  | 9.017 | 281 | 0.085662
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.013633 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (February 14, 2006) | 3 |  | 9.017 | 281 | 0.12293
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.0141 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (May 27, 2005) | 3 |  | 9.017 | 281 | 0.12714
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.016333 | lb/MMBtu | Part II | 0 | Unit 1 Engineering PMTest during Wood Chips Test | 3 |  | 9.017 | 281 | 0.14728
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.0177 | lb/MMBtu | Part II | 0 | Unit 1 Engineering PMTest during Wood Chips Test 2 | 3 |  | 9.017 | 281 | 0.1596
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.028333 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (May 28, 2009) | 3 |  | 9.017 | 281 | 0.25548
10_1 | Greene County |  | 10 | 1 | Unit 1 | Filterable Particulate | 0.083725 | lb/MMBtu | Part II | 0 | Unit 1 CAM Test (February 15, 2006) | 4 |  | 9.017 | 281 | 0.75495
6073_1 | Victor J. Daniel Jr |  | 6073 | 1 | Unit 1 | Filterable Particulate | 0.0085 | lb/MMBtu | Part II | 0 | Unit 1 PM Test Report May 19, 2009 | 1 |  | 9.6952 | 282 | 0.082409
6177_U1B | Coronado Generating Station |  | 6177 | U1B | U1B | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 10.3351 | 283 | 0.082681
6177_U1B | Coronado Generating Station |  | 6177 | U1B | U1B | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 10.3351 | 283 | 0.10335
6177_U1B | Coronado Generating Station |  | 6177 | U1B | U1B | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 10.3351 | 283 | 0.10335
6177_U1B | Coronado Generating Station |  | 6177 | U1B | U1B | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 10.3351 | 283 | 0.10335
6177_U1B | Coronado Generating Station |  | 6177 | U1B | U1B | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | 5 | 1 |  | 10.3351 | 283 | 0.13436
1743_1 | St Clair Power Plant |  | 1743 | 1 | SC1-Config | Filterable Particulate | 0.0076667 | lb/MMBtu | Part II | 0 | PM2007_Sep1 | 3 |  | 10.8882 | 284 | 0.083476
1743_1 | St Clair Power Plant |  | 1743 | 1 | SC1-Config | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | PM2007_Oct1 | 3 |  | 10.8882 | 284 | 0.087106
6018_2 | East Bend Station |  | 6018 | 2 | 2 | Filterable Particulate | 0.0087203 | lb/MMBtu | ERT | No |  | 3 | 2055 | 9.7015 | 285 | 0.0846
6018_2 | East Bend Station |  | 6018 | 2 | 2 | Filterable Particulate | 0.0318 | lb/MMBtu | Part II | 0 | UNIT2(5/21/08) | 5 |  | 9.7015 | 285 | 0.30851
6018_2 | East Bend Station |  | 6018 | 2 | 2 | Filterable Particulate | 0.04675 | lb/MMBtu | Part II | 0 | UNIT2(5/22/08) | 4 |  | 9.7015 | 285 | 0.45354
6073_2 | Victor J. Daniel Jr |  | 6073 | 2 | Unit 2 | Filterable Particulate | 0.0088 | lb/MMBtu | Part II | 0 | Unit 2 PMTest Report ‐ June 5, 2009 | 1 |  | 9.6394 | 286 | 0.084827
2549_67 | CR Huntley Generating Station |  | 2549 | 67 | 067 | Filterable Particulate | 0.0094333 | lb/MMBtu | Part II | 0 | Stack-PM-0609 | 3 |  | 9 | 287 | 0.0849
2378_2 | BL England |  | 2378 | 2 | 2 Coal w or w/o TDF | Filterable Particulate | 0.0089098 | lb/MMBtu | Part II | 0 | CAM 238-015 | 3 |  | 9.5637 | 288 | 0.08521
2378_2 | BL England |  | 2378 | 2 | 2 Coal w or w/o TDF | Filterable Particulate | 0.035097 | lb/MMBtu | Part II | 0 | CAM 238-026 | 3 |  | 9.5637 | 288 | 0.33565
6113_4 | Gibson |  | 6113 | 4 | 4 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | UNIT4(10/7/09) | 3 |  | 9.4781 | 289 | 0.085303
6113_4 | Gibson |  | 6113 | 4 | 4 | Filterable Particulate | 0.01161 | lb/MMBtu | Part II | 0 | U4010606 | 2 |  | 9.4781 | 289 | 0.11004
6113_4 | Gibson |  | 6113 | 4 | 4 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | 0 | UNIT4(10/5/05) | 3 |  | 9.4781 | 289 | 0.23063
6113_4 | Gibson |  | 6113 | 4 | 4 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | UNIT4(10/4/07) | 3 |  | 9.4781 | 289 | 0.3033
2850_B002 | J M Stuart |  | 2850 | B002 | MS2W | Filterable Particulate | 0.0092333 | lb/MMBtu | Part II | 0 | U2PM2009 | 3 |  | 9.3098 | 290 | 0.08596
525_2 | Hayden |  | 525 | 2 | Unit 2 | Filterable Particulate | 0.0090426 | lb/MMBtu | ERT | No |  | 4 | 565 | 9.5158 | 291 | 0.086047
2549_68 | CR Huntley Generating Station |  | 2549 | 68 | 068 | Filterable Particulate | 0.0094333 | lb/MMBtu | Part II | 0 | Stack-PM-0609 | 3 |  | 9.1343 | 292 | 0.086167
6139_1 | Welsh |  | 6139 | 1 | WE-1 | Filterable Particulate | 0.0093454 | lb/MMBtu | ERT | No |  | 6 | 10040004 | 9.2401 | 293 | 0.086353
6139_1 | Welsh |  | 6139 | 1 | WE-1 | Filterable Particulate | 0.0121 | lb/MMBtu | Part II | 0 | May2008PM | 1 |  | 9.2401 | 293 | 0.11181
6139_1 | Welsh |  | 6139 | 1 | WE-1 | Filterable Particulate | 0.0136 | lb/MMBtu | Part II | 0 | Jan2008PM | 1 |  | 9.2401 | 293 | 0.12567
6139_1 | Welsh |  | 6139 | 1 | WE-1 | Filterable Particulate | 0.0322 | lb/MMBtu | Part II | 0 | Sept2007PM | 1 |  | 9.2401 | 293 | 0.29753
6085_14 | R.M. Schahfer |  | 6085 | 14 | R.M.0014 | Filterable Particulate | 0.008887 | lb/MMBtu | Part II | 0 | RMSG U#14 M5 09/15/2009 | 1 |  | 9.9359 | 294 | 0.0883
6085_14 | R.M. Schahfer |  | 6085 | 14 | R.M.0014 | Filterable Particulate | 0.01514 | lb/MMBtu | ERT | No |  | 6 | 2302 | 9.9359 | 294 | 0.15043
6085_14 | R.M. Schahfer |  | 6085 | 14 | R.M.0014 | Filterable Particulate | 0.031055 | lb/MMBtu | Part II | 0 | RMSGS U#14 M5 05/30/2007 | 1 |  | 9.9359 | 294 | 0.30856
6085_14 | R.M. Schahfer |  | 6085 | 14 | R.M.0014 | Filterable Particulate | 0.097245 | lb/MMBtu | Part II | 0 | RMSGS U#14 M5 03/01/2005 | 1 |  | 9.9359 | 294 | 0.96622
3297_WAT2 | Wateree |  | 3297 | WAT2 | WAT002 | Filterable Particulate | 0.0102 | lb/MMBtu | Part II | 0 | PM-0506-WAT2 | 1 |  | 8.6976 | 295 | 0.088716
3297_WAT2 | Wateree |  | 3297 | WAT2 | WAT002 | Filterable Particulate | 0.0116 | lb/MMBtu | Part II | 0 | PM-05/07-WAT2 | 1 |  | 8.6976 | 295 | 0.10089
3297_WAT2 | Wateree |  | 3297 | WAT2 | WAT002 | Filterable Particulate | 0.0129 | lb/MMBtu | Part II | 0 | PM-HCL-HF-HG-07/06-WAT2 | 1 |  | 8.6976 | 295 | 0.1122
3297_WAT2 | Wateree |  | 3297 | WAT2 | WAT002 | Filterable Particulate | 0.0237 | lb/MMBtu | Part II | 0 | PM-06/09-WAT2 | 1 |  | 8.6976 | 295 | 0.20613
3297_WAT2 | Wateree |  | 3297 | WAT2 | WAT002 | Filterable Particulate | 0.0286 | lb/MMBtu | Part II | 0 | PM-05/08-WAT2 | 1 |  | 8.6976 | 295 | 0.24875
3297_WAT2 | Wateree |  | 3297 | WAT2 | WAT002 | Filterable Particulate | 0.0488 | lb/MMBtu | Part II | 0 | PM-08/05-WAT2 | 1 |  | 8.6976 | 295 | 0.42444
1001_2 | Cayuga |  | 1001 | 2 | 2-2008-FGDIN | Filterable Particulate | 0.00925 | lb/MMBtu | Part II | 0 | UNIT2(9/1/09) | 4 |  | 9.6 | 296 | 0.0888
1740_2 | River Rouge Power Plant |  | 1740 | 2 | RR2-Config | Filterable Particulate | 0.010333 | lb/MMBtu | Part II | 0 | 2009Mar | 3 |  | 8.6134 | 297 | 0.089005
1740_2 | River Rouge Power Plant |  | 1740 | 2 | RR2-Config | Filterable Particulate | 0.0175 | lb/MMBtu | Part II | 0 | 2010Apr | 2 |  | 8.6134 | 297 | 0.15073
1740_2 | River Rouge Power Plant |  | 1740 | 2 | RR2-Config | Filterable Particulate | 0.0185 | lb/MMBtu | Part II | 0 | 2009Apr | 2 |  | 8.6134 | 297 | 0.15935
1740_2 | River Rouge Power Plant |  | 1740 | 2 | RR2-Config | Filterable Particulate | 0.038 | lb/MMBtu | Part II | 0 | PM2008_Sep2b | 3 |  | 8.6134 | 297 | 0.32731
1740_2 | River Rouge Power Plant |  | 1740 | 2 | RR2-Config | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | PM2008_Sep2a | 2 |  | 8.6134 | 297 | 0.5168
7790_1-1 | Bonanza Power Plant |  | 7790 | 1-1 | 1-1 | Filterable Particulate | 0.0088 | lb/MMBtu | Part II | 0 | Total particulate 2005 | 3 |  | 10.1429 | 298 | 0.089257
1745_9A | Trenton Channel Power Plant |  | 1745 | 9A | TC9A-Config | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | PM2008_Jun9c | 1 |  | 7.4907 | 299 | 0.089889
1745_9A | Trenton Channel Power Plant |  | 1745 | 9A | TC9A-Config | Filterable Particulate | 0.0175 | lb/MMBtu | Part II | 0 | PM2008_Jun9a | 2 |  | 7.4907 | 299 | 0.13109
1745_9A | Trenton Channel Power Plant |  | 1745 | 9A | TC9A-Config | Filterable Particulate | 0.019667 | lb/MMBtu | Part II | 0 | PM2008_Jun9b | 3 |  | 7.4907 | 299 | 0.14732
2094_3 | Sibley |  | 2094 | 3 | 3 | Filterable Particulate | 0.0091995 | lb/MMBtu | ERT | No |  | 3 | 894 | 9.7711 | 300 | 0.089889
991_6 | Eagle Valley |  | 991 | 6 | 6 | Filterable Particulate | 0.0094993 | lb/MMBtu | ERT | No |  | 6 | 1178 | 9.6857 | 301 | 0.092008
6082_1 | AES Somerset LLC |  | 6082 | 1 | 001 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | PM2_Aug_2006 | 1 |  | 9.2244 | 302 | 0.092244
6082_1 | AES Somerset LLC |  | 6082 | 1 | 001 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | PM_Aug_2006 | 1 |  | 9.2244 | 302 | 0.13837
10672_CBC | Cedar Bay Generating Company L.P. |  | 10672 | CBC | CBC1 | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | CBC2005pm | 3 |  | 11.5543 | 303 | 0.092435
10672_CBC | Cedar Bay Generating Company L.P. |  | 10672 | CBC | CBC1 | Filterable Particulate | 0.0096667 | lb/MMBtu | Part II | 0 | CBC2006pm | 3 |  | 11.5543 | 303 | 0.11169
10672_CBC | Cedar Bay Generating Company L.P. |  | 10672 | CBC | CBC1 | Filterable Particulate | 0.010667 | lb/MMBtu | Part II | 0 | CBC2007PM | 3 |  | 11.5543 | 303 | 0.12325
10672_CBC | Cedar Bay Generating Company L.P. |  | 10672 | CBC | CBC1 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | CBC2009pm | 1 |  | 11.5543 | 303 | 0.1271
10672_CBC | Cedar Bay Generating Company L.P. |  | 10672 | CBC | CBC1 | Filterable Particulate | 0.012777 | lb/MMBtu | ERT | No |  | 3 | 2200 | 11.5543 | 303 | 0.14763
10672_CBC | Cedar Bay Generating Company L.P. |  | 10672 | CBC | CBC1 | Filterable Particulate | 0.013333 | lb/MMBtu | Part II | 0 | CBC2008pm | 3 |  | 11.5543 | 303 | 0.15406
3948_2 | Mitchell |  | 3948 | 2 | MI-2 | Filterable Particulate | 0.0108 | lb/MMBtu | Part II | 0 | April2009PM2 | 1 |  | 8.5998 | 304 | 0.092878
8042_Unit 1 | Belews Creek Steam Station |  | 8042 | Unit 1 | 1-2008 | Filterable Particulate | 0.0103 | lb/MMBtu | Part II | 0 | UNIT1(2/10/09) | 3 |  | 9.1078 | 305 | 0.09381
8042_Unit 1 | Belews Creek Steam Station |  | 8042 | Unit 1 | 1-2008 | Filterable Particulate | 0.047833 | lb/MMBtu | Part II | 0 | UNIT1(2/5/08) | 3 |  | 9.1078 | 305 | 0.43566
3776_6 | Glen Lyn |  | 3776 | 6 | GL-6 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | Sept2007 | 1 |  | 8.5895 | 306 | 0.094484
2824_10 | Stanton |  | 2824 | 10 | u10 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | Particulate test | 1 |  | 10.7 | 307 | 0.0963
8222_B1 | Coyote |  | 8222 | B1 | 001 | Filterable Particulate | 0.0083333 | lb/MMBtu | Part II | 0 | Particulate Emissions Test | 3 |  | 11.6384 | 308 | 0.096987
3161_2 | Eddystone Generating Station |  | 3161 | 2 | Unit 2 | Filterable Particulate | 0.011767 | lb/MMBtu | Part II | 0 | Particulate Emissions Test - Unit 2 | 3 |  | 8.2832 | 309 | 0.097465
3161_2 | Eddystone Generating Station |  | 3161 | 2 | Unit 2 | Filterable Particulate | 0.011955 | lb/MMBtu | ERT | No |  | 6 | 1847 | 8.2832 | 309 | 0.099026
3936_2 | Kanawha River |  | 3936 | 2 | KR-2 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | March2009PM | 1 |  | 8.8798 | 310 | 0.097678
3936_2 | Kanawha River |  | 3936 | 2 | KR-2 | Filterable Particulate | 0.085 | lb/MMBtu | Part II | 0 | March2008PM | 1 |  | 8.8798 | 310 | 0.75478
3936_1 | Kanawha River |  | 3936 | 1 | KR-1 | Filterable Particulate | 0.011 | lb/MMBtu | Part II | 0 | March2009PM | 1 |  | 8.8798 | 311 | 0.097678
3936_1 | Kanawha River |  | 3936 | 1 | KR-1 | Filterable Particulate | 0.085 | lb/MMBtu | Part II | 0 | March2008PM | 1 |  | 8.8798 | 311 | 0.75478
50_1 | Widows Creek |  | 50 | 1 | 1 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | WCF1 - 2006 | 3 |  | 10.8677 | 312 | 0.097809
50_1 | Widows Creek |  | 50 | 1 | 1 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | WCF1 - 2005 | 3 |  | 10.8677 | 312 | 0.13041
50_1 | Widows Creek |  | 50 | 1 | 1 | Filterable Particulate | 0.017667 | lb/MMBtu | Part II | 0 | WCF1 - 2007 | 3 |  | 10.8677 | 312 | 0.192
50_1 | Widows Creek |  | 50 | 1 | 1 | Filterable Particulate | 0.052667 | lb/MMBtu | Part II | 0 | WCF1 - 2008 | 3 |  | 10.8677 | 312 | 0.57237
50776_BLR2 | PANTHER CREEK ENERGY FACILITY |  | 50776 | BLR2 | BG2 | Filterable Particulate | 0.0077674 | lb/MMBtu | ERT | No |  | 6 | 2090 | 12.9032 | 313 | 0.10022
50776_BLR2 | PANTHER CREEK ENERGY FACILITY |  | 50776 | BLR2 | BG2 | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | B2 PM 06/2009 | 3 |  | 12.9032 | 313 | 0.11613
50776_BLR2 | PANTHER CREEK ENERGY FACILITY |  | 50776 | BLR2 | BG2 | Filterable Particulate | 0.0205 | lb/MMBtu | Part II | 0 | B2 Hg 06/2008 | 2 |  | 12.9032 | 313 | 0.26452
50776_BLR1 | PANTHER CREEK ENERGY FACILITY |  | 50776 | BLR1 | BG1 | Filterable Particulate | 0.0077674 | lb/MMBtu | ERT | No |  | 6 | 2090 | 12.9032 | 314 | 0.10022
50776_BLR1 | PANTHER CREEK ENERGY FACILITY |  | 50776 | BLR1 | BG1 | Filterable Particulate | 0.012333 | lb/MMBtu | Part II | 0 | B1 PM 06/2009 | 3 |  | 12.9032 | 314 | 0.15914
50776_BLR1 | PANTHER CREEK ENERGY FACILITY |  | 50776 | BLR1 | BG1 | Filterable Particulate | 0.0135 | lb/MMBtu | Part II | 0 | B1 Hg 06/2008 | 2 |  | 12.9032 | 314 | 0.17419
6264_1 | Mountaineer |  | 6264 | 1 | Mt-1 | Filterable Particulate | 0.0111 | lb/MMBtu | Part II | 0 | July2009PM | 1 |  | 9.0606 | 315 | 0.10057
6264_1 | Mountaineer |  | 6264 | 1 | Mt-1 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | 0 | Oct2007PM | 1 |  | 9.0606 | 315 | 0.11054
50835_1 | TES Filer City Station |  | 50835 | 1 | TES1-Conf | Filterable Particulate | 0.008 | lb/MMBtu | Part II | 0 | 2007-Unit 1 PM | 2 |  | 12.6708 | 316 | 0.10137
4054_1 | Nelson Dewey |  | 4054 | 1 | Unit 1 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | ND1-PM-20090929 | 1 |  | 10.1833 | 317 | 0.10183
2094_1 | Sibley |  | 2094 | 1 | 1 | Filterable Particulate | 0.0091995 | lb/MMBtu | ERT | No |  | 3 | 894 | 11.0836 | 318 | 0.10196
1893_1 | Boswell Energy Center |  | 1893 | 1 | BEC1 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 1,2-Jul2009-PM | 2 |  | 10.274 | 319 | 0.10274
1893_2 | Boswell Energy Center |  | 1893 | 2 | BEC2 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 1,2-Jul2009-PM | 2 |  | 10.4167 | 320 | 0.10417
1893_2 | Boswell Energy Center |  | 1893 | 2 | BEC2 | Filterable Particulate | 0.01 | lb/MMBtu | Part II | 0 | 1,2,3,4-May2007-PM | 1 |  | 10.4167 | 320 | 0.10417
988_3 | Tanners Creek |  | 988 | 3 | TC-3 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | 0 | Aug2009PM | 1 |  | 8.5608 | 322 | 0.10444
6009_1 | White Bluff |  | 6009 | 1 | 001 | Filterable Particulate | 0.010333 | lb/MMBtu | Part II | 0 | 1 | 3 |  | 10.1993 | 323 | 0.10539
2324_3 | Reid Gardner |  | 2324 | 3 | 3 | Filterable Particulate | 0.0095933 | lb/MMBtu | Part II | 0 | U3_2009_COMPLIANCE | 3 |  | 11.1441 | 324 | 0.10691
2324_3 | Reid Gardner |  | 2324 | 3 | 3 | Filterable Particulate | 0.027333 | lb/MMBtu | Part II | 0 | U3_2009_BAGHOUSE_STACK | 3 |  | 11.1441 | 324 | 0.30461
2104_4 | Meramec |  | 2104 | 4 | 004 | Filterable Particulate | 0.0103 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 10.4475 | 325 | 0.10761
50835_2 | TES Filer City Station |  | 50835 | 2 | TES2-Conf | Filterable Particulate | 0.0085 | lb/MMBtu | Part II | 0 | 2007 -Unit 2 PM | 2 |  | 12.6708 | 326 | 0.1077
2872_5 | Muskingum River |  | 2872 | 5 | MR-5 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | Mar2006PM | 1 |  | 9.0215 | 327 | 0.10826
2872_5 | Muskingum River |  | 2872 | 5 | MR-5 | Filterable Particulate | 0.0269 | lb/MMBtu | Part II | 0 | July2009PM2 | 1 |  | 9.0215 | 327 | 0.24268
2872_5 | Muskingum River |  | 2872 | 5 | MR-5 | Filterable Particulate | 0.0537 | lb/MMBtu | Part II | 0 | July2009PM | 1 |  | 9.0215 | 327 | 0.48445
2872_5 | Muskingum River |  | 2872 | 5 | MR-5 | Filterable Particulate | 0.0566 | lb/MMBtu | Part II | 0 | Oct2006PM | 1 |  | 9.0215 | 327 | 0.51061
10678_BLR1 | AES Warrior Run Cogeneration Facility |  | 10678 | BLR1 | BLR1 | Filterable Particulate | 0.010695 | lb/MMBtu | ERT | No |  | 6 | 1539 | 10.1337 | 328 | 0.10838
8102_1 | General James M. Gavin |  | 8102 | 1 | GA-1 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 9.0424 | 329 | 0.10851
8102_1 | General James M. Gavin |  | 8102 | 1 | GA-1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | July2006PM | 1 |  | 9.0424 | 329 | 0.3617
3161_1 | Eddystone Generating Station |  | 3161 | 1 | Unit 1 | Filterable Particulate | 0.012933 | lb/MMBtu | Part II | 0 | Particulate Emissions Test - Unit 1 | 3 |  | 8.3981 | 330 | 0.10862
3938_51 | Philip Sporn |  | 3938 | 51 | SP-5 | Filterable Particulate | 0.0136 | lb/MMBtu | Part II | 0 | June2005PM | 1 |  | 7.9939 | 331 | 0.10872
3938_51 | Philip Sporn |  | 3938 | 51 | SP-5 | Filterable Particulate | 0.0234 | lb/MMBtu | Part II | 0 | Feb2009PM2 | 1 |  | 7.9939 | 331 | 0.18706
3938_51 | Philip Sporn |  | 3938 | 51 | SP-5 | Filterable Particulate | 0.0301 | lb/MMBtu | Part II | 0 | June2007PM2 | 1 |  | 7.9939 | 331 | 0.24062
54081_2B | Spruance Genco, LLC |  | 54081 | 2B | GEN2 | Filterable Particulate | 0.0084421 | lb/MMBtu | ERT | No |  | 3 | 13461 | 13.0662 | 332 | 0.11031
54081_2A | Spruance Genco, LLC |  | 54081 | 2A | GEN2 | Filterable Particulate | 0.0084421 | lb/MMBtu | ERT | No |  | 3 | 13461 | 13.0662 | 333 | 0.11031
54081_4B | Spruance Genco, LLC |  | 54081 | 4B | GEN4 | Filterable Particulate | 0.00845 | lb/MMBtu | Part II | 0 | 2006 Emissions Testing at Boilers 4A and 4B | 2 |  | 13.0662 | 334 | 0.11041
54081_4B | Spruance Genco, LLC |  | 54081 | 4B | GEN4 | Filterable Particulate | 0.027134 | lb/MMBtu | ERT | No |  | 3 | 1346111 | 13.0662 | 334 | 0.35454
54081_4A | Spruance Genco, LLC |  | 54081 | 4A | GEN4 | Filterable Particulate | 0.00845 | lb/MMBtu | Part II | 0 | 2006 Emissions Testing at Boilers 4A and 4B | 2 |  | 13.0662 | 335 | 0.11041
54081_4A | Spruance Genco, LLC |  | 54081 | 4A | GEN4 | Filterable Particulate | 0.027134 | lb/MMBtu | ERT | No |  | 3 | 1346111 | 13.0662 | 335 | 0.35454
988_2 | Tanners Creek |  | 988 | 2 | TC-2 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | 0 | Aug2009PM | 1 |  | 9.1213 | 336 | 0.11128
988_1 | Tanners Creek |  | 988 | 1 | TC-1 | Filterable Particulate | 0.0122 | lb/MMBtu | Part II | 0 | Aug2009PM | 1 |  | 9.1213 | 337 | 0.11128
2442_1 | Four Corners |  | 2442 | 1 | 001 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | 13 | 1 |  | 8.5814 | 338 | 0.11156
2442_1 | Four Corners |  | 2442 | 1 | 001 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | 7 | 1 |  | 8.5814 | 338 | 0.14588
2442_1 | Four Corners |  | 2442 | 1 | 001 | Filterable Particulate | 0.026 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 8.5814 | 338 | 0.22312
1393_6 | RS Nelson |  | 1393 | 6 | 001 | Filterable Particulate | 0.011306 | lb/MMBtu | ERT | No |  | 3 | 2103 | 9.9328 | 339 | 0.1123
50_4 | Widows Creek |  | 50 | 4 | 4 | Filterable Particulate | 0.010333 | lb/MMBtu | Part II | 0 | WCF4 - 2005 | 3 |  | 10.8677 | 340 | 0.1123
50_4 | Widows Creek |  | 50 | 4 | 4 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | WCF4 - 2006 | 3 |  | 10.8677 | 340 | 0.15215
50_4 | Widows Creek |  | 50 | 4 | 4 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | WCF4 - 2008 | 3 |  | 10.8677 | 340 | 0.15215
50_4 | Widows Creek |  | 50 | 4 | 4 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | WCF4 - 2007 | 3 |  | 10.8677 | 340 | 0.15939
2104_2 | Meramec |  | 2104 | 2 | 002 | Filterable Particulate | 0.0092 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 12.2344 | 341 | 0.11256
3992_7 | Blount Street |  | 3992 | 7 | 7B1345T | Filterable Particulate | 0.0081333 | lb/MMBtu | Part II | 0 | M074302 | 3 |  | 13.8393 | 342 | 0.11256
2094_2 | Sibley |  | 2094 | 2 | 2 | Filterable Particulate | 0.0091995 | lb/MMBtu | ERT | No |  | 3 | 894 | 12.3 | 343 | 0.11315
6249_3 | Winyah |  | 6249 | 3 | W3 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | W3PM2008 | 1 |  | 9.4328 | 344 | 0.11319
6249_3 | Winyah |  | 6249 | 3 | W3 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 0 | W3PM2009 | 1 |  | 9.4328 | 344 | 0.23582
6249_3 | Winyah |  | 6249 | 3 | W3 | Filterable Particulate | 0.042 | lb/MMBtu | Part II | 0 | W3PM2005 | 1 |  | 9.4328 | 344 | 0.39618
6249_3 | Winyah |  | 6249 | 3 | W3 | Filterable Particulate | 0.045 | lb/MMBtu | Part II | 0 | W3PM2006 | 1 |  | 9.4328 | 344 | 0.42448
6249_3 | Winyah |  | 6249 | 3 | W3 | Filterable Particulate | 0.058 | lb/MMBtu | Part II | 0 | W3PM2007 | 1 |  | 9.4328 | 344 | 0.5471
2840_4 | Conesville |  | 2840 | 4 | CV-4 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | Feb2010PM2 | 1 |  | 9.4593 | 345 | 0.11351
2840_4 | Conesville |  | 2840 | 4 | CV-4 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | Oct2009PM | 1 |  | 9.4593 | 345 | 0.16081
2832_Unit 7 | Miami Fort |  | 2832 | Unit 7 | U7 | Filterable Particulate | 0.0125 | lb/MMBtu | Part II | 0 | U7050108 | 4 |  | 9.0818 | 346 | 0.11352
2832_Unit 7 | Miami Fort |  | 2832 | Unit 7 | U7 | Filterable Particulate | 0.01425 | lb/MMBtu | Part II | 0 | U7050808 | 4 |  | 9.0818 | 346 | 0.12942
2832_Unit 7 | Miami Fort |  | 2832 | Unit 7 | U7 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 0 | U7052008 | 3 |  | 9.0818 | 346 | 0.15136
2832_Unit 7 | Miami Fort |  | 2832 | Unit 7 | U7 | Filterable Particulate | 0.0392 | lb/MMBtu | Part II | 0 | U7042908 | 5 |  | 9.0818 | 346 | 0.35601
727_3 | Mitchell |  | 727 | 3 | Unit 3 | Filterable Particulate | 0.022033 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (August 8, 2006) | 3 |  | 5.2134 | 347 | 0.11487
727_3 | Mitchell |  | 727 | 3 | Unit 3 | Filterable Particulate | 0.047627 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (August 6, 2008) | 3 |  | 5.2134 | 347 | 0.2483
3149_2 | PPL Montour |  | 3149 | 2 | U2 | Filterable Particulate | 0.0126 | lb/MMBtu | Part II | 0 | M2409 | 1 |  | 9.1402 | 348 | 0.11517
3149_2 | PPL Montour |  | 3149 | 2 | U2 | Filterable Particulate | 0.0165 | lb/MMBtu | Part II | 0 | M2408 | 1 |  | 9.1402 | 348 | 0.15081
3149_2 | PPL Montour |  | 3149 | 2 | U2 | Filterable Particulate | 0.016599 | lb/MMBtu | ERT | No |  | 6 | 1187 | 9.1402 | 348 | 0.15172
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.012171 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (May 21, 2008) | 3 |  | 9.4672 | 349 | 0.11522
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.016584 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (August 13, 2009) | 3 |  | 9.4672 | 349 | 0.15701
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.017297 | lb/MMBtu | Part II | 0 | Unit 2 Engineering Particulate Test (7/24/07) | 3 |  | 9.4672 | 349 | 0.16375
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.021043 | lb/MMBtu | Part II | 0 | Unit 2 Engineering Particulate Test (7/27/07) | 3 |  | 9.4672 | 349 | 0.19922
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.02336 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (May 22, 2007) | 3 |  | 9.4672 | 349 | 0.22116
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.031496 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (August 21, 2006) | 3 |  | 9.4672 | 349 | 0.29818
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.035345 | lb/MMBtu | Part II | 0 | Unit 2 Engineering Particulate Test Part 1 | 3 |  | 9.4672 | 349 | 0.33462
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.051039 | lb/MMBtu | Part II | 0 | Unit 2 Engineering Particulate Test Part 2 | 2 |  | 9.4672 | 349 | 0.48319
3_2 | Barry |  | 3 | 2 | Unit 2 | Filterable Particulate | 0.067267 | lb/MMBtu | Part II | 0 | Unit 2 CAM Test (August 22, 2006) | 3 |  | 9.4672 | 349 | 0.63683
6068_3 | Jeffrey Energy Center |  | 6068 | 3 | 3 | Filterable Particulate | 0.011567 | lb/MMBtu | Part II | 0 | PM 0707/3 | 3 |  | 9.9808 | 350 | 0.11545
6068_3 | Jeffrey Energy Center |  | 6068 | 3 | 3 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | 0 | PRECPERF 0709/3 | 3 |  | 9.9808 | 350 | 0.24287
6068_3 | Jeffrey Energy Center |  | 6068 | 3 | 3 | Filterable Particulate | 0.025833 | lb/MMBtu | Part II | 0 | CAM 0609/3 | 18 |  | 9.9808 | 350 | 0.25784
6068_3 | Jeffrey Energy Center |  | 6068 | 3 | 3 | Filterable Particulate | 0.026389 | lb/MMBtu | Part II | 0 | CAM 0406/3 | 9 |  | 9.9808 | 350 | 0.26338
1702_2 | D.E. Karn |  | 1702 | 2 | DEK2-Conf | Filterable Particulate | 0.012667 | lb/MMBtu | Part II | 0 | DEK2 - 2008 PM Testing | 3 |  | 9.2064 | 351 | 0.11661
1702_2 | D.E. Karn |  | 1702 | 2 | DEK2-Conf | Filterable Particulate | 0.042333 | lb/MMBtu | Part II | 0 | 2005 DEK2-PM Testing | 3 |  | 9.2064 | 351 | 0.38974
3_3 | Barry |  | 3 | 3 | Unit 3 | Filterable Particulate | 0.012667 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (May 22, 2008) | 3 |  | 9.2565 | 352 | 0.11725
3_3 | Barry |  | 3 | 3 | Unit 3 | Filterable Particulate | 0.017333 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (July 16, 2009) | 3 |  | 9.2565 | 352 | 0.16045
3_3 | Barry |  | 3 | 3 | Unit 3 | Filterable Particulate | 0.017733 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (July 25, 2006) | 3 |  | 9.2565 | 352 | 0.16415
3_3 | Barry |  | 3 | 3 | Unit 3 | Filterable Particulate | 0.033867 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (May 23, 2007) | 3 |  | 9.2565 | 352 | 0.31349
3_3 | Barry |  | 3 | 3 | Unit 3 | Filterable Particulate | 0.085633 | lb/MMBtu | Part II | 0 | Unit 3 CAM Test (July 26, 2006) | 3 |  | 9.2565 | 352 | 0.79267
2828_2 | Cardinal |  | 2828 | 2 | CD-U2 | Filterable Particulate | 0.0138 | lb/MMBtu | Part II | 0 | June2009PM2 | 1 |  | 8.5744 | 353 | 0.11833
1897_4 | Hibbard Energy Center |  | 1897 | 4 | HREC4 | Filterable Particulate | 0.00905 | lb/MMBtu | Part II | 0 | PM_CO-Boiler4 | 4 |  | 13.0833 | 354 | 0.1184
26_4 | E. C. Gaston |  | 26 | 4 | Unit 4 | Filterable Particulate | 0.013022 | lb/MMBtu | Part II | 0 | Report 4 | 3 |  | 9.142 | 355 | 0.11905
26_4 | E. C. Gaston |  | 26 | 4 | Unit 4 | Filterable Particulate | 0.018267 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (February 9, 2006) | 3 |  | 9.142 | 355 | 0.16699
26_4 | E. C. Gaston |  | 26 | 4 | Unit 4 | Filterable Particulate | 0.050333 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (May 29, 2008) | 3 |  | 9.142 | 355 | 0.46015
26_4 | E. C. Gaston |  | 26 | 4 | Unit 4 | Filterable Particulate | 0.052867 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (April 18, 2007) | 3 |  | 9.142 | 355 | 0.48331
26_4 | E. C. Gaston |  | 26 | 4 | Unit 4 | Filterable Particulate | 0.063 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (July 8, 2009) | 3 |  | 9.142 | 355 | 0.57595
26_4 | E. C. Gaston |  | 26 | 4 | Unit 4 | Filterable Particulate | 0.09615 | lb/MMBtu | Part II | 0 | Unit 4 CAM Test (February 10, 2006) | 4 |  | 9.142 | 355 | 0.87901
733_1 | Kraft |  | 733 | 1 | Unit 1 | Filterable Particulate | 0.01089 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (September 27, 2007) | 3 |  | 10.9507 | 356 | 0.11925
733_1 | Kraft |  | 733 | 1 | Unit 1 | Filterable Particulate | 0.019798 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (September 20, 2005) | 3 |  | 10.9507 | 356 | 0.2168
733_1 | Kraft |  | 733 | 1 | Unit 1 | Filterable Particulate | 0.026218 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (September 9, 2009) | 3 |  | 10.9507 | 356 | 0.2871
6085_17 | R.M. Schahfer |  | 6085 | 17 | R.M.0017 | Filterable Particulate | 0.011848 | lb/MMBtu | Part II | 0 | RMSGS U#17 M5 04/21/2009 | 1 |  | 10.0941 | 357 | 0.11959
6085_17 | R.M. Schahfer |  | 6085 | 17 | R.M.0017 | Filterable Particulate | 0.022107 | lb/MMBtu | Part II | 0 | RMSGS U#17 M5b 04/12/2005 | 1 |  | 10.0941 | 357 | 0.22316
6085_17 | R.M. Schahfer |  | 6085 | 17 | R.M.0017 | Filterable Particulate | 0.026815 | lb/MMBtu | Part II | 0 | RMSGS U#17 M5b 04/24/2007 | 1 |  | 10.0941 | 357 | 0.27068
2876_4 | Kyger Creek |  | 2876 | 4 | Unit 4 | Filterable Particulate | 0.0119 | lb/MMBtu | Part II | 0 | Unit4Particulate2005 | 1 |  | 10.1348 | 358 | 0.1206
2876_4 | Kyger Creek |  | 2876 | 4 | Unit 4 | Filterable Particulate | 0.0202 | lb/MMBtu | Part II | 0 | Unit4Particulate2007 | 1 |  | 10.1348 | 358 | 0.20472
3393_1 | Allen Steam Plant |  | 3393 | 1 | 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | ALF1 - 2008 | 3 |  | 9.2848 | 359 | 0.1207
3393_1 | Allen Steam Plant |  | 3393 | 1 | 1 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | ALF1 - 2006 | 3 |  | 9.2848 | 359 | 0.32497
1374_1374-2 | Elmer Smith Station |  | 1374 | 1374-2 | Unit001 | Filterable Particulate | 0.014672 | lb/MMBtu | ERT | No |  | 6 | 1330 | 8.2947 | 360 | 0.1217
1374_1374 | Elmer Smith Station |  | 1374 | 1374 | Unit001 | Filterable Particulate | 0.014672 | lb/MMBtu | ERT | No |  | 6 | 1330 | 8.2947 | 361 | 0.1217
10774_2 | Southampton Power Station |  | 10774 | 2 | Unit 1 & 2 | Filterable Particulate | 0.0093337 | lb/MMBtu | ERT | No |  | 3 | 1524 | 13.0735 | 362 | 0.12202
10774_1 | Southampton Power Station |  | 10774 | 1 | Unit 1 & 2 | Filterable Particulate | 0.0093337 | lb/MMBtu | ERT | No |  | 3 | 1524 | 13.0735 | 363 | 0.12202
728_Y7BR | Yates |  | 728 | Y7BR | Y7BR | Filterable Particulate | 0.012828 | lb/MMBtu | Part II | 0 | Unit 7 PM Emissions Test (April 27, 2005) | 3 |  | 9.523 | 364 | 0.12216
728_Y7BR | Yates |  | 728 | Y7BR | Y7BR | Filterable Particulate | 0.029006 | lb/MMBtu | Part II | 0 | Unit 7 PM Emissions Test (February 28, 2007) | 3 |  | 9.523 | 364 | 0.27623
728_Y7BR | Yates |  | 728 | Y7BR | Y7BR | Filterable Particulate | 0.045877 | lb/MMBtu | Part II | 0 | Unit 7 PM Emissions Test (February 24, 2009) | 3 |  | 9.523 | 364 | 0.43688
2324_2 | Reid Gardner |  | 2324 | 2 | 2 | Filterable Particulate | 0.011267 | lb/MMBtu | Part II | 0 | U2_2009_COMPLIANCE | 3 |  | 10.9459 | 365 | 0.12332
1382_H1 | HMP&L Station Two Henderson |  | 1382 | H1 | 1 | Filterable Particulate | 0.011467 | lb/MMBtu | Part II | 0 | H1 compliance 2007 | 3 |  | 10.8308 | 366 | 0.12419
3140_3 | PPL Brunner Island |  | 3140 | 3 | U3 | Filterable Particulate | 0.0134 | lb/MMBtu | Part II | 0 | B3509 | 1 |  | 9.2808 | 367 | 0.12436
2952_6 | Muskogee |  | 2952 | 6 | MK6 Config | Filterable Particulate | 0.009 | lb/MMBtu | Part II | 0 | Stack Sampling Report\ Muskogee 6 | 1 |  | 14.0563 | 368 | 0.12651
898_Unit 5 | Wood River |  | 898 | Unit 5 | 5 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | 15 | 1 |  | 10.5448 | 369 | 0.12654
3131_4 | Shawville |  | 3131 | 4 | SHAW4-2 | Filterable Particulate | 0.013283 | lb/MMBtu | ERT | No |  | 9 | 1471 | 9.5426 | 370 | 0.12675
3131_4 | Shawville |  | 3131 | 4 | SHAW4-2 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | SH-184 U3-4 | 3 |  | 9.5426 | 370 | 0.20994
3131_3 | Shawville |  | 3131 | 3 | SHAW3-2 | Filterable Particulate | 0.013283 | lb/MMBtu | ERT | No |  | 9 | 1471 | 9.5426 | 371 | 0.12675
3131_3 | Shawville |  | 3131 | 3 | SHAW3-2 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | SH-184 U3-4 | 3 |  | 9.5426 | 371 | 0.20994
3159_1 | Cromby Generating Station |  | 3159 | 1 | Unit 1 | Filterable Particulate | 0.013433 | lb/MMBtu | Part II | 0 | 6/16/09 PM/PM2.5 | 3 |  | 9.5466 | 372 | 0.12824
6085_18 | R.M. Schahfer |  | 6085 | 18 | R.M.0018 | Filterable Particulate | 0.013022 | lb/MMBtu | Part II | 0 | RMSGS U#18 M5b 05/02/2006 | 1 |  | 10.0941 | 373 | 0.13144
6085_18 | R.M. Schahfer |  | 6085 | 18 | R.M.0018 | Filterable Particulate | 0.01552 | lb/MMBtu | Part II | 0 | RMSGS U#18 M5b 06/12/2008 | 1 |  | 10.0941 | 373 | 0.15666
6085_18 | R.M. Schahfer |  | 6085 | 18 | R.M.0018 | Filterable Particulate | 0.025599 | lb/MMBtu | Part II | 0 | RMSGS U#18 M5b 06/16/09 | 1 |  | 10.0941 | 373 | 0.2584
6085_18 | R.M. Schahfer |  | 6085 | 18 | R.M.0018 | Filterable Particulate | 0.035716 | lb/MMBtu | Part II | 0 | RMSGS U#18 M5b 05/28/2008 | 1 |  | 10.0941 | 373 | 0.36053
6085_18 | R.M. Schahfer |  | 6085 | 18 | R.M.0018 | Filterable Particulate | 0.065123 | lb/MMBtu | Part II | 0 | RMSGS U#18 M5b 05/05/2009 | 1 |  | 10.0941 | 373 | 0.65736
645_1 | Big Bend |  | 645 | 1 | BB01_pre-SCR | Filterable Particulate | 0.013489 | lb/MMBtu | Part II | 0 | BB#1_FY2007 | 1 |  | 9.8463 | 374 | 0.13281
645_1 | Big Bend |  | 645 | 1 | BB01_pre-SCR | Filterable Particulate | 0.01429 | lb/MMBtu | Part II | 0 | BB#1_FY2009 | 1 |  | 9.8463 | 374 | 0.1407
645_1 | Big Bend |  | 645 | 1 | BB01_pre-SCR | Filterable Particulate | 0.024524 | lb/MMBtu | Part II | 0 | BB#1_FY2008 | 1 |  | 9.8463 | 374 | 0.24147
4259_1 | Endicott Station |  | 4259 | 1 | 1 | Filterable Particulate | 0.013 | lb/MMBtu | Part II | 0 | PM 7/1/2008 | 3 |  | 10.2833 | 375 | 0.13368
4259_1 | Endicott Station |  | 4259 | 1 | 1 | Filterable Particulate | 0.034667 | lb/MMBtu | Part II | 0 | PM 8/17/2006 | 3 |  | 10.2833 | 375 | 0.35649
4259_1 | Endicott Station |  | 4259 | 1 | 1 | Filterable Particulate | 0.10267 | lb/MMBtu | Part II | 0 | PM 10/26/2006 | 3 |  | 10.2833 | 375 | 1.0558
3935_1 | John E. Amos |  | 3935 | 1 | AM-1 | Filterable Particulate | 0.0156 | lb/MMBtu | Part II | 0 | CS012 | 1 |  | 8.5998 | 376 | 0.13416
3935_1 | John E. Amos |  | 3935 | 1 | AM-1 | Filterable Particulate | 0.02506 | lb/MMBtu | Part II | 0 | CS012 Stack | 1 |  | 8.5998 | 376 | 0.21551
8102_2 | General James M. Gavin |  | 8102 | 2 | GA-2 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | Feb2009PM2 | 1 |  | 9.0424 | 377 | 0.13564
8102_2 | General James M. Gavin |  | 8102 | 2 | GA-2 | Filterable Particulate | 0.023 | lb/MMBtu | Part II | 0 | June2006PM | 1 |  | 9.0424 | 377 | 0.20798
56_2 | Charles R. Lowman |  | 56 | 2 | 2 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | 2009 PM Test - 2 | 1 |  | 9.6899 | 378 | 0.13566
56_2 | Charles R. Lowman |  | 56 | 2 | 2 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | 2008 PM test - 2 | 1 |  | 9.6899 | 378 | 0.31977
1363_5 | Cane Run |  | 1363 | 5 | CR5 | Filterable Particulate | 0.011257 | lb/MMBtu | ERT | No |  | 3 | 18261 | 12.0552 | 379 | 0.13571
1363_5 | Cane Run |  | 1363 | 5 | CR5 | Filterable Particulate | 0.031 | lb/MMBtu | Part II | 0 | CR5-PM-2005 | 1 |  | 12.0552 | 379 | 0.37371
1363_5 | Cane Run |  | 1363 | 5 | CR5 | Filterable Particulate | 0.034 | lb/MMBtu | Part II | 0 | CR5-PM-2009 | 1 |  | 12.0552 | 379 | 0.40988
1363_5 | Cane Run |  | 1363 | 5 | CR5 | Filterable Particulate | 0.039 | lb/MMBtu | Part II | 0 | CR5-PM-2006 | 1 |  | 12.0552 | 379 | 0.47015
1363_5 | Cane Run |  | 1363 | 5 | CR5 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | CR5-PM-2008 | 1 |  | 12.0552 | 379 | 0.48221
1363_5 | Cane Run |  | 1363 | 5 | CR5 | Filterable Particulate | 0.049 | lb/MMBtu | Part II | 0 | CR5-PM-2007 | 1 |  | 12.0552 | 379 | 0.59071
1356_4 | Ghent |  | 1356 | 4 | GH4 | Filterable Particulate | 0.012 | lb/MMBtu | Part II | 0 | GH4-PM-2008 | 1 |  | 11.3657 | 380 | 0.13639
1356_4 | Ghent |  | 1356 | 4 | GH4 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | 0 | GH4-PM-2009 | 1 |  | 11.3657 | 380 | 0.31824
6139_3 | Welsh |  | 6139 | 3 | WE-3 | Filterable Particulate | 0.0148 | lb/MMBtu | Part II | 0 | May2008PM | 1 |  | 9.2401 | 381 | 0.13675
6139_3 | Welsh |  | 6139 | 3 | WE-3 | Filterable Particulate | 0.0206 | lb/MMBtu | Part II | 0 | Jan2008PM | 1 |  | 9.2401 | 381 | 0.19035
6139_3 | Welsh |  | 6139 | 3 | WE-3 | Filterable Particulate | 0.0217 | lb/MMBtu | Part II | 0 | Sept2007PM | 1 |  | 9.2401 | 381 | 0.20051
7030_U2 | Twin Oaks Power One |  | 7030 | U2 | U2 | Filterable Particulate | 0.013838 | lb/MMBtu | ERT | No |  | 6 | 941 | 9.9826 | 382 | 0.13814
2442_2 | Four Corners |  | 2442 | 2 | 002 | Filterable Particulate | 0.016 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 8.6685 | 383 | 0.1387
2442_2 | Four Corners |  | 2442 | 2 | 002 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | 14 | 1 |  | 8.6685 | 383 | 0.15603
2442_2 | Four Corners |  | 2442 | 2 | 002 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | 8 | 1 |  | 8.6685 | 383 | 0.19071
3393_3 | Allen Steam Plant |  | 3393 | 3 | 3 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | ALF3 - 2008 | 3 |  | 9.2848 | 384 | 0.13927
3393_3 | Allen Steam Plant |  | 3393 | 3 | 3 | Filterable Particulate | 0.019333 | lb/MMBtu | Part II | 0 | ALF3 - 2006 | 3 |  | 9.2848 | 384 | 0.17951
2963_3314 | Northeastern |  | 2963 | 3314 | NE-4 | Filterable Particulate | 0.0143 | lb/MMBtu | Part II | 0 | June2006PM | 1 |  | 9.7449 | 385 | 0.13935
2963_3314 | Northeastern |  | 2963 | 3314 | NE-4 | Filterable Particulate | 0.0224 | lb/MMBtu | Part II | 0 | May2006PM | 1 |  | 9.7449 | 385 | 0.21829
2963_3313 | Northeastern |  | 2963 | 3313 | NE-3 | Filterable Particulate | 0.0143 | lb/MMBtu | Part II | 0 | June2006PM | 1 |  | 9.7449 | 386 | 0.13935
2963_3313 | Northeastern |  | 2963 | 3313 | NE-3 | Filterable Particulate | 0.0224 | lb/MMBtu | Part II | 0 | May2006PM | 1 |  | 9.7449 | 386 | 0.21829
994_4 | AES Petersburg |  | 994 | 4 | 4s | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | Unit 4 - PM 08/2009 | 3 |  | 9.5034 | 387 | 0.13938
994_4 | AES Petersburg |  | 994 | 4 | 4s | Filterable Particulate | 0.024667 | lb/MMBtu | Part II | 0 | Unit 4 - PM 07/2005 | 3 |  | 9.5034 | 387 | 0.23442
994_4 | AES Petersburg |  | 994 | 4 | 4s | Filterable Particulate | 0.044333 | lb/MMBtu | Part II | 0 | Unit 4 - PM 07/2007 | 3 |  | 9.5034 | 387 | 0.42132
645_3 | Big Bend |  | 645 | 3 | BB03_SCR_iso | Filterable Particulate | 0.013609 | lb/MMBtu | Part II | 0 | BB#3_FY2009 | 1 |  | 10.2875 | 388 | 0.14
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.012233 | lb/MMBtu | Part II | 0 | 2006 H-1 retest | 3 |  | 11.4528 | 389 | 0.14011
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.0225 | lb/MMBtu | Part II | 0 | 2009 H-1 | 3 |  | 11.4528 | 389 | 0.25769
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.024667 | lb/MMBtu | Part II | 0 | 2007 H-1 | 3 |  | 11.4528 | 389 | 0.2825
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.031 | lb/MMBtu | Part II | 0 | 2005 H-1 | 3 |  | 11.4528 | 389 | 0.35504
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.049667 | lb/MMBtu | Part II | 0 | 2007 H-1 Hg | 3 |  | 11.4528 | 389 | 0.56882
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.071967 | lb/MMBtu | Part II | 0 | 2008 H-1 | 3 |  | 11.4528 | 389 | 0.82422
2848_H-1 | O H Hutchings |  | 2848 | H-1 | H-1 | Filterable Particulate | 0.11133 | lb/MMBtu | Part II | 0 | 2006 H-1 | 3 |  | 11.4528 | 389 | 1.2751
3944_3 | Harrison Power Station |  | 3944 | 3 | Boiler3 | Filterable Particulate | 0.016667 | lb/MMBtu | Part II | 0 | 10 | 3 |  | 8.4913 | 390 | 0.14152
3944_3 | Harrison Power Station |  | 3944 | 3 | Boiler3 | Filterable Particulate | 0.019833 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 8.4913 | 390 | 0.16841
3944_3 | Harrison Power Station |  | 3944 | 3 | Boiler3 | Filterable Particulate | 0.034333 | lb/MMBtu | Part II | 0 | 6 | 3 |  | 8.4913 | 390 | 0.29154
54081_1B | Spruance Genco, LLC |  | 54081 | 1B | GEN1 | Filterable Particulate | 0.01085 | lb/MMBtu | ERT | No |  | 3 | 1346 | 13.0662 | 391 | 0.14177
54081_1A | Spruance Genco, LLC |  | 54081 | 1A | GEN1 | Filterable Particulate | 0.01085 | lb/MMBtu | ERT | No |  | 3 | 1346 | 13.0662 | 392 | 0.14177
3113_1 | Portland |  | 3113 | 1 | POR-1 | Filterable Particulate | 0.0142 | lb/MMBtu | Part II | 0 | P-92-U1 | 3 |  | 9.9942 | 393 | 0.14192
728_Y6BR | Yates |  | 728 | Y6BR | Y6BR | Filterable Particulate | 0.014795 | lb/MMBtu | Part II | 0 | Unit 6 PM Emissions Test (February 28, 2007) | 3 |  | 9.6223 | 394 | 0.14236
728_Y6BR | Yates |  | 728 | Y6BR | Y6BR | Filterable Particulate | 0.014893 | lb/MMBtu | Part II | 0 | Unit 6 PM Emissions Test (April 27, 2005) | 3 |  | 9.6223 | 394 | 0.1433
728_Y6BR | Yates |  | 728 | Y6BR | Y6BR | Filterable Particulate | 0.024491 | lb/MMBtu | Part II | 0 | Unit 6 PM Emissions Test (February 24, 2009) | 3 |  | 9.6223 | 394 | 0.23566
728_Y6BR | Yates |  | 728 | Y6BR | Y6BR | Filterable Particulate | 0.067467 | lb/MMBtu | Part II | 0 | Unit 6 Sorbent Injection Mercury Study | 6 |  | 9.6223 | 394 | 0.64918
2718_ES-2 | G G Allen |  | 2718 | ES-2 | 2-2009 | Filterable Particulate | 0.016933 | lb/MMBtu | Part II | 0 | CS125(4/23/09) | 3 |  | 8.5254 | 395 | 0.14436
2535_1 | AES Cayuga, LLC |  | 2535 | 1 | Unit_1 | Filterable Particulate | 0.0162 | lb/MMBtu | Part II | 0 | 9_902519TSP_a | 1 |  | 8.9146 | 396 | 0.14442
2535_1 | AES Cayuga, LLC |  | 2535 | 1 | Unit_1 | Filterable Particulate | 0.0376 | lb/MMBtu | Part II | 0 | 1_902306_a | 1 |  | 8.9146 | 396 | 0.33519
10603_031 | Ebensburg Power Company |  | 10603 | 031 | EPC01 | Filterable Particulate | 0.010167 | lb/MMBtu | Part II | 0 | 2005 Emissions | 6 |  | 14.3103 | 397 | 0.14549
10603_031 | Ebensburg Power Company |  | 10603 | 031 | EPC01 | Filterable Particulate | 0.024684 | lb/MMBtu | ERT | No |  | 6 | 1893 | 14.3103 | 397 | 0.35324
6641_1 | Independence |  | 6641 | 1 | 001 | Filterable Particulate | 0.014333 | lb/MMBtu | Part II | 0 | 1 | 3 |  | 10.1993 | 398 | 0.14619
55076_AA-002 | Red Hills Generating Facility |  | 55076 | AA-002 | 002 | Filterable Particulate | 0.015443 | lb/MMBtu | ERT | No |  | 3 | 1060 | 9.5292 | 399 | 0.14716
2828_3 | Cardinal |  | 2828 | 3 | CD-U3 | Filterable Particulate | 0.018161 | lb/MMBtu | ERT | No |  | 6 | 1004 | 8.1154 | 400 | 0.14738
2828_3 | Cardinal |  | 2828 | 3 | CD-U3 | Filterable Particulate | 0.0321 | lb/MMBtu | Part II | 0 | June2009PM3 | 1 |  | 8.1154 | 400 | 0.2605
2828_3 | Cardinal |  | 2828 | 3 | CD-U3 | Filterable Particulate | 0.0469 | lb/MMBtu | Part II | 0 | July2007PM3 | 1 |  | 8.1154 | 400 | 0.38061
55076_AA-001 | Red Hills Generating Facility |  | 55076 | AA-001 | 001 | Filterable Particulate | 0.015443 | lb/MMBtu | ERT | No |  | 3 | 1058 | 9.604 | 401 | 0.14831
2832_Unit 8 | Miami Fort |  | 2832 | Unit 8 | U8 | Filterable Particulate | 0.016333 | lb/MMBtu | Part II | 0 | U8082907 | 3 |  | 9.0964 | 402 | 0.14857
3152_4 | Sunbury Generation LP |  | 3152 | 4 | Boiler 4 | Filterable Particulate | 0.014 | lb/MMBtu | ERT | No |  | 6 | 2306 | 10.625 | 403 | 0.14875
6768_1 | Sikeston Power Station |  | 6768 | 1 | 1 | Filterable Particulate | 0.012533 | lb/MMBtu | Part II | 0 | 2007 CPM | 3 |  | 11.9313 | 404 | 0.14954
6768_1 | Sikeston Power Station |  | 6768 | 1 | 1 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | 081029 | 3 |  | 11.9313 | 404 | 0.3818
3407_9 | Kingston |  | 3407 | 9 | 9 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | KIF6-9 - 2007 | 3 |  | 10.28 | 405 | 0.15077
3407_9 | Kingston |  | 3407 | 9 | 9 | Filterable Particulate | 0.023 | lb/MMBtu | Part II | 0 | KIF9 - 2009 | 3 |  | 10.28 | 405 | 0.23644
3407_8 | Kingston |  | 3407 | 8 | 8 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | KIF6-9 - 2007 | 3 |  | 10.28 | 406 | 0.15077
3407_8 | Kingston |  | 3407 | 8 | 8 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | KIF6-9 - 2005 | 3 |  | 10.28 | 406 | 0.15763
3407_7 | Kingston |  | 3407 | 7 | 7 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | KIF6-9 - 2007 | 3 |  | 10.28 | 407 | 0.15077
3407_7 | Kingston |  | 3407 | 7 | 7 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | KIF6-9 - 2005 | 3 |  | 10.28 | 407 | 0.15763
3407_6 | Kingston |  | 3407 | 6 | 6 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | KIF6-9 - 2007 | 3 |  | 10.28 | 408 | 0.15077
3407_6 | Kingston |  | 3407 | 6 | 6 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | KIF6-9 - 2005 | 3 |  | 10.28 | 408 | 0.15763
2828_1 | Cardinal |  | 2828 | 1 | CD-U1 | Filterable Particulate | 0.0176 | lb/MMBtu | Part II | 0 | June2009PM | 1 |  | 8.5744 | 409 | 0.15091
2917_9 | Hamilton |  | 2917 | 9 | Unit 9 | Filterable Particulate | 0.0105 | lb/MMBtu | Part II | 0 | U9-Particulate | 6 |  | 14.4071 | 410 | 0.15127
6085_15 | R.M. Schahfer |  | 6085 | 15 | R.M.0015 | Filterable Particulate | 0.014908 | lb/MMBtu | Part II | 0 | RMSGS U#15 M5 04/04/2006 | 1 |  | 10.1594 | 411 | 0.15145
6085_15 | R.M. Schahfer |  | 6085 | 15 | R.M.0015 | Filterable Particulate | 0.028472 | lb/MMBtu | Part II | 0 | RMSGS U#15 M5 04/29/2008 | 1 |  | 10.1594 | 411 | 0.28926
136_1 | Seminole Generating Station |  | 136 | 1 | Unit 1 | Filterable Particulate | 0.014667 | lb/MMBtu | Part II | 0 | Multi-Pollutant Test Report 2009 (Unit 1) | 3 |  | 10.3343 | 412 | 0.15157
1385_3 | Dale Station |  | 1385 | 3 | 03 | Filterable Particulate | 0.012871 | lb/MMBtu | ERT | No |  | 3 | 993 | 11.8 | 413 | 0.15188
990_60 | Harding Street |  | 990 | 60 | 60s | Filterable Particulate | 0.016765 | lb/MMBtu | ERT | No |  | 6 | 632 | 9.0804 | 414 | 0.15223
3406_9 | Johnsonville |  | 3406 | 9 | 9 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 10.0347 | 415 | 0.15387
3406_9 | Johnsonville |  | 3406 | 9 | 9 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 10.0347 | 415 | 0.25421
3406_9 | Johnsonville |  | 3406 | 9 | 9 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 10.0347 | 415 | 0.41142
3406_8 | Johnsonville |  | 3406 | 8 | 8 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 10.0347 | 416 | 0.15387
3406_8 | Johnsonville |  | 3406 | 8 | 8 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 10.0347 | 416 | 0.25421
3406_8 | Johnsonville |  | 3406 | 8 | 8 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 10.0347 | 416 | 0.41142
3406_7 | Johnsonville |  | 3406 | 7 | 7 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 10.0347 | 417 | 0.15387
3406_7 | Johnsonville |  | 3406 | 7 | 7 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 10.0347 | 417 | 0.25421
3406_7 | Johnsonville |  | 3406 | 7 | 7 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 10.0347 | 417 | 0.41142
3406_10 | Johnsonville |  | 3406 | 10 | 10 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 10.0347 | 418 | 0.15387
3406_10 | Johnsonville |  | 3406 | 10 | 10 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 10.0347 | 418 | 0.25421
3406_10 | Johnsonville |  | 3406 | 10 | 10 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 10.0347 | 418 | 0.41142
2442_3 | Four Corners |  | 2442 | 3 | 003 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | 15 | 1 |  | 8.5531 | 419 | 0.15396
2442_3 | Four Corners |  | 2442 | 3 | 003 | Filterable Particulate | 0.023 | lb/MMBtu | Part II | 0 | 9 | 1 |  | 8.5531 | 419 | 0.19672
2442_3 | Four Corners |  | 2442 | 3 | 003 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | 10 | 1 |  | 8.5531 | 419 | 0.25659
2442_3 | Four Corners |  | 2442 | 3 | 003 | Filterable Particulate | 0.031 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 8.5531 | 419 | 0.26515
2442_3 | Four Corners |  | 2442 | 3 | 003 | Filterable Particulate | 0.178 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 8.5531 | 419 | 1.5225
6823_W1 | D B Wilson |  | 6823 | W1 | 1 | Filterable Particulate | 0.0153 | lb/MMBtu | Part II | 0 | W1 Compliance 2008 | 3 |  | 10.1061 | 420 | 0.15462
10143_AAB01 | Colver Power Project |  | 10143 | AAB01 | AAB01 | Filterable Particulate | 0.016939 | lb/MMBtu | ERT | No |  | 6 | 1293 | 9.1908 | 421 | 0.15569
10143_AAB01 | Colver Power Project |  | 10143 | AAB01 | AAB01 | Filterable Particulate | 0.021667 | lb/MMBtu | Part II | 0 | PM Emissions 5-2009 | 3 |  | 9.1908 | 421 | 0.19913
733_3 | Kraft |  | 733 | 3 | Unit 3 | Filterable Particulate | 0.016107 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (September 21, 2006) | 3 |  | 9.8349 | 422 | 0.15841
733_3 | Kraft |  | 733 | 3 | Unit 3 | Filterable Particulate | 0.082996 | lb/MMBtu | Part II | 0 | Unit 3 PM Emissions Test (August 28, 2008) | 3 |  | 9.8349 | 422 | 0.81626
2535_2 | AES Cayuga, LLC |  | 2535 | 2 | Unit_2 | Filterable Particulate | 0.0185 | lb/MMBtu | Part II | 0 | 2_902306_b | 1 |  | 8.631 | 423 | 0.15967
2535_2 | AES Cayuga, LLC |  | 2535 | 2 | Unit_2 | Filterable Particulate | 0.0214 | lb/MMBtu | Part II | 0 | 10_902519TSP_b | 1 |  | 8.631 | 423 | 0.1847
2535_2 | AES Cayuga, LLC |  | 2535 | 2 | Unit_2 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | 4_902426TSP_b | 1 |  | 8.631 | 423 | 0.27619
1831_EUBoiler5 | Otto E. Eckert Station |  | 1831 | EUBoiler5 | 005 | Filterable Particulate | 0.014067 | lb/MMBtu | Part II | 0 | PM-5-9/05 | 3 |  | 11.3662 | 424 | 0.15988
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_6 | 3 |  | 8.9057 | 425 | 0.1603
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.029667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_6 | 3 |  | 8.9057 | 425 | 0.2642
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_3 | 3 |  | 8.9057 | 425 | 0.35623
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_4 | 3 |  | 8.9057 | 425 | 0.35623
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.040282 | lb/MMBtu | ERT | No |  | 3 | 979 | 8.9057 | 425 | 0.35874
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.048333 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_3 | 3 |  | 8.9057 | 425 | 0.43044
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.055667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_5 | 3 |  | 8.9057 | 425 | 0.49575
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.058667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_1 | 3 |  | 8.9057 | 425 | 0.52247
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.058667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_2 | 3 |  | 8.9057 | 425 | 0.52247
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.061667 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_1 | 3 |  | 8.9057 | 425 | 0.54918
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.062667 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_4 | 3 |  | 8.9057 | 425 | 0.55809
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.063 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_2 | 3 |  | 8.9057 | 425 | 0.56106
2716_2 | W.H. Weatherspoon Plant |  | 2716 | 2 | Wea_Cfg_1 | Filterable Particulate | 0.074333 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_5 | 3 |  | 8.9057 | 425 | 0.66199
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.018 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_6 | 3 |  | 8.9057 | 426 | 0.1603
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.029667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_6 | 3 |  | 8.9057 | 426 | 0.2642
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_3 | 3 |  | 8.9057 | 426 | 0.35623
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_4 | 3 |  | 8.9057 | 426 | 0.35623
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.040282 | lb/MMBtu | ERT | No |  | 3 | 979 | 8.9057 | 426 | 0.35874
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.048333 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_3 | 3 |  | 8.9057 | 426 | 0.43044
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.055667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_5 | 3 |  | 8.9057 | 426 | 0.49575
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.058667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_1 | 3 |  | 8.9057 | 426 | 0.52247
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.058667 | lb/MMBtu | Part II | 0 | Wea_Blr_2_Test_2 | 3 |  | 8.9057 | 426 | 0.52247
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.061667 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_1 | 3 |  | 8.9057 | 426 | 0.54918
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.062667 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_4 | 3 |  | 8.9057 | 426 | 0.55809
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.063 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_2 | 3 |  | 8.9057 | 426 | 0.56106
2716_1 | W.H. Weatherspoon Plant |  | 2716 | 1 | Wea_Cfg_1 | Filterable Particulate | 0.074333 | lb/MMBtu | Part II | 0 | Wea_Blr_1_Test_5 | 3 |  | 8.9057 | 426 | 0.66199
2718_ES-5 | G G Allen |  | 2718 | ES-5 | 5-2009 | Filterable Particulate | 0.016933 | lb/MMBtu | Part II | 0 | CS125(4/23/09) | 3 |  | 9.4812 | 427 | 0.16055
6068_1 | Jeffrey Energy Center |  | 6068 | 1 | 1 | Filterable Particulate | 0.015213 | lb/MMBtu | Part II | 0 | PM TEST 0709\1 | 3 |  | 10.6278 | 428 | 0.16168
6068_1 | Jeffrey Energy Center |  | 6068 | 1 | 1 | Filterable Particulate | 0.019133 | lb/MMBtu | Part II | 0 | PM 0707/1 | 3 |  | 10.6278 | 428 | 0.20335
6068_1 | Jeffrey Energy Center |  | 6068 | 1 | 1 | Filterable Particulate | 0.023333 | lb/MMBtu | Part II | 0 | CAM 0609/1 | 3 |  | 10.6278 | 428 | 0.24798
6068_1 | Jeffrey Energy Center |  | 6068 | 1 | 1 | Filterable Particulate | 0.030111 | lb/MMBtu | Part II | 0 | CAM 0406/1 | 9 |  | 10.6278 | 428 | 0.32002
6068_1 | Jeffrey Energy Center |  | 6068 | 1 | 1 | Filterable Particulate | 0.045167 | lb/MMBtu | Part II | 0 | CAM 0109\1 | 18 |  | 10.6278 | 428 | 0.48002
1077_2 | Sutherland |  | 1077 | 2 | Unit 2 | Filterable Particulate | 0.0134 | lb/MMBtu | Part II | 0 | SUTH2-PM-20060517 | 1 |  | 12.1553 | 429 | 0.16288
1077_2 | Sutherland |  | 1077 | 2 | Unit 2 | Filterable Particulate | 0.0178 | lb/MMBtu | Part II | 0 | SUTH2-PM-20080717 | 1 |  | 12.1553 | 429 | 0.21637
1702_1 | D.E. Karn |  | 1702 | 1 | DEK1-Conf | Filterable Particulate | 0.018333 | lb/MMBtu | Part II | 0 | DEK1 - 2005 PM Testing | 3 |  | 8.8909 | 430 | 0.163
1702_1 | D.E. Karn |  | 1702 | 1 | DEK1-Conf | Filterable Particulate | 0.0263 | lb/MMBtu | Part II | 0 | DEK1 - 2009 PM Testing | 3 |  | 8.8909 | 430 | 0.23383
3406_6 | Johnsonville |  | 3406 | 6 | 6 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 10.6531 | 431 | 0.16335
3406_6 | Johnsonville |  | 3406 | 6 | 6 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 10.6531 | 431 | 0.26988
3406_6 | Johnsonville |  | 3406 | 6 | 6 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 10.6531 | 431 | 0.43678
3406_5 | Johnsonville |  | 3406 | 5 | 5 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 10.6531 | 432 | 0.16335
3406_5 | Johnsonville |  | 3406 | 5 | 5 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 10.6531 | 432 | 0.26988
3406_5 | Johnsonville |  | 3406 | 5 | 5 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 10.6531 | 432 | 0.43678
2718_ES-1 | G G Allen |  | 2718 | ES-1 | 1-2009 | Filterable Particulate | 0.016933 | lb/MMBtu | Part II | 0 | CS125(4/23/09) | 3 |  | 9.8638 | 433 | 0.16703
6124_1 | McIntosh |  | 6124 | 1 | Unit 1 | Filterable Particulate | 0.017305 | lb/MMBtu | Part II | 0 | + | 3 |  | 9.6869 | 434 | 0.16763
6124_1 | McIntosh |  | 6124 | 1 | Unit 1 | Filterable Particulate | 0.032162 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (February 8, 2007) | 3 |  | 9.6869 | 434 | 0.31155
6641_2 | Independence |  | 6641 | 2 | 002 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 9.8976 | 435 | 0.16826
2161_5 | James River Power Station |  | 2161 | 5 | Unit_5_JRPS | Filterable Particulate | 0.017637 | lb/MMBtu | ERT | No |  | 3 | 21351 | 9.619 | 436 | 0.16965
3406_1 | Johnsonville |  | 3406 | 1 | 1 | Filterable Particulate | 0.015333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2005 | 3 |  | 11.24 | 437 | 0.17235
3406_1 | Johnsonville |  | 3406 | 1 | 1 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 11.24 | 437 | 0.28475
3406_1 | Johnsonville |  | 3406 | 1 | 1 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 11.24 | 437 | 0.46084
2732_9 | Riverbend |  | 2732 | 9 | 9 | Filterable Particulate | 0.018567 | lb/MMBtu | Part II | 0 | BLR9(3/20/07) | 3 |  | 9.3013 | 438 | 0.17269
2732_9 | Riverbend |  | 2732 | 9 | 9 | Filterable Particulate | 0.0427 | lb/MMBtu | Part II | 0 | BLR9(3/3/09) | 3 |  | 9.3013 | 438 | 0.39717
2732_9 | Riverbend |  | 2732 | 9 | 9 | Filterable Particulate | 0.065333 | lb/MMBtu | Part II | 0 | BLR9(2/20/08) | 3 |  | 9.3013 | 438 | 0.60769
1382_H2 | HMP&L Station Two Henderson |  | 1382 | H2 | 2 | Filterable Particulate | 0.016067 | lb/MMBtu | Part II | 0 | H2 compliance 2006 | 3 |  | 10.7811 | 439 | 0.17322
1382_H2 | HMP&L Station Two Henderson |  | 1382 | H2 | 2 | Filterable Particulate | 0.020167 | lb/MMBtu | Part II | 0 | H2 compliance 2009 | 3 |  | 10.7811 | 439 | 0.21742
6071_1 | Trimble Co. |  | 6071 | 1 | TC01 | Filterable Particulate | 0.017 | lb/MMBtu | Part II | 0 | TC1-PM-2008 | 1 |  | 10.2413 | 440 | 0.1741
2832_Unit 6 | Miami Fort |  | 2832 | Unit 6 | U6 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | 0 | U6032708 | 3 |  | 7.16 | 441 | 0.17423
2832_Unit 6 | Miami Fort |  | 2832 | Unit 6 | U6 | Filterable Particulate | 0.034 | lb/MMBtu | Part II | 0 | U6030306 | 3 |  | 7.16 | 441 | 0.24344
3935_3 | John E. Amos |  | 3935 | 3 | AM-3 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | Unit 3 | 1 |  | 9.1815 | 442 | 0.17445
6031_2 | Killen Station |  | 6031 | 2 | 2-Operation | Filterable Particulate | 0.019433 | lb/MMBtu | Part II | 0 | PM Test 2007 | 3 |  | 9.0091 | 443 | 0.17508
3938_21 | Philip Sporn |  | 3938 | 21 | SP-2 | Filterable Particulate | 0.0206 | lb/MMBtu | Part II | 0 | July2005PM | 1 |  | 8.5967 | 444 | 0.17709
3938_21 | Philip Sporn |  | 3938 | 21 | SP-2 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 8.5967 | 444 | 0.20202
3938_21 | Philip Sporn |  | 3938 | 21 | SP-2 | Filterable Particulate | 0.0285 | lb/MMBtu | Part II | 0 | June2007PM | 1 |  | 8.5967 | 444 | 0.24501
3938_11 | Philip Sporn |  | 3938 | 11 | SP-1 | Filterable Particulate | 0.0206 | lb/MMBtu | Part II | 0 | July2005PM | 1 |  | 8.5967 | 445 | 0.17709
3938_11 | Philip Sporn |  | 3938 | 11 | SP-1 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 8.5967 | 445 | 0.20202
3938_11 | Philip Sporn |  | 3938 | 11 | SP-1 | Filterable Particulate | 0.0285 | lb/MMBtu | Part II | 0 | June2007PM | 1 |  | 8.5967 | 445 | 0.24501
6061_2 | South Mississippi El Pwr Assn |  | 6061 | 2 | 2 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | Morrow PM 2008 | 1 |  | 12.7451 | 446 | 0.17843
6061_1 | South Mississippi El Pwr Assn |  | 6061 | 1 | 1 | Filterable Particulate | 0.014 | lb/MMBtu | Part II | 0 | Morrow PM 2008 | 1 |  | 12.7451 | 447 | 0.17843
898_Unit 4 | Wood River |  | 898 | Unit 4 | 4 | Filterable Particulate | 0.0147 | lb/MMBtu | Part II | 0 | 10 | 1 |  | 12.1753 | 448 | 0.17898
898_Unit 4 | Wood River |  | 898 | Unit 4 | 4 | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | 12 | 1 |  | 12.1753 | 448 | 0.18263
898_Unit 4 | Wood River |  | 898 | Unit 4 | 4 | Filterable Particulate | 0.0275 | lb/MMBtu | Part II | 0 | 8 | 1 |  | 12.1753 | 448 | 0.33482
898_Unit 4 | Wood River |  | 898 | Unit 4 | 4 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 12.1753 | 448 | 0.42613
2732_10 | Riverbend |  | 2732 | 10 | 10 | Filterable Particulate | 0.0193 | lb/MMBtu | Part II | 0 | BLR10(3/5/09) | 3 |  | 9.3409 | 449 | 0.18028
2732_10 | Riverbend |  | 2732 | 10 | 10 | Filterable Particulate | 0.0313 | lb/MMBtu | Part II | 0 | BLR10(3/21/07) | 3 |  | 9.3409 | 449 | 0.29237
2732_10 | Riverbend |  | 2732 | 10 | 10 | Filterable Particulate | 0.0351 | lb/MMBtu | Part II | 0 | BLR10(2/20/08) | 3 |  | 9.3409 | 449 | 0.32787
6166_MB2 | Rockport |  | 6166 | MB2 | RP-2 | Filterable Particulate | 0.0194 | lb/MMBtu | Part II | 0 | Feb2010PMwPAC | 1 |  | 9.3742 | 450 | 0.18186
6166_MB2 | Rockport |  | 6166 | MB2 | RP-2 | Filterable Particulate | 0.0255 | lb/MMBtu | Part II | 0 | Feb2010PMnoPAC | 1 |  | 9.3742 | 450 | 0.23904
6166_MB1 | Rockport |  | 6166 | MB1 | RP-1 | Filterable Particulate | 0.0194 | lb/MMBtu | Part II | 0 | Feb2010PMwPAC | 1 |  | 9.3742 | 451 | 0.18186
6166_MB1 | Rockport |  | 6166 | MB1 | RP-1 | Filterable Particulate | 0.0255 | lb/MMBtu | Part II | 0 | Feb2010PMnoPAC | 1 |  | 9.3742 | 451 | 0.23904
2824_1 | Stanton |  | 2824 | 1 | u1 | Filterable Particulate | 0.0135 | lb/MMBtu | Part II | 0 | Particulate test | 4 |  | 13.6364 | 452 | 0.18409
7253_1 | Richard Gorsuch |  | 7253 | 1 | UNIT1 | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | Particulate2008(1,2,4) | 3 |  | 8.5422 | 453 | 0.18793
7253_1 | Richard Gorsuch |  | 7253 | 1 | UNIT1 | Filterable Particulate | 0.031 | lb/MMBtu | Part II | 0 | Particulate 2006 | 3 |  | 8.5422 | 453 | 0.26481
990_70 | Harding Street |  | 990 | 70 | 70ss | Filterable Particulate | 0.021119 | lb/MMBtu | ERT | No |  | 6 | 1177 | 8.905 | 454 | 0.18806
6139_2 | Welsh |  | 6139 | 2 | WE-2 | Filterable Particulate | 0.0204 | lb/MMBtu | Part II | 0 | Jan2008PM | 1 |  | 9.2401 | 455 | 0.1885
6139_2 | Welsh |  | 6139 | 2 | WE-2 | Filterable Particulate | 0.0225 | lb/MMBtu | Part II | 0 | May2008PM | 1 |  | 9.2401 | 455 | 0.2079
6139_2 | Welsh |  | 6139 | 2 | WE-2 | Filterable Particulate | 0.0306 | lb/MMBtu | Part II | 0 | Sept2007PM | 1 |  | 9.2401 | 455 | 0.28275
3098_4 | Elrama Power Plant |  | 3098 | 4 | ELR4-2 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT | No |  | 9 | 966 | 10.3838 | 456 | 0.19156
3098_4 | Elrama Power Plant |  | 3098 | 4 | ELR4-2 | Filterable Particulate | 0.039667 | lb/MMBtu | Part II | 0 | E-37C | 3 |  | 10.3838 | 456 | 0.41189
3098_4 | Elrama Power Plant |  | 3098 | 4 | ELR4-2 | Filterable Particulate | 0.040333 | lb/MMBtu | Part II | 0 | E-37I | 3 |  | 10.3838 | 456 | 0.41881
3098_4 | Elrama Power Plant |  | 3098 | 4 | ELR4-2 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | E-37 | 3 |  | 10.3838 | 456 | 0.53996
3098_4 | Elrama Power Plant |  | 3098 | 4 | ELR4-2 | Filterable Particulate | 0.136 | lb/MMBtu | Part II | 0 | E-37B | 3 |  | 10.3838 | 456 | 1.4122
3098_4 | Elrama Power Plant |  | 3098 | 4 | ELR4-2 | Filterable Particulate | 0.16217 | lb/MMBtu | Part II | 0 | E-36 | 3 |  | 10.3838 | 456 | 1.6839
3098_3 | Elrama Power Plant |  | 3098 | 3 | ELR3-2 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT | No |  | 9 | 966 | 10.424 | 457 | 0.1923
3098_3 | Elrama Power Plant |  | 3098 | 3 | ELR3-2 | Filterable Particulate | 0.039667 | lb/MMBtu | Part II | 0 | E-37C | 3 |  | 10.424 | 457 | 0.41349
3098_3 | Elrama Power Plant |  | 3098 | 3 | ELR3-2 | Filterable Particulate | 0.040333 | lb/MMBtu | Part II | 0 | E-37I | 3 |  | 10.424 | 457 | 0.42043
3098_3 | Elrama Power Plant |  | 3098 | 3 | ELR3-2 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | E-37 | 3 |  | 10.424 | 457 | 0.54205
3098_3 | Elrama Power Plant |  | 3098 | 3 | ELR3-2 | Filterable Particulate | 0.136 | lb/MMBtu | Part II | 0 | E-37B | 3 |  | 10.424 | 457 | 1.4177
3098_3 | Elrama Power Plant |  | 3098 | 3 | ELR3-2 | Filterable Particulate | 0.16217 | lb/MMBtu | Part II | 0 | E-36 | 3 |  | 10.424 | 457 | 1.6904
2161_4 | James River Power Station |  | 2161 | 4 | Unit_4_JRPS | Filterable Particulate | 0.019434 | lb/MMBtu | ERT | No |  | 3 | 2135 | 10 | 458 | 0.19434
709_2 | Harllee Branch |  | 709 | 2 | Unit 2 | Filterable Particulate | 0.020999 | lb/MMBtu | Part II | 0 | Unit 1&2 PM Emissions Test (June 15, 2005) | 3 |  | 9.3124 | 459 | 0.19555
709_2 | Harllee Branch |  | 709 | 2 | Unit 2 | Filterable Particulate | 0.028334 | lb/MMBtu | Part II | 0 | Unit 1&2 PM Emissions Test (June 11, 2009) | 3 |  | 9.3124 | 459 | 0.26386
709_2 | Harllee Branch |  | 709 | 2 | Unit 2 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | Unit 1&2 PM Emissions Test (May 24, 2007) | 3 |  | 9.3124 | 459 | 0.27937
136_2 | Seminole Generating Station |  | 136 | 2 | Unit 2 | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | Multi-Pollutant Test Report 2009 (Unit 2) | 3 |  | 10.3343 | 460 | 0.19635
995_8 | Bailly |  | 995 | 8 | 8 | Filterable Particulate | 0.020491 | lb/MMBtu | Part II | 0 | BGS U#7/8 M5 06/27/2006 | 1 |  | 9.5852 | 461 | 0.19641
995_8 | Bailly |  | 995 | 8 | 8 | Filterable Particulate | 0.040045 | lb/MMBtu | Part II | 0 | BGS U#7&8 M5 09/30/2008 | 1 |  | 9.5852 | 461 | 0.38384
3152_2A | Sunbury Generation LP |  | 3152 | 2A | Boiler 2A | Filterable Particulate | 0.014996 | lb/MMBtu | Part II | 0 | PM_012709 | 3 |  | 13.125 | 462 | 0.19682
3152_2A | Sunbury Generation LP |  | 3152 | 2A | Boiler 2A | Filterable Particulate | 0.021454 | lb/MMBtu | Part II | 0 | PM_011909 | 3 |  | 13.125 | 462 | 0.28159
3948_1 | Mitchell |  | 3948 | 1 | MI-1 | Filterable Particulate | 0.023 | lb/MMBtu | Part II | 0 | April2009PM | 1 |  | 8.5998 | 463 | 0.19779
6096_NC1 | Nebraska City |  | 6096 | NC1 | NC1 | Filterable Particulate | 0.0195 | lb/MMBtu | Part II | 0 | PM NC Unit 1 | 1 |  | 10.147 | 464 | 0.19787
68029_BLR1 | AES Puerto Rico Cogeneration Facility |  | 68029 | BLR1 | Unit_1 | Filterable Particulate | 0.020522 | lb/MMBtu | ERT | No |  | 6 | 2027 | 9.6525 | 465 | 0.19809
709_1 | Harllee Branch |  | 709 | 1 | Unit 1 | Filterable Particulate | 0.020999 | lb/MMBtu | Part II | 0 | Unit 1&2 PM Emissions Test (June 15, 2005) | 3 |  | 9.5232 | 466 | 0.19998
709_1 | Harllee Branch |  | 709 | 1 | Unit 1 | Filterable Particulate | 0.028334 | lb/MMBtu | Part II | 0 | Unit 1&2 PM Emissions Test (June 11, 2009) | 3 |  | 9.5232 | 466 | 0.26983
709_1 | Harllee Branch |  | 709 | 1 | Unit 1 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | Unit 1&2 PM Emissions Test (May 24, 2007) | 3 |  | 9.5232 | 466 | 0.2857
6254_1 | Ottumwa |  | 6254 | 1 | Unit 1 | Filterable Particulate | 0.0193 | lb/MMBtu | Part II | 0 | OGS1-PM-20060615 | 1 |  | 10.4431 | 467 | 0.20155
6254_1 | Ottumwa |  | 6254 | 1 | Unit 1 | Filterable Particulate | 0.0292 | lb/MMBtu | Part II | 0 | OGS1-PM-20080501 | 1 |  | 10.4431 | 467 | 0.30494
3280_CAN2 | Canadys Steam |  | 3280 | CAN2 | CAN002 | Filterable Particulate | 0.0211 | lb/MMBtu | Part II | 0 | PM-03/06-CAN2 | 1 |  | 9.5585 | 468 | 0.20169
3280_CAN2 | Canadys Steam |  | 3280 | CAN2 | CAN002 | Filterable Particulate | 0.0613 | lb/MMBtu | Part II | 0 | PM-01/08-CAN2 | 1 |  | 9.5585 | 468 | 0.58594
3280_CAN2 | Canadys Steam |  | 3280 | CAN2 | CAN002 | Filterable Particulate | 0.1154 | lb/MMBtu | Part II | 0 | PM-01/09-CAN2 | 1 |  | 9.5585 | 468 | 1.1031
3280_CAN2 | Canadys Steam |  | 3280 | CAN2 | CAN002 | Filterable Particulate | 0.1386 | lb/MMBtu | Part II | 0 | PM-03/05-CAN2 | 1 |  | 9.5585 | 468 | 1.3248
3280_CAN2 | Canadys Steam |  | 3280 | CAN2 | CAN002 | Filterable Particulate | 0.158 | lb/MMBtu | Part II | 0 | PM-02/07-CAN2 | 1 |  | 9.5585 | 468 | 1.5102
3938_41 | Philip Sporn |  | 3938 | 41 | SP-4 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 8.5967 | 469 | 0.20202
3938_31 | Philip Sporn |  | 3938 | 31 | SP-3 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 8.5967 | 470 | 0.20202
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.018913 | lb/MMBtu | Part II | 0 | PM2005_NovB | 1 |  | 10.7364 | 471 | 0.20306
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.03016 | lb/MMBtu | Part II | 0 | PM2006_FebC | 2 |  | 10.7364 | 471 | 0.32381
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.048008 | lb/MMBtu | Part II | 0 | PM2006_FebB | 2 |  | 10.7364 | 471 | 0.51543
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.057756 | lb/MMBtu | Part II | 0 | PM2005_OctB | 1 |  | 10.7364 | 471 | 0.62009
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.063752 | lb/MMBtu | Part II | 0 | PM2006_FebD | 2 |  | 10.7364 | 471 | 0.68446
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.068329 | lb/MMBtu | Part II | 0 | PM2006_AprE | 2 |  | 10.7364 | 471 | 0.7336
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.075085 | lb/MMBtu | Part II | 0 | PM2006_AprC | 2 |  | 10.7364 | 471 | 0.80613
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.092185 | lb/MMBtu | Part II | 0 | PM2006_AprD | 2 |  | 10.7364 | 471 | 0.98973
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.10418 | lb/MMBtu | Part II | 0 | PM2006_AprA | 2 |  | 10.7364 | 471 | 1.1185
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.10708 | lb/MMBtu | Part II | 0 | PM2006_FebA | 2 |  | 10.7364 | 471 | 1.1497
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.11344 | lb/MMBtu | Part II | 0 | PM2005_NovA | 3 |  | 10.7364 | 471 | 1.2179
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.12029 | lb/MMBtu | Part II | 0 | PM2005_AugA | 2 |  | 10.7364 | 471 | 1.2915
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.13961 | lb/MMBtu | Part II | 0 | PM2005_SeptB | 2 |  | 10.7364 | 471 | 1.4989
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.16121 | lb/MMBtu | Part II | 0 | PM2005_AugB | 1 |  | 10.7364 | 471 | 1.7309
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.17023 | lb/MMBtu | Part II | 0 | PM2006_AprB | 2 |  | 10.7364 | 471 | 1.8277
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.18323 | lb/MMBtu | Part II | 0 | PM2005_SeptC | 2 |  | 10.7364 | 471 | 1.9672
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.19133 | lb/MMBtu | Part II | 0 | PM2008_Sept | 3 |  | 10.7364 | 471 | 2.0542
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.193 | lb/MMBtu | Part II | 0 | PM2008_July | 2 |  | 10.7364 | 471 | 2.0721
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.2137 | lb/MMBtu | Part II | 0 | PM2005_SeptA | 2 |  | 10.7364 | 471 | 2.2944
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.21907 | lb/MMBtu | Part II | 0 | PM2005_Jan | 2 |  | 10.7364 | 471 | 2.352
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.233 | lb/MMBtu | Part II | 0 | PM2005_AugC | 2 |  | 10.7364 | 471 | 2.5016
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.262 | lb/MMBtu | Part II | 0 | PM2008_June | 2 |  | 10.7364 | 471 | 2.8129
1731_1 | Harbor Beach Power Plant |  | 1731 | 1 | HB1-Config | Filterable Particulate | 0.50112 | lb/MMBtu | Part II | 0 | PM2005_AugD | 2 |  | 10.7364 | 471 | 5.3802
10075_1 | Taconite Harbor Energy Center |  | 10075 | 1 | THEC1 | Filterable Particulate | 0.020079 | lb/MMBtu | ERT | No |  | 6 | 1735 | 10.2048 | 472 | 0.2049
2836_10 | Avon Lake |  | 2836 | 10 | AL10 | Filterable Particulate | 0.014333 | lb/MMBtu | Part II | 0 | AL-15 | 3 |  | 14.3267 | 473 | 0.20535
2836_10 | Avon Lake |  | 2836 | 10 | AL10 | Filterable Particulate | 0.034333 | lb/MMBtu | Part II | 0 | AL-15A | 3 |  | 14.3267 | 473 | 0.49188
3393_2 | Allen Steam Plant |  | 3393 | 2 | 2 | Filterable Particulate | 0.022333 | lb/MMBtu | Part II | 0 | ALF2 - 2006 | 3 |  | 9.2848 | 474 | 0.20736
3393_2 | Allen Steam Plant |  | 3393 | 2 | 2 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | ALF2 - 2008 | 3 |  | 9.2848 | 474 | 0.2445
2850_B001 | J M Stuart |  | 2850 | B001 | MS1W | Filterable Particulate | 0.022333 | lb/MMBtu | Part II | 0 | U1PM2009 | 3 |  | 9.3098 | 475 | 0.20792
2850_B001 | J M Stuart |  | 2850 | B001 | MS1W | Filterable Particulate | 0.032367 | lb/MMBtu | Part II | 0 | U1PM2008 | 3 |  | 9.3098 | 475 | 0.30133
2104_3 | Meramec |  | 2104 | 3 | 003 | Filterable Particulate | 0.0185 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 11.2482 | 476 | 0.20809
4072_7 | Pulliam |  | 4072 | 7 | 7 | Filterable Particulate | 0.018333 | lb/MMBtu | Part II | 0 | P7 PM 2008 | 3 |  | 11.3911 | 477 | 0.20884
6064_N1 | Nearman Creek |  | 6064 | N1 | N1 | Filterable Particulate | 0.0223 | lb/MMBtu | Part II | 0 | PM Test Report | 3 |  | 9.4522 | 478 | 0.21078
3_1 | Barry |  | 3 | 1 | Unit 1 | Filterable Particulate | 0.022297 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (June 2, 2009) | 3 |  | 9.5233 | 479 | 0.21234
3_1 | Barry |  | 3 | 1 | Unit 1 | Filterable Particulate | 0.025746 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (June 19, 2008) | 3 |  | 9.5233 | 479 | 0.24519
3_1 | Barry |  | 3 | 1 | Unit 1 | Filterable Particulate | 0.03606 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Emissions Test (June 21, 2006) | 3 |  | 9.5233 | 479 | 0.34341
3_1 | Barry |  | 3 | 1 | Unit 1 | Filterable Particulate | 0.061396 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (May 22, 2007) | 3 |  | 9.5233 | 479 | 0.58469
3_1 | Barry |  | 3 | 1 | Unit 1 | Filterable Particulate | 0.092989 | lb/MMBtu | Part II | 0 | Unit 1 CAM Test (June 22, 2006) | 3 |  | 9.5233 | 479 | 0.88557
56_3 | Charles R. Lowman |  | 56 | 3 | 3D | Filterable Particulate | 0.022 | lb/MMBtu | Part II | 0 | 2009 PM Test - 3 | 1 |  | 9.6899 | 480 | 0.21318
2708_5 | Cape Fear Steam Electric Plant |  | 2708 | 5 | Cap_Cfg_5b | Filterable Particulate | 0.026504 | lb/MMBtu | ERT | No |  | 6 | 981 | 8.1176 | 481 | 0.21515
2708_5 | Cape Fear Steam Electric Plant |  | 2708 | 5 | Cap_Cfg_5b | Filterable Particulate | 0.031667 | lb/MMBtu | Part II | 0 | Cap_Blr_5_Test_8 | 3 |  | 8.1176 | 481 | 0.25706
2708_5 | Cape Fear Steam Electric Plant |  | 2708 | 5 | Cap_Cfg_5b | Filterable Particulate | 0.066 | lb/MMBtu | Part II | 0 | Cap_Blr_5_Test_7 | 3 |  | 8.1176 | 481 | 0.53576
2708_5 | Cape Fear Steam Electric Plant |  | 2708 | 5 | Cap_Cfg_5b | Filterable Particulate | 0.067333 | lb/MMBtu | Part II | 0 | Cap_Blr_5_Test_5 | 3 |  | 8.1176 | 481 | 0.54659
2708_5 | Cape Fear Steam Electric Plant |  | 2708 | 5 | Cap_Cfg_5b | Filterable Particulate | 0.069667 | lb/MMBtu | Part II | 0 | Cap_Blr_5_Test_6 | 3 |  | 8.1176 | 481 | 0.56553
6095_1 | Sooner |  | 6095 | 1 | SO1 Config | Filterable Particulate | 0.016 | lb/MMBtu | Part II | 0 | Stack Sampling Report\Sooner 1 | 1 |  | 13.5382 | 482 | 0.21661
26_1 | E. C. Gaston |  | 26 | 1 | Unit 1 | Filterable Particulate | 0.024086 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Emissions Test (May 12, 2005) | 3 |  | 9.0009 | 483 | 0.2168
26_1 | E. C. Gaston |  | 26 | 1 | Unit 1 | Filterable Particulate | 0.030744 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (April 17, 2008) | 3 |  | 9.0009 | 483 | 0.27672
26_1 | E. C. Gaston |  | 26 | 1 | Unit 1 | Filterable Particulate | 0.045433 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Emissions Test (May 8, 2007) | 3 |  | 9.0009 | 483 | 0.40894
26_1 | E. C. Gaston |  | 26 | 1 | Unit 1 | Filterable Particulate | 0.0642 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (June 1, 2006) | 3 |  | 9.0009 | 483 | 0.57786
26_1 | E. C. Gaston |  | 26 | 1 | Unit 1 | Filterable Particulate | 0.089667 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (July 29 and 30, 2009) | 3 |  | 9.0009 | 483 | 0.80708
26_1 | E. C. Gaston |  | 26 | 1 | Unit 1 | Filterable Particulate | 0.11923 | lb/MMBtu | Part II | 0 | Unit 1 CAM Test (June 2, 2006) | 3 |  | 9.0009 | 483 | 1.0732
663_B-2 | Deerhaven Generating Station |  | 663 | B-2 | 001 | Filterable Particulate | 0.021 | lb/MMBtu | Part II | 0 | 5 | 1 |  | 10.3319 | 484 | 0.21697
6068_2 | Jeffrey Energy Center |  | 6068 | 2 | 2 | Filterable Particulate | 0.021067 | lb/MMBtu | Part II | 0 | PM 0707/2 | 3 |  | 10.3359 | 485 | 0.21774
6068_2 | Jeffrey Energy Center |  | 6068 | 2 | 2 | Filterable Particulate | 0.022012 | lb/MMBtu | Part II | 0 | CAM 0709/2 | 18 |  | 10.3359 | 485 | 0.22751
6068_2 | Jeffrey Energy Center |  | 6068 | 2 | 2 | Filterable Particulate | 0.02424 | lb/MMBtu | Part II | 0 | CAM 0406/2 | 10 |  | 10.3359 | 485 | 0.25054
51_24641 | Dolet Hills |  | 51 | 24641 | 001 | Filterable Particulate | 0.020974 | lb/MMBtu | Part II | 0 | Stack Compliance Test DHPS | 3 |  | 10.4371 | 486 | 0.2189
6250_1B | Mayo Electric Generating Facility |  | 6250 | 1B | May_Cfg_1b | Filterable Particulate | 0.023333 | lb/MMBtu | Part II | 0 | May_Unit_1_Test_6h | 3 |  | 9.452 | 487 | 0.22055
6250_1A | Mayo Electric Generating Facility |  | 6250 | 1A | May_Cfg_1b | Filterable Particulate | 0.023333 | lb/MMBtu | Part II | 0 | May_Unit_1_Test_6h | 3 |  | 9.452 | 488 | 0.22055
6095_2 | Sooner |  | 6095 | 2 | SO2 Config | Filterable Particulate | 0.015 | lb/MMBtu | Part II | 0 | Stack Sampling Report\Sooner 2 | 1 |  | 14.7829 | 489 | 0.22174
2848_H-6 | O H Hutchings |  | 2848 | H-6 | H-6 | Filterable Particulate | 0.021 | lb/MMBtu | Part II | 0 | 2005 H-6 | 3 |  | 10.6777 | 490 | 0.22423
2848_H-6 | O H Hutchings |  | 2848 | H-6 | H-6 | Filterable Particulate | 0.023 | lb/MMBtu | Part II | 0 | 2007 H-6 | 3 |  | 10.6777 | 490 | 0.24559
2848_H-6 | O H Hutchings |  | 2848 | H-6 | H-6 | Filterable Particulate | 0.031067 | lb/MMBtu | Part II | 0 | 2009 H-6 | 3 |  | 10.6777 | 490 | 0.33172
2848_H-6 | O H Hutchings |  | 2848 | H-6 | H-6 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | 2006 H-6 | 3 |  | 10.6777 | 490 | 0.37372
2848_H-6 | O H Hutchings |  | 2848 | H-6 | H-6 | Filterable Particulate | 0.042 | lb/MMBtu | Part II | 0 | 2007 H-6 Hg | 3 |  | 10.6777 | 490 | 0.44846
2848_H-6 | O H Hutchings |  | 2848 | H-6 | H-6 | Filterable Particulate | 0.050367 | lb/MMBtu | Part II | 0 | 2008 H-6 | 3 |  | 10.6777 | 490 | 0.5378
6076_3 | Colstrip |  | 6076 | 3 | Unit3 | Filterable Particulate | 0.024066 | lb/MMBtu | ERT | No |  | 6 | 1558 | 9.4075 | 491 | 0.2264
2103_4 | Labadie |  | 2103 | 4 | 004 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 0 | 6 | 1 |  | 9.6477 | 492 | 0.22672
7253_3 | Richard Gorsuch |  | 7253 | 3 | UNIT3 | Filterable Particulate | 0.021855 | lb/MMBtu | ERT | No |  | 6 | 1906 | 10.3752 | 493 | 0.22675
7253_3 | Richard Gorsuch |  | 7253 | 3 | UNIT3 | Filterable Particulate | 0.027667 | lb/MMBtu | Part II | 0 | Particulate 2006 | 3 |  | 10.3752 | 493 | 0.28705
7253_3 | Richard Gorsuch |  | 7253 | 3 | UNIT3 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | 0 | Particulate2008(3) | 3 |  | 10.3752 | 493 | 0.29051
3181_33 | Mitchell Power Station |  | 3181 | 33 | 033 | Filterable Particulate | 0.026 | lb/MMBtu | Part II | 0 | 1 | 3 |  | 8.8685 | 494 | 0.23058
3098_2 | Elrama Power Plant |  | 3098 | 2 | ELR2-2 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT | No |  | 9 | 966 | 12.54 | 495 | 0.23134
3098_2 | Elrama Power Plant |  | 3098 | 2 | ELR2-2 | Filterable Particulate | 0.039667 | lb/MMBtu | Part II | 0 | E-37C | 3 |  | 12.54 | 495 | 0.49742
3098_2 | Elrama Power Plant |  | 3098 | 2 | ELR2-2 | Filterable Particulate | 0.040333 | lb/MMBtu | Part II | 0 | E-37I | 3 |  | 12.54 | 495 | 0.50578
3098_2 | Elrama Power Plant |  | 3098 | 2 | ELR2-2 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | E-37 | 3 |  | 12.54 | 495 | 0.65208
3098_2 | Elrama Power Plant |  | 3098 | 2 | ELR2-2 | Filterable Particulate | 0.136 | lb/MMBtu | Part II | 0 | E-37B | 3 |  | 12.54 | 495 | 1.7054
3098_2 | Elrama Power Plant |  | 3098 | 2 | ELR2-2 | Filterable Particulate | 0.16217 | lb/MMBtu | Part II | 0 | E-36 | 3 |  | 12.54 | 495 | 2.0336
3098_1 | Elrama Power Plant |  | 3098 | 1 | ELR1-2 | Filterable Particulate | 0.018448 | lb/MMBtu | ERT | No |  | 9 | 966 | 12.54 | 496 | 0.23134
3098_1 | Elrama Power Plant |  | 3098 | 1 | ELR1-2 | Filterable Particulate | 0.039667 | lb/MMBtu | Part II | 0 | E-37C | 3 |  | 12.54 | 496 | 0.49742
3098_1 | Elrama Power Plant |  | 3098 | 1 | ELR1-2 | Filterable Particulate | 0.040333 | lb/MMBtu | Part II | 0 | E-37I | 3 |  | 12.54 | 496 | 0.50578
3098_1 | Elrama Power Plant |  | 3098 | 1 | ELR1-2 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | E-37 | 3 |  | 12.54 | 496 | 0.65208
3098_1 | Elrama Power Plant |  | 3098 | 1 | ELR1-2 | Filterable Particulate | 0.136 | lb/MMBtu | Part II | 0 | E-37B | 3 |  | 12.54 | 496 | 1.7054
3098_1 | Elrama Power Plant |  | 3098 | 1 | ELR1-2 | Filterable Particulate | 0.16217 | lb/MMBtu | Part II | 0 | E-36 | 3 |  | 12.54 | 496 | 2.0336
2732_7 | Riverbend |  | 2732 | 7 | 7 | Filterable Particulate | 0.021767 | lb/MMBtu | Part II | 0 | BLR7(2/12/08) | 3 |  | 10.6432 | 497 | 0.23167
2732_7 | Riverbend |  | 2732 | 7 | 7 | Filterable Particulate | 0.025433 | lb/MMBtu | Part II | 0 | BLR7(2/24/09) | 3 |  | 10.6432 | 497 | 0.27069
2732_7 | Riverbend |  | 2732 | 7 | 7 | Filterable Particulate | 0.025967 | lb/MMBtu | Part II | 0 | BLR7(3/27/07) | 3 |  | 10.6432 | 497 | 0.27637
2732_7 | Riverbend |  | 2732 | 7 | 7 | Filterable Particulate | 0.028377 | lb/MMBtu | ERT | No |  | 3 | 902 | 10.6432 | 497 | 0.30202
2732_7 | Riverbend |  | 2732 | 7 | 7 | Filterable Particulate | 0.10562 | lb/MMBtu | ERT | No |  | 3 | 903 | 10.6432 | 497 | 1.1241
2848_H-4 | O H Hutchings |  | 2848 | H-4 | H-4 | Filterable Particulate | 0.021333 | lb/MMBtu | Part II | 0 | 2007 H-4 | 3 |  | 10.875 | 498 | 0.232
2848_H-4 | O H Hutchings |  | 2848 | H-4 | H-4 | Filterable Particulate | 0.0239 | lb/MMBtu | Part II | 0 | 2009 H-4 | 3 |  | 10.875 | 498 | 0.25991
2848_H-4 | O H Hutchings |  | 2848 | H-4 | H-4 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | 2005 H-4 | 3 |  | 10.875 | 498 | 0.28637
2848_H-4 | O H Hutchings |  | 2848 | H-4 | H-4 | Filterable Particulate | 0.078667 | lb/MMBtu | Part II | 0 | 2007 H-4 Hg | 3 |  | 10.875 | 498 | 0.8555
2848_H-4 | O H Hutchings |  | 2848 | H-4 | H-4 | Filterable Particulate | 0.079133 | lb/MMBtu | Part II | 0 | 2008 H-4 | 3 |  | 10.875 | 498 | 0.86057
2848_H-4 | O H Hutchings |  | 2848 | H-4 | H-4 | Filterable Particulate | 0.095 | lb/MMBtu | Part II | 0 | 2006 H-4 | 3 |  | 10.875 | 498 | 1.0331
2732_8 | Riverbend |  | 2732 | 8 | 8 | Filterable Particulate | 0.021967 | lb/MMBtu | Part II | 0 | BLR8(2/25/09) | 3 |  | 10.59 | 499 | 0.23263
2732_8 | Riverbend |  | 2732 | 8 | 8 | Filterable Particulate | 0.024233 | lb/MMBtu | Part II | 0 | BLR8(2/13/08) | 3 |  | 10.59 | 499 | 0.25663
4072_6 | Pulliam |  | 4072 | 6 | 6 | Filterable Particulate | 0.019667 | lb/MMBtu | Part II | 0 | P5 PM 2008 | 3 |  | 11.8725 | 500 | 0.23349
54755_BLR2 | Roanoke Valley II |  | 54755 | BLR2 | Boiler 2 | Filterable Particulate | 0.021314 | lb/MMBtu | ERT | No |  | 6 | 2021 | 11.2 | 501 | 0.23871
7253_4 | Richard Gorsuch |  | 7253 | 4 | UNIT4 | Filterable Particulate | 0.024667 | lb/MMBtu | Part II | 0 | Particulate2008(1,2,4) | 3 |  | 9.7373 | 502 | 0.24019
7253_4 | Richard Gorsuch |  | 7253 | 4 | UNIT4 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | 0 | Particulate 2006 | 3 |  | 9.7373 | 502 | 0.48687
628_1 | Crystal River Power Plant |  | 628 | 1 | CryR_Cfg_1 | Filterable Particulate | 0.025133 | lb/MMBtu | Part II | 0 | CryR_Blr_1_Test_4 | 3 |  | 9.5925 | 503 | 0.24109
628_1 | Crystal River Power Plant |  | 628 | 1 | CryR_Cfg_1 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | CryR_Blr_1_Test_1 | 6 |  | 9.5925 | 503 | 0.28777
628_1 | Crystal River Power Plant |  | 628 | 1 | CryR_Cfg_1 | Filterable Particulate | 0.030367 | lb/MMBtu | Part II | 0 | CryR_Blr_1_Test_3 | 3 |  | 9.5925 | 503 | 0.29129
628_1 | Crystal River Power Plant |  | 628 | 1 | CryR_Cfg_1 | Filterable Particulate | 0.051967 | lb/MMBtu | Part II | 0 | CryR_Blr_1_Test_5 | 6 |  | 9.5925 | 503 | 0.49849
628_1 | Crystal River Power Plant |  | 628 | 1 | CryR_Cfg_1 | Filterable Particulate | 0.1089 | lb/MMBtu | Part II | 0 | CryR_Blr_1_Test_2 | 6 |  | 9.5925 | 503 | 1.0446
628_1 | Crystal River Power Plant |  | 628 | 1 | CryR_Cfg_1 | Filterable Particulate | 0.14705 | lb/MMBtu | ERT | No |  | 3 | 975 | 9.5925 | 503 | 1.4105
2850_B003 | J M Stuart |  | 2850 | B003 | MS3W | Filterable Particulate | 0.025967 | lb/MMBtu | Part II | 0 | U3PM2009 | 3 |  | 9.3098 | 504 | 0.24174
887_1 | Joppa Steam |  | 887 | 1 | 1 | Filterable Particulate | 0.024659 | lb/MMBtu | ERT | No |  | 6 | 2097 | 9.82 | 505 | 0.24215
889_Unit 3 | Baldwin Energy Complex |  | 889 | Unit 3 | 003 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 0 | 15 | 1 |  | 9.6961 | 506 | 0.2424
1904_4 | Black Dog |  | 1904 | 4 | Boiler 4 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 0 | Boiler 3 & 4 PM 2008 | 1 |  | 9.7472 | 507 | 0.24368
6113_5 | Gibson |  | 6113 | 5 | 5 | Filterable Particulate | 0.024333 | lb/MMBtu | Part II | 0 | UNIT5(10/6/09) | 3 |  | 10.0681 | 508 | 0.24499
6113_5 | Gibson |  | 6113 | 5 | 5 | Filterable Particulate | 0.040333 | lb/MMBtu | Part II | 0 | UNIT5(10/2/07) | 3 |  | 10.0681 | 508 | 0.40608
6113_5 | Gibson |  | 6113 | 5 | 5 | Filterable Particulate | 0.043 | lb/MMBtu | Part II | 0 | UNIT5(12/1/05) | 3 |  | 10.0681 | 508 | 0.43293
8_6 | Gorgas |  | 8 | 6 | Unit 6 | Filterable Particulate | 0.020867 | lb/MMBtu | Part II | 0 | Unit 6 Particulate Emissions Test (July 1, 2009) | 3 |  | 11.7441 | 509 | 0.24506
8_6 | Gorgas |  | 8 | 6 | Unit 6 | Filterable Particulate | 0.057377 | lb/MMBtu | Part II | 0 | Unit 6 Particulate Emissions Test (June 15, 2005) | 3 |  | 11.7441 | 509 | 0.67384
8_6 | Gorgas |  | 8 | 6 | Unit 6 | Filterable Particulate | 0.059833 | lb/MMBtu | Part II | 0 | Unit 6 Particulate Emissions Test (July 12, 2006) | 3 |  | 11.7441 | 509 | 0.70269
8_6 | Gorgas |  | 8 | 6 | Unit 6 | Filterable Particulate | 0.0614 | lb/MMBtu | Part II | 0 | Unit 6 Particulate Emissions Test (June 25, 2008) | 3 |  | 11.7441 | 509 | 0.72108
8_6 | Gorgas |  | 8 | 6 | Unit 6 | Filterable Particulate | 0.073167 | lb/MMBtu | Part II | 0 | Unit 6 CAM Test (September 6, 2007) | 3 |  | 11.7441 | 509 | 0.85927
8_6 | Gorgas |  | 8 | 6 | Unit 6 | Filterable Particulate | 0.0734 | lb/MMBtu | Part II | 0 | Unit 6 Particulate Emissions Test (July 10, 2007) | 3 |  | 11.7441 | 509 | 0.86201
3178_2 | Armstrong Power Station |  | 3178 | 2 | Unit 2 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | 06092009 | 3 |  | 9.3224 | 510 | 0.24549
2952_5 | Muskogee |  | 2952 | 5 | MK5 Config | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | Stack Sampling Report\ Muskogee 5 | 1 |  | 12.947 | 511 | 0.24599
1831_EUBoiler4 | Otto E. Eckert Station |  | 1831 | EUBoiler4 | 004 | Filterable Particulate | 0.021967 | lb/MMBtu | Part II | 0 | PM-4-9/05 | 3 |  | 11.2083 | 512 | 0.24621
2720_Boiler 6 | Buck |  | 2720 | Boiler 6 | 6 | Filterable Particulate | 0.016214 | lb/MMBtu | Part II | 0 | BLR6(2/28/07) | 7 |  | 15.475 | 513 | 0.25092
2720_Boiler 6 | Buck |  | 2720 | Boiler 6 | 6 | Filterable Particulate | 0.016967 | lb/MMBtu | Part II | 0 | BLR6(2/8/05) | 3 |  | 15.475 | 513 | 0.26256
2720_Boiler 6 | Buck |  | 2720 | Boiler 6 | 6 | Filterable Particulate | 0.02844 | lb/MMBtu | Part II | 0 | BLR6(2/27/07) | 5 |  | 15.475 | 513 | 0.44011
2720_Boiler 6 | Buck |  | 2720 | Boiler 6 | 6 | Filterable Particulate | 0.050333 | lb/MMBtu | Part II | 0 | BLR6(3/7/06) | 3 |  | 15.475 | 513 | 0.77891
2720_Boiler 6 | Buck |  | 2720 | Boiler 6 | 6 | Filterable Particulate | 0.066233 | lb/MMBtu | Part II | 0 | BLR6(1/28/09) | 3 |  | 15.475 | 513 | 1.025
2720_Boiler 6 | Buck |  | 2720 | Boiler 6 | 6 | Filterable Particulate | 0.070967 | lb/MMBtu | Part II | 0 | BLR6(1/18/08) | 3 |  | 15.475 | 513 | 1.0982
994_3 | AES Petersburg |  | 994 | 3 | 3ss | Filterable Particulate | 0.0265 | lb/MMBtu | Part II | 0 | Unit 3 - PM 07/2005 | 2 |  | 9.5517 | 514 | 0.25312
994_3 | AES Petersburg |  | 994 | 3 | 3ss | Filterable Particulate | 0.05475 | lb/MMBtu | Part II | 0 | Unit 3 - PM 07/2007 | 4 |  | 9.5517 | 514 | 0.52296
1295_1 | Quindaro |  | 1295 | 1 | Unit 1 | Filterable Particulate | 0.024933 | lb/MMBtu | Part II | 0 | PM Testing August 2009 | 3 |  | 10.1558 | 515 | 0.25322
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.021762 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (August 17, 2006) | 3 |  | 11.648 | 516 | 0.25348
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.025445 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (September 25, 2008) | 3 |  | 11.648 | 516 | 0.29638
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.030078 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Emissions Test (June 9, 2009) | 3 |  | 11.648 | 516 | 0.35035
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.031387 | lb/MMBtu | Part II | 0 | Unit 1 Particulate Emissions Test (March 3, 2005) | 3 |  | 11.648 | 516 | 0.3656
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.04127 | lb/MMBtu | Part II | 0 | Unit 1 PM Emissions Test (April 19, 2007) | 3 |  | 11.648 | 516 | 0.48071
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.069556 | lb/MMBtu | Part II | 0 | Unit 1 Reference Method PM Emissions Test 2005 | 3 |  | 11.648 | 516 | 0.81019
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.12382 | lb/MMBtu | Part II | 0 | Unit 1 CAM Test (April 20, 2007) | 4 |  | 11.648 | 516 | 1.4423
7_1 | Gadsden |  | 7 | 1 | Unit 1 | Filterable Particulate | 0.26012 | lb/MMBtu | Part II | 0 | Unit 1 CAM Test (8/18/06) | 2 |  | 11.648 | 516 | 3.0298
6138_1 | Flint Creek |  | 6138 | 1 | FC-1 | Filterable Particulate | 0.0224 | lb/MMBtu | Part II | 0 | March2006PM&CO | 1 |  | 11.3333 | 517 | 0.25387
4072_5 | Pulliam |  | 4072 | 5 | 5 | Filterable Particulate | 0.019667 | lb/MMBtu | Part II | 0 | P5 PM 2008 | 3 |  | 12.9219 | 518 | 0.25413
1379_9 | Shawnee |  | 1379 | 9 | 9 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | SHF6-9 - 04/20/2007 | 3 |  | 9.6629 | 519 | 0.25446
1379_9 | Shawnee |  | 1379 | 9 | 9 | Filterable Particulate | 0.051333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2005 | 3 |  | 9.6629 | 519 | 0.49603
1379_9 | Shawnee |  | 1379 | 9 | 9 | Filterable Particulate | 0.088333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2009 | 3 |  | 9.6629 | 519 | 0.85355
1379_9 | Shawnee |  | 1379 | 9 | 9 | Filterable Particulate | 0.19467 | lb/MMBtu | Part II | 0 | SHF6-9 - 03/29/2007 | 3 |  | 9.6629 | 519 | 1.881
1379_8 | Shawnee |  | 1379 | 8 | 8 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | SHF6-9 - 04/20/2007 | 3 |  | 9.6629 | 520 | 0.25446
1379_8 | Shawnee |  | 1379 | 8 | 8 | Filterable Particulate | 0.051333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2005 | 3 |  | 9.6629 | 520 | 0.49603
1379_8 | Shawnee |  | 1379 | 8 | 8 | Filterable Particulate | 0.088333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2009 | 3 |  | 9.6629 | 520 | 0.85355
1379_8 | Shawnee |  | 1379 | 8 | 8 | Filterable Particulate | 0.19467 | lb/MMBtu | Part II | 0 | SHF6-9 - 03/29/2007 | 3 |  | 9.6629 | 520 | 1.881
1379_7 | Shawnee |  | 1379 | 7 | 7 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | SHF6-9 - 04/20/2007 | 3 |  | 9.6629 | 521 | 0.25446
1379_7 | Shawnee |  | 1379 | 7 | 7 | Filterable Particulate | 0.051333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2005 | 3 |  | 9.6629 | 521 | 0.49603
1379_7 | Shawnee |  | 1379 | 7 | 7 | Filterable Particulate | 0.088333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2009 | 3 |  | 9.6629 | 521 | 0.85355
1379_7 | Shawnee |  | 1379 | 7 | 7 | Filterable Particulate | 0.19467 | lb/MMBtu | Part II | 0 | SHF6-9 - 03/29/2007 | 3 |  | 9.6629 | 521 | 1.881
1379_6 | Shawnee |  | 1379 | 6 | 6 | Filterable Particulate | 0.026333 | lb/MMBtu | Part II | 0 | SHF6-9 - 04/20/2007 | 3 |  | 9.6629 | 522 | 0.25446
1379_6 | Shawnee |  | 1379 | 6 | 6 | Filterable Particulate | 0.051333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2005 | 3 |  | 9.6629 | 522 | 0.49603
1379_6 | Shawnee |  | 1379 | 6 | 6 | Filterable Particulate | 0.088333 | lb/MMBtu | Part II | 0 | SHF6-10 - 2009 | 3 |  | 9.6629 | 522 | 0.85355
1379_6 | Shawnee |  | 1379 | 6 | 6 | Filterable Particulate | 0.19467 | lb/MMBtu | Part II | 0 | SHF6-9 - 03/29/2007 | 3 |  | 9.6629 | 522 | 1.881
1904_3 | Black Dog |  | 1904 | 3 | Boiler 3 | Filterable Particulate | 0.025 | lb/MMBtu | Part II | 0 | Boiler 3 & 4 PM 2008 | 1 |  | 10.2604 | 523 | 0.25651
2840_6 | Conesville |  | 2840 | 6 | CV-6 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | 0 | Oct2005PM | 1 |  | 9.216 | 524 | 0.25805
2840_6 | Conesville |  | 2840 | 6 | CV-6 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | Oct2007PM | 1 |  | 9.216 | 524 | 0.32256
2840_6 | Conesville |  | 2840 | 6 | CV-6 | Filterable Particulate | 0.037 | lb/MMBtu | Part II | 0 | May2005PM | 1 |  | 9.216 | 524 | 0.34099
2840_6 | Conesville |  | 2840 | 6 | CV-6 | Filterable Particulate | 0.039 | lb/MMBtu | Part II | 0 | Nov2007PM2 | 1 |  | 9.216 | 524 | 0.35943
2840_5 | Conesville |  | 2840 | 5 | CV-5 | Filterable Particulate | 0.028 | lb/MMBtu | Part II | 0 | Oct2005PM | 1 |  | 9.216 | 525 | 0.25805
2840_5 | Conesville |  | 2840 | 5 | CV-5 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | Oct2007PM | 1 |  | 9.216 | 525 | 0.32256
2840_5 | Conesville |  | 2840 | 5 | CV-5 | Filterable Particulate | 0.037 | lb/MMBtu | Part II | 0 | May2005PM | 1 |  | 9.216 | 525 | 0.34099
2840_5 | Conesville |  | 2840 | 5 | CV-5 | Filterable Particulate | 0.039 | lb/MMBtu | Part II | 0 | Nov2007PM2 | 1 |  | 9.216 | 525 | 0.35943
2952_4 | Muskogee |  | 2952 | 4 | MK4 Config | Filterable Particulate | 0.019 | lb/MMBtu | Part II | 0 | Stack Sampling Report\ Muskogee 4 | 1 |  | 13.7091 | 526 | 0.26047
2876_2 | Kyger Creek |  | 2876 | 2 | Unit 2 | Filterable Particulate | 0.0261 | lb/MMBtu | Part II | 0 | Unit2Particulate2007 | 1 |  | 10.0278 | 527 | 0.26173
2876_2 | Kyger Creek |  | 2876 | 2 | Unit 2 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | Unit2Particulate2005 | 1 |  | 10.0278 | 527 | 0.32089
7253_2 | Richard Gorsuch |  | 7253 | 2 | UNIT2 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | Particulate2008(1,2,4) | 3 |  | 10.3358 | 528 | 0.26184
7253_2 | Richard Gorsuch |  | 7253 | 2 | UNIT2 | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | 0 | Particulate 2006 | 3 |  | 10.3358 | 528 | 0.46856
1077_1 | Sutherland |  | 1077 | 1 | Unit 1 | Filterable Particulate | 0.0203 | lb/MMBtu | Part II | 0 | SUTH1-PM-20060516 | 1 |  | 12.9516 | 529 | 0.26292
1077_1 | Sutherland |  | 1077 | 1 | Unit 1 | Filterable Particulate | 0.0238 | lb/MMBtu | Part II | 0 | SUTH1-PM-20080716 | 1 |  | 12.9516 | 529 | 0.30825
733_2 | Kraft |  | 733 | 2 | Unit 2 | Filterable Particulate | 0.027064 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (September 20, 2006) | 3 |  | 9.8627 | 530 | 0.26693
733_2 | Kraft |  | 733 | 2 | Unit 2 | Filterable Particulate | 0.058923 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (August 27, 2008) | 3 |  | 9.8627 | 530 | 0.58114
1831_EUBoiler1 | Otto E. Eckert Station |  | 1831 | EUBoiler1 | 001 | Filterable Particulate | 0.021133 | lb/MMBtu | Part II | 0 | PM-1-9/05 | 3 |  | 12.725 | 531 | 0.26892
6257_4 | Scherer |  | 6257 | 4 | Unit 4 | Filterable Particulate | 0.02687 | lb/MMBtu | Part II | 0 | Unit 4 PM Emissions Test (January 5, 2010) | 3 |  | 10.0245 | 532 | 0.26936
54035_BLR1 | Roanoke Valley I |  | 54035 | BLR1 | Boiler 1 | Filterable Particulate | 0.028971 | lb/MMBtu | ERT | No |  | 4 | 2022 | 9.3407 | 533 | 0.27061
6004_1 | Pleasants Power Station |  | 6004 | 1 | 001 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | 7 | 1 |  | 8.5271 | 534 | 0.27287
6004_1 | Pleasants Power Station |  | 6004 | 1 | 001 | Filterable Particulate | 0.034 | lb/MMBtu | Part II | 0 | 1 | 2 |  | 8.5271 | 534 | 0.28992
3179_1 | Hatfield's Ferry Power Station |  | 3179 | 1 | 001 | Filterable Particulate | 0.028667 | lb/MMBtu | Part II | 0 | PM-CO-VOC-11/09-1 | 3 |  | 9.661 | 535 | 0.27695
3179_1 | Hatfield's Ferry Power Station |  | 3179 | 1 | 001 | Filterable Particulate | 0.032347 | lb/MMBtu | ERT | No |  | 3 | 1120 | 9.661 | 535 | 0.31251
1363_6 | Cane Run |  | 1363 | 6 | CR6 | Filterable Particulate | 0.024 | lb/MMBtu | Part II | 0 | CR6-PM-2009 | 1 |  | 11.5594 | 536 | 0.27743
1363_6 | Cane Run |  | 1363 | 6 | CR6 | Filterable Particulate | 0.031 | lb/MMBtu | Part II | 0 | CR6-PM-2008 | 1 |  | 11.5594 | 536 | 0.35834
1363_6 | Cane Run |  | 1363 | 6 | CR6 | Filterable Particulate | 0.036 | lb/MMBtu | Part II | 0 | CR6-PM-2006 | 1 |  | 11.5594 | 536 | 0.41614
1363_6 | Cane Run |  | 1363 | 6 | CR6 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | CR6-PM-2007 | 1 |  | 11.5594 | 536 | 0.46238
1363_6 | Cane Run |  | 1363 | 6 | CR6 | Filterable Particulate | 0.048 | lb/MMBtu | Part II | 0 | CR6-PM-2005 | 1 |  | 11.5594 | 536 | 0.55485
1695_4 | B.C. Cobb |  | 1695 | 4 | BCCobb4-Conf | Filterable Particulate | 0.028133 | lb/MMBtu | Part II | 0 | BCC4 - 2006 PM Testing | 3 |  | 9.9162 | 537 | 0.27897
1695_4 | B.C. Cobb |  | 1695 | 4 | BCCobb4-Conf | Filterable Particulate | 0.12287 | lb/MMBtu | Part II | 0 | BCC4 - 2009 PMTesting | 3 |  | 9.9162 | 537 | 1.2184
884_4 | Will County |  | 884 | 4 | WC4CONFIG | Filterable Particulate | 0.028842 | lb/MMBtu | ERT | No |  | 6 | 2011 | 9.6947 | 538 | 0.27961
3406_4 | Johnsonville |  | 3406 | 4 | 4 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 11.24 | 539 | 0.28475
3406_4 | Johnsonville |  | 3406 | 4 | 4 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | JOF1-10 - 2007 | 3 |  | 11.24 | 539 | 0.46084
3406_2 | Johnsonville |  | 3406 | 2 | 2 | Filterable Particulate | 0.025333 | lb/MMBtu | Part II | 0 | JOF1-10 - 2009 | 3 |  | 11.24 | 540 | 0.28475
2103_3 | Labadie |  | 2103 | 3 | 003 | Filterable Particulate | 0.0298 | lb/MMBtu | Part II | 0 | 5 | 1 |  | 9.6477 | 541 | 0.2875
1295_2 | Quindaro |  | 1295 | 2 | Unit 2 | Filterable Particulate | 0.024767 | lb/MMBtu | Part II | 0 | PM Testing August 2009 | 3 |  | 11.6361 | 542 | 0.28819
1295_2 | Quindaro |  | 1295 | 2 | Unit 2 | Filterable Particulate | 0.028344 | lb/MMBtu | ERT | No |  | 6 | 1989 | 11.6361 | 542 | 0.32981
2291_NO4 | North Omaha |  | 2291 | NO4 | NO4 | Filterable Particulate | 0.0272 | lb/MMBtu | Part II | 0 | PM Testing Unit 4 (NO4) | 1 |  | 10.644 | 543 | 0.28952
10771_10771-02 | Hopewell |  | 10771 | 10771-02 | 1 & 2 | Filterable Particulate | 0.02308 | lb/MMBtu | ERT | No |  | 3 | 1532 | 12.5735 | 544 | 0.2902
10771_10771-01 | Hopewell |  | 10771 | 10771-01 | 1 & 2 | Filterable Particulate | 0.02308 | lb/MMBtu | ERT | No |  | 3 | 1532 | 12.5735 | 545 | 0.2902
3264_3 | W. S. Lee |  | 3264 | 3 | 3 | Filterable Particulate | 0.0235 | lb/MMBtu | Part II | 0 | UNIT3(2/20/07) | 3 |  | 12.3668 | 546 | 0.29062
3264_3 | W. S. Lee |  | 3264 | 3 | 3 | Filterable Particulate | 0.0334 | lb/MMBtu | Part II | 0 | UNIT3(3/15/06) | 3 |  | 12.3668 | 546 | 0.41305
3264_3 | W. S. Lee |  | 3264 | 3 | 3 | Filterable Particulate | 0.045967 | lb/MMBtu | Part II | 0 | UNIT3(3/17/09) | 3 |  | 12.3668 | 546 | 0.56846
3264_3 | W. S. Lee |  | 3264 | 3 | 3 | Filterable Particulate | 0.059667 | lb/MMBtu | Part II | 0 | UNIT3(3/4/08) | 3 |  | 12.3668 | 546 | 0.73789
3264_3 | W. S. Lee |  | 3264 | 3 | 3 | Filterable Particulate | 0.14723 | lb/MMBtu | Part II | 0 | UNIT3(4/12/05) | 3 |  | 12.3668 | 546 | 1.8208
2843_9 | Picway |  | 2843 | 9 | PI | Filterable Particulate | 0.024 | lb/MMBtu | Part II | 0 | Sept2009PM2 | 1 |  | 12.1469 | 547 | 0.29153
2843_9 | Picway |  | 2843 | 9 | PI | Filterable Particulate | 0.0447 | lb/MMBtu | Part II | 0 | Mar2006PM | 1 |  | 12.1469 | 547 | 0.54297
2843_9 | Picway |  | 2843 | 9 | PI | Filterable Particulate | 0.048 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 12.1469 | 547 | 0.58305
2527_6 | AES Greenidge |  | 2527 | 6 | Unit 4 | Filterable Particulate | 0.029267 | lb/MMBtu | Part II | 0 | 2009 PM and H2SO4 | 3 |  | 9.9732 | 548 | 0.29188
2364_2 | Merrimack Station |  | 2364 | 2 | mk2 | Filterable Particulate | 0.03321 | lb/MMBtu | ERT | No |  | 3 | 1809 | 8.9525 | 549 | 0.29732
709_4 | Harllee Branch |  | 709 | 4 | Unit 4 | Filterable Particulate | 0.031733 | lb/MMBtu | Part II | 0 | Unit 3&4 PM Emissions Test (May 22, 2008) | 3 |  | 9.3737 | 550 | 0.29746
709_4 | Harllee Branch |  | 709 | 4 | Unit 4 | Filterable Particulate | 0.081524 | lb/MMBtu | Part II | 0 | Unit 3&4 PM Emissions Test (May 24, 2006) | 3 |  | 9.3737 | 550 | 0.76418
709_3 | Harllee Branch |  | 709 | 3 | Unit 3 | Filterable Particulate | 0.031733 | lb/MMBtu | Part II | 0 | Unit 3&4 PM Emissions Test (May 22, 2008) | 3 |  | 9.4071 | 551 | 0.29852
709_3 | Harllee Branch |  | 709 | 3 | Unit 3 | Filterable Particulate | 0.081524 | lb/MMBtu | Part II | 0 | Unit 3&4 PM Emissions Test (May 24, 2006) | 3 |  | 9.4071 | 551 | 0.76691
1733_2 | Monroe Power Plant |  | 1733 | 2 | MN2-Config | Filterable Particulate | 0.0345 | lb/MMBtu | Part II | 0 | PM2006_Mar_2 | 2 |  | 8.7607 | 552 | 0.30225
1733_2 | Monroe Power Plant |  | 1733 | 2 | MN2-Config | Filterable Particulate | 0.0705 | lb/MMBtu | Part II | 0 | PM2005_May_2 | 2 |  | 8.7607 | 552 | 0.61763
1733_2 | Monroe Power Plant |  | 1733 | 2 | MN2-Config | Filterable Particulate | 0.074333 | lb/MMBtu | Part II | 0 | PM2009_Aug12 | 3 |  | 8.7607 | 552 | 0.65121
2403_U2 | PSEG Hudson Generating Station |  | 2403 | U2 | HUDU2E2PT2OS1-Coal | Filterable Particulate | 0.030333 | lb/MMBtu | Part II | 0 | EG07044 | 3 |  | 10.0045 | 553 | 0.30347
2403_U2 | PSEG Hudson Generating Station |  | 2403 | U2 | HUDU2E2PT2OS1-Coal | Filterable Particulate | 0.044 | lb/MMBtu | Part II | 0 | EG08009 | 3 |  | 10.0045 | 553 | 0.4402
2403_U2 | PSEG Hudson Generating Station |  | 2403 | U2 | HUDU2E2PT2OS1-Coal | Filterable Particulate | 0.0505 | lb/MMBtu | Part II | 0 | EG06031A | 2 |  | 10.0045 | 553 | 0.50523
2403_U2 | PSEG Hudson Generating Station |  | 2403 | U2 | HUDU2E2PT2OS1-Coal | Filterable Particulate | 0.057667 | lb/MMBtu | Part II | 0 | EG07046 | 3 |  | 10.0045 | 553 | 0.57693
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.026867 | lb/MMBtu | Part II | 0 | UNIT3(4/9/08) | 3 |  | 11.3245 | 554 | 0.30425
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.040657 | lb/MMBtu | Part II | 0 | UNIT3(1/24/07) | 7 |  | 11.3245 | 554 | 0.46042
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.04218 | lb/MMBtu | Part II | 0 | UNIT3(1/23/07) | 5 |  | 11.3245 | 554 | 0.47767
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.05144 | lb/MMBtu | Part II | 0 | UNIT3(9/27/06) | 5 |  | 11.3245 | 554 | 0.58253
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.05305 | lb/MMBtu | Part II | 0 | UNIT3(9/26/06) | 4 |  | 11.3245 | 554 | 0.60076
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.062767 | lb/MMBtu | Part II | 0 | UNIT3(6/16/09) | 3 |  | 11.3245 | 554 | 0.7108
2723_3 | Dan River |  | 2723 | 3 | 3 | Filterable Particulate | 0.080867 | lb/MMBtu | Part II | 0 | UNIT3(2/14/06) | 3 |  | 11.3245 | 554 | 0.91577
2103_2 | Labadie |  | 2103 | 2 | 002 | Filterable Particulate | 0.0308 | lb/MMBtu | Part II | 0 | 4 | 1 |  | 9.9246 | 555 | 0.30568
50_8 | Widows Creek |  | 50 | 8 | 8 | Filterable Particulate | 0.029 | lb/MMBtu | Part II | 0 | WCF8 - 2006 | 3 |  | 10.6164 | 556 | 0.30787
50_8 | Widows Creek |  | 50 | 8 | 8 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | WCF8 - 2008 | 3 |  | 10.6164 | 556 | 0.31849
50_8 | Widows Creek |  | 50 | 8 | 8 | Filterable Particulate | 0.042 | lb/MMBtu | Part II | 0 | WCF8 - 2005 | 3 |  | 10.6164 | 556 | 0.44589
50_8 | Widows Creek |  | 50 | 8 | 8 | Filterable Particulate | 0.049667 | lb/MMBtu | Part II | 0 | WCF8 - 2007 | 3 |  | 10.6164 | 556 | 0.52728
50_8 | Widows Creek |  | 50 | 8 | 8 | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | 0 | WCF8 - 2009 | 3 |  | 10.6164 | 556 | 0.58744
7_2 | Gadsden |  | 7 | 2 | Unit 2 | Filterable Particulate | 0.025443 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (August 13, 2008) | 3 |  | 12.112 | 557 | 0.30817
7_2 | Gadsden |  | 7 | 2 | Unit 2 | Filterable Particulate | 0.028692 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (August 15, 2006) | 3 |  | 12.112 | 557 | 0.34752
7_2 | Gadsden |  | 7 | 2 | Unit 2 | Filterable Particulate | 0.040279 | lb/MMBtu | Part II | 0 | Unit 2 Particulate Emissions Test (July 7, 2005) | 3 |  | 12.112 | 557 | 0.48786
7_2 | Gadsden |  | 7 | 2 | Unit 2 | Filterable Particulate | 0.064661 | lb/MMBtu | Part II | 0 | Unit 2 PM Emissions Test (April 17, 2007) | 4 |  | 12.112 | 557 | 0.78317
7_2 | Gadsden |  | 7 | 2 | Unit 2 | Filterable Particulate | 0.11659 | lb/MMBtu | Part II | 0 | Unit 2 CAM Test (April 18, 2007) | 3 |  | 12.112 | 557 | 1.4121
7_2 | Gadsden |  | 7 | 2 | Unit 2 | Filterable Particulate | 0.12339 | lb/MMBtu | Part II | 0 | Unit 2 CAM Test (August 18, 2006) (R12) | 3 |  | 12.112 | 557 | 1.4945
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.033333 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_6e | 3 |  | 9.2674 | 558 | 0.30891
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.039333 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_6b | 3 |  | 9.2674 | 558 | 0.36452
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.042421 | lb/MMBtu | ERT | No |  | 6 | 1754 | 9.2674 | 558 | 0.39313
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.043333 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_9d | 6 |  | 9.2674 | 558 | 0.40159
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.043667 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_7 | 3 |  | 9.2674 | 558 | 0.40468
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.047667 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_8b | 3 |  | 9.2674 | 558 | 0.44175
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_4b | 3 |  | 9.2674 | 558 | 0.46337
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.059 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_1 | 3 |  | 9.2674 | 558 | 0.54678
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_11 | 3 |  | 9.2674 | 558 | 0.66107
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.071667 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_3 | 3 |  | 9.2674 | 558 | 0.66416
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.084 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_2 | 3 |  | 9.2674 | 558 | 0.77846
3251_1 | HB Robinson / Darlington Electric Power Plant |  | 3251 | 1 | Rob_Cfg_1 | Filterable Particulate | 0.13667 | lb/MMBtu | Part II | 0 | Rob_Blr_1_Test_5c | 3 |  | 9.2674 | 558 | 1.2665
2848_H-3 | O H Hutchings |  | 2848 | H-3 | H-3 | Filterable Particulate | 0.027 | lb/MMBtu | Part II | 0 | 2005 H-3 | 3 |  | 11.456 | 559 | 0.30931
2848_H-3 | O H Hutchings |  | 2848 | H-3 | H-3 | Filterable Particulate | 0.039 | lb/MMBtu | Part II | 0 | 2007 H-3 | 3 |  | 11.456 | 559 | 0.44678
2848_H-3 | O H Hutchings |  | 2848 | H-3 | H-3 | Filterable Particulate | 0.063567 | lb/MMBtu | Part II | 0 | 2009 H-3 | 3 |  | 11.456 | 559 | 0.72822
2848_H-3 | O H Hutchings |  | 2848 | H-3 | H-3 | Filterable Particulate | 0.0741 | lb/MMBtu | Part II | 0 | 2008 H-3 | 3 |  | 11.456 | 559 | 0.84889
2848_H-3 | O H Hutchings |  | 2848 | H-3 | H-3 | Filterable Particulate | 0.083333 | lb/MMBtu | Part II | 0 | 2006 H-3 | 3 |  | 11.456 | 559 | 0.95467
2848_H-2 | O H Hutchings |  | 2848 | H-2 | H-2 | Filterable Particulate | 0.028667 | lb/MMBtu | Part II | 0 | 2006 H-2 | 3 |  | 10.8302 | 560 | 0.31047
2848_H-2 | O H Hutchings |  | 2848 | H-2 | H-2 | Filterable Particulate | 0.031 | lb/MMBtu | Part II | 0 | 2007 H-2 | 3 |  | 10.8302 | 560 | 0.33574
2848_H-2 | O H Hutchings |  | 2848 | H-2 | H-2 | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | 0 | 2005 H-2 | 3 |  | 10.8302 | 560 | 0.59927
2848_H-2 | O H Hutchings |  | 2848 | H-2 | H-2 | Filterable Particulate | 0.055867 | lb/MMBtu | Part II | 0 | 2008 H-2 | 3 |  | 10.8302 | 560 | 0.60505
2848_H-2 | O H Hutchings |  | 2848 | H-2 | H-2 | Filterable Particulate | 0.065167 | lb/MMBtu | Part II | 0 | 2009 H-2 | 3 |  | 10.8302 | 560 | 0.70577
1047_4 | Lansing |  | 1047 | 4 | Unit 4 | Filterable Particulate | 0.0313 | lb/MMBtu | Part II | 0 | LANS4-PM-20060502 | 1 |  | 9.9394 | 561 | 0.3111
54634_1 | St. Nicholas Cogen Project |  | 54634 | 1 | 1 | Filterable Particulate | 0.02389 | lb/MMBtu | Part II | 0 | Particulate | 3 |  | 13.1048 | 562 | 0.31308
628_2 | Crystal River Power Plant |  | 628 | 2 | CryR_Cfg_2 | Filterable Particulate | 0.038883 | lb/MMBtu | Part II | 0 | CryR_Blr_2_Test_2 | 6 |  | 8.0796 | 563 | 0.31416
628_2 | Crystal River Power Plant |  | 628 | 2 | CryR_Cfg_2 | Filterable Particulate | 0.041283 | lb/MMBtu | Part II | 0 | CryR_Blr_2_Test_3 | 6 |  | 8.0796 | 563 | 0.33355
628_2 | Crystal River Power Plant |  | 628 | 2 | CryR_Cfg_2 | Filterable Particulate | 0.053633 | lb/MMBtu | Part II | 0 | CryR_Blr_2_Test_4 | 6 |  | 8.0796 | 563 | 0.43334
628_2 | Crystal River Power Plant |  | 628 | 2 | CryR_Cfg_2 | Filterable Particulate | 0.09983 | lb/MMBtu | Part II | 0 | CryR_Blr_2_Test_1 | 6 |  | 8.0796 | 563 | 0.80659
2876_3 | Kyger Creek |  | 2876 | 3 | Unit 3 | Filterable Particulate | 0.0313 | lb/MMBtu | Part II | 0 | Unit3Particulate2007 | 1 |  | 10.038 | 564 | 0.31419
2876_3 | Kyger Creek |  | 2876 | 3 | Unit 3 | Filterable Particulate | 0.0447 | lb/MMBtu | Part II | 0 | Unit3Particulate2005 | 1 |  | 10.038 | 564 | 0.4487
983_5 | Clifty Creek |  | 983 | 5 | Unit 5 | Filterable Particulate | 0.0312 | lb/MMBtu | Part II | 0 | Stack2Particulate2007 | 1 |  | 10.1233 | 565 | 0.31585
983_5 | Clifty Creek |  | 983 | 5 | Unit 5 | Filterable Particulate | 0.0468 | lb/MMBtu | Part II | 0 | Stack2Particulate2005 | 1 |  | 10.1233 | 565 | 0.47377
983_5 | Clifty Creek |  | 983 | 5 | Unit 5 | Filterable Particulate | 0.0485 | lb/MMBtu | Part II | 0 | Stack2Particulate2009 | 1 |  | 10.1233 | 565 | 0.49098
68029_BLR2 | AES Puerto Rico Cogeneration Facility |  | 68029 | BLR2 | Unit_2 | Filterable Particulate | 0.033002 | lb/MMBtu | ERT | No |  | 6 | 2028 | 9.6525 | 566 | 0.31856
983_6 | Clifty Creek |  | 983 | 6 | Unit 6 | Filterable Particulate | 0.0312 | lb/MMBtu | Part II | 0 | Stack2Particulate2007 | 1 |  | 10.2606 | 567 | 0.32013
983_6 | Clifty Creek |  | 983 | 6 | Unit 6 | Filterable Particulate | 0.0468 | lb/MMBtu | Part II | 0 | Stack2Particulate2005 | 1 |  | 10.2606 | 567 | 0.48019
983_6 | Clifty Creek |  | 983 | 6 | Unit 6 | Filterable Particulate | 0.0485 | lb/MMBtu | Part II | 0 | Stack2Particulate2009 | 1 |  | 10.2606 | 567 | 0.49764
1743_7 | St Clair Power Plant |  | 1743 | 7 | SC7-Config | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | PM2007_Oct7 | 2 |  | 9.7785 | 568 | 0.32269
1743_7 | St Clair Power Plant |  | 1743 | 7 | SC7-Config | Filterable Particulate | 0.067333 | lb/MMBtu | Part II | 0 | PM2007_Nov7 | 3 |  | 9.7785 | 568 | 0.65842
983_4 | Clifty Creek |  | 983 | 4 | Unit 4 | Filterable Particulate | 0.0312 | lb/MMBtu | Part II | 0 | Stack2Particulate2007 | 1 |  | 10.3464 | 569 | 0.32281
983_4 | Clifty Creek |  | 983 | 4 | Unit 4 | Filterable Particulate | 0.0468 | lb/MMBtu | Part II | 0 | Stack2Particulate2005 | 1 |  | 10.3464 | 569 | 0.48421
983_4 | Clifty Creek |  | 983 | 4 | Unit 4 | Filterable Particulate | 0.0485 | lb/MMBtu | Part II | 0 | Stack2Particulate2009 | 1 |  | 10.3464 | 569 | 0.5018
2713_3 | L.V. Sutton Electric Plant |  | 2713 | 3 | Sut_Cfg_3b | Filterable Particulate | 0.037 | lb/MMBtu | Part II | 0 | Sut_Blr_3_Test_3 | 3 |  | 8.7976 | 570 | 0.32551
2713_3 | L.V. Sutton Electric Plant |  | 2713 | 3 | Sut_Cfg_3b | Filterable Particulate | 0.044 | lb/MMBtu | Part II | 0 | Sut_Blr_3_Test_7 | 3 |  | 8.7976 | 570 | 0.3871
2713_3 | L.V. Sutton Electric Plant |  | 2713 | 3 | Sut_Cfg_3b | Filterable Particulate | 0.046 | lb/MMBtu | Part II | 0 | Sut_Blr_3_Test_5 | 3 |  | 8.7976 | 570 | 0.40469
2713_3 | L.V. Sutton Electric Plant |  | 2713 | 3 | Sut_Cfg_3b | Filterable Particulate | 0.053333 | lb/MMBtu | Part II | 0 | Sut_Blr_3_Test_4 | 3 |  | 8.7976 | 570 | 0.46921
2713_3 | L.V. Sutton Electric Plant |  | 2713 | 3 | Sut_Cfg_3b | Filterable Particulate | 0.07 | lb/MMBtu | Part II | 0 | Sut_Blr_3_Test_2 | 3 |  | 8.7976 | 570 | 0.61583
1356_1 | Ghent |  | 1356 | 1 | GH1 | Filterable Particulate | 0.027 | lb/MMBtu | Part II | 0 | GH1-PM-2009 | 1 |  | 12.0885 | 571 | 0.32639
6052_2 | Wansley |  | 6052 | 2 | Unit 2 | Filterable Particulate | 0.035764 | lb/MMBtu | Part II | 0 | Unit 2 PM Test, FGD Stack (May 20, 2009) | 3 |  | 9.2981 | 572 | 0.33254
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_6 | 3 |  | 10.1502 | 573 | 0.33496
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_10 | 3 |  | 10.1502 | 573 | 0.35526
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.037333 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_5 | 3 |  | 10.1502 | 573 | 0.37894
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_3 | 3 |  | 10.1502 | 573 | 0.40601
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_3 | 3 |  | 10.1502 | 573 | 0.52781
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.056 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_4 | 1 |  | 10.1502 | 573 | 0.56841
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_9 | 3 |  | 10.1502 | 573 | 0.60901
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.062 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_2 | 2 |  | 10.1502 | 573 | 0.62931
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.063333 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_2 | 3 |  | 10.1502 | 573 | 0.64285
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_4 | 3 |  | 10.1502 | 573 | 0.68007
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.068333 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_1 | 3 |  | 10.1502 | 573 | 0.6936
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.071 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_6 | 3 |  | 10.1502 | 573 | 0.72067
2713_2 | L.V. Sutton Electric Plant |  | 2713 | 2 | Sut_Cfg_1 | Filterable Particulate | 0.079667 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_1 | 3 |  | 10.1502 | 573 | 0.80864
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_6 | 3 |  | 10.1502 | 574 | 0.33496
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_10 | 3 |  | 10.1502 | 574 | 0.35526
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.037333 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_5 | 3 |  | 10.1502 | 574 | 0.37894
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_3 | 3 |  | 10.1502 | 574 | 0.40601
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_3 | 3 |  | 10.1502 | 574 | 0.52781
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.056 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_4 | 1 |  | 10.1502 | 574 | 0.56841
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_9 | 3 |  | 10.1502 | 574 | 0.60901
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.062 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_2 | 2 |  | 10.1502 | 574 | 0.62931
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.063333 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_2 | 3 |  | 10.1502 | 574 | 0.64285
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_4 | 3 |  | 10.1502 | 574 | 0.68007
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.068333 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_1 | 3 |  | 10.1502 | 574 | 0.6936
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.071 | lb/MMBtu | Part II | 0 | Sut_Blr_1_Test_6 | 3 |  | 10.1502 | 574 | 0.72067
2713_1 | L.V. Sutton Electric Plant |  | 2713 | 1 | Sut_Cfg_1 | Filterable Particulate | 0.079667 | lb/MMBtu | Part II | 0 | Sut_Blr_2_Test_1 | 3 |  | 10.1502 | 574 | 0.80864
1046_5 | Dubuque |  | 1046 | 5 | Unit 5 | Filterable Particulate | 0.029 | lb/MMBtu | Part II | 0 | DBQ5-PM-20051028 | 1 |  | 11.5514 | 575 | 0.33499
1046_5 | Dubuque |  | 1046 | 5 | Unit 5 | Filterable Particulate | 0.0526 | lb/MMBtu | Part II | 0 | DBQ5-PM-20051206 | 1 |  | 11.5514 | 575 | 0.6076
1046_5 | Dubuque |  | 1046 | 5 | Unit 5 | Filterable Particulate | 0.1006 | lb/MMBtu | Part II | 0 | DBQ5-PM-20051025 | 1 |  | 11.5514 | 575 | 1.1621
1364_4 | Mill Creek |  | 1364 | 4 | MC4 | Filterable Particulate | 0.03 | lb/MMBtu | Part II | 0 | MC4-PM-2005 | 1 |  | 11.2282 | 576 | 0.33685
1364_4 | Mill Creek |  | 1364 | 4 | MC4 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | MC4-PM-2009 | 1 |  | 11.2282 | 576 | 0.37053
1364_4 | Mill Creek |  | 1364 | 4 | MC4 | Filterable Particulate | 0.036 | lb/MMBtu | Part II | 0 | MC4-PM-2006 | 1 |  | 11.2282 | 576 | 0.40422
1364_4 | Mill Creek |  | 1364 | 4 | MC4 | Filterable Particulate | 0.045 | lb/MMBtu | Part II | 0 | MC4-PM-2007 | 1 |  | 11.2282 | 576 | 0.50527
10671_2b | AES Shady Point,LLC |  | 10671 | 2b | Unit 2 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | 0 | Stack Test 2008 | 8 |  | 13.8804 | 577 | 0.34105
10671_2b | AES Shady Point,LLC |  | 10671 | 2b | Unit 2 | Filterable Particulate | 0.027327 | lb/MMBtu | ERT | No |  | 6 | 2256 | 13.8804 | 577 | 0.3793
10671_2a | AES Shady Point,LLC |  | 10671 | 2a | Unit 2 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | 0 | Stack Test 2008 | 8 |  | 13.8804 | 578 | 0.34105
10671_2a | AES Shady Point,LLC |  | 10671 | 2a | Unit 2 | Filterable Particulate | 0.027327 | lb/MMBtu | ERT | No |  | 6 | 2256 | 13.8804 | 578 | 0.3793
10671_1b | AES Shady Point,LLC |  | 10671 | 1b | Unit 1 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | 0 | Stack Test 2008 | 8 |  | 13.8804 | 579 | 0.34105
10671_1b | AES Shady Point,LLC |  | 10671 | 1b | Unit 1 | Filterable Particulate | 0.027327 | lb/MMBtu | ERT | No |  | 6 | 2256 | 13.8804 | 579 | 0.3793
10671_1A | AES Shady Point,LLC |  | 10671 | 1A | Unit 1 | Filterable Particulate | 0.024571 | lb/MMBtu | Part II | 0 | Stack Test 2008 | 8 |  | 13.8804 | 580 | 0.34105
10671_1A | AES Shady Point,LLC |  | 10671 | 1A | Unit 1 | Filterable Particulate | 0.027327 | lb/MMBtu | ERT | No |  | 6 | 2256 | 13.8804 | 580 | 0.3793
50611_031 | WPS Westwood Generation, LLC |  | 50611 | 031 | 001 | Filterable Particulate | 0.02 | lb/MMBtu | Part II | 0 | 2009 PM Test | 3 |  | 17.0833 | 581 | 0.34167
1745_19 | Trenton Channel Power Plant |  | 1745 | 19 | TC16-Config | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | PM2008_JunHPc | 1 |  | 10.3966 | 582 | 0.34309
1745_19 | Trenton Channel Power Plant |  | 1745 | 19 | TC16-Config | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | 0 | PM2008_JunHPb | 3 |  | 10.3966 | 582 | 0.47131
1745_19 | Trenton Channel Power Plant |  | 1745 | 19 | TC16-Config | Filterable Particulate | 0.0465 | lb/MMBtu | Part II | 0 | PM2008_JunHPa | 2 |  | 10.3966 | 582 | 0.48344
1745_18 | Trenton Channel Power Plant |  | 1745 | 18 | TC16-Config | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | PM2008_JunHPc | 1 |  | 10.3966 | 583 | 0.34309
1745_18 | Trenton Channel Power Plant |  | 1745 | 18 | TC16-Config | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | 0 | PM2008_JunHPb | 3 |  | 10.3966 | 583 | 0.47131
1745_18 | Trenton Channel Power Plant |  | 1745 | 18 | TC16-Config | Filterable Particulate | 0.0465 | lb/MMBtu | Part II | 0 | PM2008_JunHPa | 2 |  | 10.3966 | 583 | 0.48344
1745_17 | Trenton Channel Power Plant |  | 1745 | 17 | TC16-Config | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | PM2008_JunHPc | 1 |  | 10.3966 | 584 | 0.34309
1745_17 | Trenton Channel Power Plant |  | 1745 | 17 | TC16-Config | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | 0 | PM2008_JunHPb | 3 |  | 10.3966 | 584 | 0.47131
1745_17 | Trenton Channel Power Plant |  | 1745 | 17 | TC16-Config | Filterable Particulate | 0.0465 | lb/MMBtu | Part II | 0 | PM2008_JunHPa | 2 |  | 10.3966 | 584 | 0.48344
1745_16 | Trenton Channel Power Plant |  | 1745 | 16 | TC16-Config | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | PM2008_JunHPc | 1 |  | 10.3966 | 585 | 0.34309
1745_16 | Trenton Channel Power Plant |  | 1745 | 16 | TC16-Config | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | 0 | PM2008_JunHPb | 3 |  | 10.3966 | 585 | 0.47131
1745_16 | Trenton Channel Power Plant |  | 1745 | 16 | TC16-Config | Filterable Particulate | 0.0465 | lb/MMBtu | Part II | 0 | PM2008_JunHPa | 2 |  | 10.3966 | 585 | 0.48344
4140_B5 | Alma |  | 4140 | B5 | B5 | Filterable Particulate | 0.034 | lb/MMBtu | Part II | 0 | 1 | 3 |  | 10.3311 | 586 | 0.35126
1363_4 | Cane Run |  | 1363 | 4 | CR4 | Filterable Particulate | 0.025678 | lb/MMBtu | ERT | No |  | 3 | 1826 | 13.75 | 587 | 0.35308
1363_4 | Cane Run |  | 1363 | 4 | CR4 | Filterable Particulate | 0.029 | lb/MMBtu | Part II | 0 | CR4-PM-2008 | 1 |  | 13.75 | 587 | 0.39875
1363_4 | Cane Run |  | 1363 | 4 | CR4 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | CR4-PM-2009 | 1 |  | 13.75 | 587 | 0.56375
1363_4 | Cane Run |  | 1363 | 4 | CR4 | Filterable Particulate | 0.059 | lb/MMBtu | Part II | 0 | CR4-PM-2005 | 1 |  | 13.75 | 587 | 0.81125
1363_4 | Cane Run |  | 1363 | 4 | CR4 | Filterable Particulate | 0.066 | lb/MMBtu | Part II | 0 | CR4-PM-2006 | 1 |  | 13.75 | 587 | 0.9075
1363_4 | Cane Run |  | 1363 | 4 | CR4 | Filterable Particulate | 0.068 | lb/MMBtu | Part II | 0 | CR4-PM-2007 | 1 |  | 13.75 | 587 | 0.935
2049_4 | Jack Watson |  | 2049 | 4 | Unit 4 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | PM Reports (2008) | 1 |  | 8.9074 | 588 | 0.3563
2049_4 | Jack Watson |  | 2049 | 4 | Unit 4 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | PM Reports (2006) | 1 |  | 8.9074 | 588 | 0.46319
2104_1 | Meramec |  | 2104 | 1 | 001 | Filterable Particulate | 0.0292 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 12.2344 | 589 | 0.35724
1356_3 | Ghent |  | 1356 | 3 | GH3 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | GH23-PM-2009 | 1 |  | 11.1771 | 590 | 0.35767
1356_2 | Ghent |  | 1356 | 2 | GH2 | Filterable Particulate | 0.032 | lb/MMBtu | Part II | 0 | GH23-PM-2009 | 1 |  | 11.1863 | 591 | 0.35796
3113_2 | Portland |  | 3113 | 2 | POR-2 | Filterable Particulate | 0.035933 | lb/MMBtu | Part II | 0 | P-92-U2 | 3 |  | 9.9686 | 592 | 0.35821
2876_5 | Kyger Creek |  | 2876 | 5 | Unit 5 | Filterable Particulate | 0.0361 | lb/MMBtu | Part II | 0 | Unit5Particulate2007 | 1 |  | 9.9983 | 593 | 0.36094
2876_5 | Kyger Creek |  | 2876 | 5 | Unit 5 | Filterable Particulate | 0.0547 | lb/MMBtu | Part II | 0 | Unit5Particulate2005 | 1 |  | 9.9983 | 593 | 0.54691
3776_52 | Glen Lyn |  | 3776 | 52 | GL-5 | Filterable Particulate | 0.0316 | lb/MMBtu | Part II | 0 | June2007PM | 1 |  | 11.44 | 594 | 0.3615
3776_52 | Glen Lyn |  | 3776 | 52 | GL-5 | Filterable Particulate | 0.0593 | lb/MMBtu | Part II | 0 | June2007PM2 | 1 |  | 11.44 | 594 | 0.67839
3776_51 | Glen Lyn |  | 3776 | 51 | GL-5 | Filterable Particulate | 0.0316 | lb/MMBtu | Part II | 0 | June2007PM | 1 |  | 11.44 | 595 | 0.3615
3776_51 | Glen Lyn |  | 3776 | 51 | GL-5 | Filterable Particulate | 0.0593 | lb/MMBtu | Part II | 0 | June2007PM2 | 1 |  | 11.44 | 595 | 0.67839
4078_2 | Weston |  | 4078 | 2 | W2 | Filterable Particulate | 0.032667 | lb/MMBtu | Part II | 0 | W2 PM 2009 | 3 |  | 11.2486 | 596 | 0.36745
4078_2 | Weston |  | 4078 | 2 | W2 | Filterable Particulate | 0.067333 | lb/MMBtu | Part II | 0 | W2 PM 2005 | 3 |  | 11.2486 | 596 | 0.75741
1720_7 | J.C. Weadock |  | 1720 | 7 | JCW7-Conf | Filterable Particulate | 0.039133 | lb/MMBtu | Part II | 0 | JCW7-2005 PM Testing | 3 |  | 9.3976 | 597 | 0.36776
1720_7 | J.C. Weadock |  | 1720 | 7 | JCW7-Conf | Filterable Particulate | 0.0602 | lb/MMBtu | Part II | 0 | JCW7-2008 PM Testing | 3 |  | 9.3976 | 597 | 0.56573
2840_3 | Conesville |  | 2840 | 3 | CV-3 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | Dec2005PM | 1 |  | 11.2848 | 598 | 0.3724
2840_3 | Conesville |  | 2840 | 3 | CV-3 | Filterable Particulate | 0.037 | lb/MMBtu | Part II | 0 | Dec2005PM2 | 1 |  | 11.2848 | 598 | 0.41754
2840_3 | Conesville |  | 2840 | 3 | CV-3 | Filterable Particulate | 0.049072 | lb/MMBtu | ERT | No |  | 6 | 1286 | 11.2848 | 598 | 0.55377
2840_3 | Conesville |  | 2840 | 3 | CV-3 | Filterable Particulate | 0.064 | lb/MMBtu | Part II | 0 | Nov2007PM | 1 |  | 11.2848 | 598 | 0.72223
8_7 | Gorgas |  | 8 | 7 | Unit 7 | Filterable Particulate | 0.03397 | lb/MMBtu | Part II | 0 | Unit 7 Particulate Emissions Test (July 1, 2009) | 3 |  | 11.0757 | 599 | 0.37625
8_7 | Gorgas |  | 8 | 7 | Unit 7 | Filterable Particulate | 0.034052 | lb/MMBtu | Part II | 0 | Unit 7 Particulate Emissions Test (June 16, 2005) | 3 |  | 11.0757 | 599 | 0.37716
8_7 | Gorgas |  | 8 | 7 | Unit 7 | Filterable Particulate | 0.059367 | lb/MMBtu | Part II | 0 | Unit 7 CAM Test (July 12, 2007) | 3 |  | 11.0757 | 599 | 0.65753
8_7 | Gorgas |  | 8 | 7 | Unit 7 | Filterable Particulate | 0.067533 | lb/MMBtu | Part II | 0 | Unit 7 Particulate Emissions Test (July 11, 2006) | 3 |  | 11.0757 | 599 | 0.74798
8_7 | Gorgas |  | 8 | 7 | Unit 7 | Filterable Particulate | 0.074433 | lb/MMBtu | Part II | 0 | Unit 7 Particulate Emissions Test (July 11, 2007) | 3 |  | 11.0757 | 599 | 0.8244
8_7 | Gorgas |  | 8 | 7 | Unit 7 | Filterable Particulate | 0.086933 | lb/MMBtu | Part II | 0 | Unit 7 Particulate Emissions Test (June 27, 2008) | 3 |  | 11.0757 | 599 | 0.96285
50974_#2 CFB Boiler | Scrubgrass Generating Company L.P. |  | 50974 | #2 CFB Boiler | Gen 1 | Filterable Particulate | 0.029396 | lb/MMBtu | ERT | No |  | 3 | 10000000 | 12.8866 | 600 | 0.37882
50974_#1 CFB boiler | Scrubgrass Generating Company L.P. |  | 50974 | #1 CFB boiler | Gen 1 | Filterable Particulate | 0.029396 | lb/MMBtu | ERT | No |  | 3 | 10000000 | 12.8866 | 601 | 0.37882
1364_3 | Mill Creek |  | 1364 | 3 | MC3 | Filterable Particulate | 0.033 | lb/MMBtu | Part II | 0 | MC3-PM-2006 | 1 |  | 11.6019 | 602 | 0.38286
1364_3 | Mill Creek |  | 1364 | 3 | MC3 | Filterable Particulate | 0.037 | lb/MMBtu | Part II | 0 | MC3-PM-2008 | 1 |  | 11.6019 | 602 | 0.42927
1364_3 | Mill Creek |  | 1364 | 3 | MC3 | Filterable Particulate | 0.046 | lb/MMBtu | Part II | 0 | MC3-PM-2005 | 1 |  | 11.6019 | 602 | 0.53369
1364_3 | Mill Creek |  | 1364 | 3 | MC3 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | 0 | MC3-PM-2007 | 1 |  | 11.6019 | 602 | 0.54529
1364_3 | Mill Creek |  | 1364 | 3 | MC3 | Filterable Particulate | 0.066 | lb/MMBtu | Part II | 0 | MC3-PM-2009 | 1 |  | 11.6019 | 602 | 0.76573
995_7 | Bailly |  | 995 | 7 | 7 | Filterable Particulate | 0.041243 | lb/MMBtu | Part II | 0 | BGS U#7&8 M5 09/30/2008 | 1 |  | 9.3068 | 603 | 0.38384
1082_2 | Walter Scott Jr. Energy Center |  | 1082 | 2 | 2 | Filterable Particulate | 0.039081 | lb/MMBtu | Part II | 0 | 6/2006 PM2 | 1 |  | 9.9468 | 604 | 0.38874
1082_2 | Walter Scott Jr. Energy Center |  | 1082 | 2 | 2 | Filterable Particulate | 0.089187 | lb/MMBtu | Part II | 0 | 8/2008 PM2 | 1 |  | 9.9468 | 604 | 0.88713
710_MB2 | Jack McDonough |  | 710 | MB2 | MB2 | Filterable Particulate | 0.042205 | lb/MMBtu | Part II | 0 | Units 1&2 PM Emissions Test (February 21, 2007) | 3 |  | 9.2166 | 605 | 0.38898
710_MB2 | Jack McDonough |  | 710 | MB2 | MB2 | Filterable Particulate | 0.045887 | lb/MMBtu | Part II | 0 | Units 1&2 PM Emissions Test (October 22, 2008) | 3 |  | 9.2166 | 605 | 0.42292
710_MB2 | Jack McDonough |  | 710 | MB2 | MB2 | Filterable Particulate | 0.060154 | lb/MMBtu | Part II | 0 | Units 1&2 PM Emissions Test (February 17, 2005) | 3 |  | 9.2166 | 605 | 0.55441
710_MB1 | Jack McDonough |  | 710 | MB1 | MB1 | Filterable Particulate | 0.042205 | lb/MMBtu | Part II | 0 | Units 1&2 PM Emissions Test (February 21, 2007) | 3 |  | 9.2259 | 606 | 0.38937
710_MB1 | Jack McDonough |  | 710 | MB1 | MB1 | Filterable Particulate | 0.045887 | lb/MMBtu | Part II | 0 | Units 1&2 PM Emissions Test (October 22, 2008) | 3 |  | 9.2259 | 606 | 0.42335
710_MB1 | Jack McDonough |  | 710 | MB1 | MB1 | Filterable Particulate | 0.060154 | lb/MMBtu | Part II | 0 | Units 1&2 PM Emissions Test (February 17, 2005) | 3 |  | 9.2259 | 606 | 0.55497
2723_2 | Dan River |  | 2723 | 2 | 2 | Filterable Particulate | 0.024052 | lb/MMBtu | Part II | 0 | UNIT2(7/28/05) | 3 |  | 16.1932 | 607 | 0.38948
2723_2 | Dan River |  | 2723 | 2 | 2 | Filterable Particulate | 0.029333 | lb/MMBtu | Part II | 0 | UNIT2(7/20/06) | 3 |  | 16.1932 | 607 | 0.475
2723_2 | Dan River |  | 2723 | 2 | 2 | Filterable Particulate | 0.042433 | lb/MMBtu | Part II | 0 | UNIT2(6/24/09) | 3 |  | 16.1932 | 607 | 0.68713
2723_2 | Dan River |  | 2723 | 2 | 2 | Filterable Particulate | 0.045033 | lb/MMBtu | Part II | 0 | UNIT2(9/19/07) | 3 |  | 16.1932 | 607 | 0.72923
2723_2 | Dan River |  | 2723 | 2 | 2 | Filterable Particulate | 0.11303 | lb/MMBtu | Part II | 0 | UNIT2(4/2/08) | 3 |  | 16.1932 | 607 | 1.8304
2708_6 | Cape Fear Steam Electric Plant |  | 2708 | 6 | Cap_Cfg_6b | Filterable Particulate | 0.041333 | lb/MMBtu | Part II | 0 | Cap_Blr_6_Test_6 | 3 |  | 9.5217 | 608 | 0.39357
2708_6 | Cape Fear Steam Electric Plant |  | 2708 | 6 | Cap_Cfg_6b | Filterable Particulate | 0.052667 | lb/MMBtu | Part II | 0 | Cap_Blr_6_Test_4 | 3 |  | 9.5217 | 608 | 0.50148
2708_6 | Cape Fear Steam Electric Plant |  | 2708 | 6 | Cap_Cfg_6b | Filterable Particulate | 0.062667 | lb/MMBtu | Part II | 0 | Cap_Blr_6_Test_5 | 3 |  | 9.5217 | 608 | 0.5967
2708_6 | Cape Fear Steam Electric Plant |  | 2708 | 6 | Cap_Cfg_6b | Filterable Particulate | 0.066 | lb/MMBtu | Part II | 0 | Cap_Blr_6_Test_3 | 3 |  | 9.5217 | 608 | 0.62843
2291_NO5 | North Omaha |  | 2291 | NO5 | NO5 | Filterable Particulate | 0.0376 | lb/MMBtu | Part II | 0 | PM Testing Unit 5 (NO5) | 1 |  | 10.485 | 609 | 0.39424
4140_B4 | Alma |  | 4140 | B4 | B4 | Filterable Particulate | 0.038 | lb/MMBtu | Part II | 0 | 2 | 3 |  | 10.3897 | 610 | 0.39481
1720_8 | J.C. Weadock |  | 1720 | 8 | JCW8-Conf | Filterable Particulate | 0.044733 | lb/MMBtu | Part II | 0 | 2005-JCW8 PM Testing | 3 |  | 8.8589 | 611 | 0.39629
1720_8 | J.C. Weadock |  | 1720 | 8 | JCW8-Conf | Filterable Particulate | 0.10157 | lb/MMBtu | Part II | 0 | 2008-JCW8 | 3 |  | 8.8589 | 611 | 0.89976
1048_2 | ML Kapp |  | 1048 | 2 | Unit 2 | Filterable Particulate | 0.0391 | lb/MMBtu | Part II | 0 | KAPP2-PM-20060608 | 1 |  | 10.1834 | 612 | 0.39817
1048_2 | ML Kapp |  | 1048 | 2 | Unit 2 | Filterable Particulate | 0.0577 | lb/MMBtu | Part II | 0 | KAPP2-PM-20090225 | 1 |  | 10.1834 | 612 | 0.58758
1218_2 | Fair Station |  | 1218 | 2 | U2 | Filterable Particulate | 0.038 | lb/MMBtu | Part II | 0 | TITLEVU209 | 1 |  | 10.5682 | 613 | 0.40159
1218_2 | Fair Station |  | 1218 | 2 | U2 | Filterable Particulate | 0.064561 | lb/MMBtu | ERT | No |  | 6 | 1845 | 10.5682 | 613 | 0.68229
1218_2 | Fair Station |  | 1218 | 2 | U2 | Filterable Particulate | 0.093 | lb/MMBtu | Part II | 0 | COALU206 | 1 |  | 10.5682 | 613 | 0.98284
1218_2 | Fair Station |  | 1218 | 2 | U2 | Filterable Particulate | 0.093 | lb/MMBtu | Part II | 0 | SYNFUEL06 | 1 |  | 10.5682 | 613 | 0.98284
1004_7-1 | Edwardsport |  | 1004 | 7-1 | 7-1 | Filterable Particulate | 0.033667 | lb/MMBtu | Part II | 0 | UNIT7-1(4/10/08) | 3 |  | 11.9298 | 614 | 0.40164
1004_7-1 | Edwardsport |  | 1004 | 7-1 | 7-1 | Filterable Particulate | 0.049667 | lb/MMBtu | Part II | 0 | UNIT7-1(11/15/06) | 3 |  | 11.9298 | 614 | 0.59251
2103_1 | Labadie |  | 2103 | 1 | 001 | Filterable Particulate | 0.041 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 9.8143 | 615 | 0.40239
981_4 | State Line |  | 981 | 4 | Unit 4 | Filterable Particulate | 0.04 | lb/MMBtu | Part II | 0 | Unit4_2008 | 1 |  | 10.1105 | 616 | 0.40442
981_4 | State Line |  | 981 | 4 | Unit 4 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | Unit4_2006 | 1 |  | 10.1105 | 616 | 0.60663
2709_3 | H.F. Lee Plant |  | 2709 | 3 | Lee_Cfg_3b | Filterable Particulate | 0.044 | lb/MMBtu | Part II | 0 | Lee_Blr_3_Test_9 | 3 |  | 9.2769 | 617 | 0.40818
2709_3 | H.F. Lee Plant |  | 2709 | 3 | Lee_Cfg_3b | Filterable Particulate | 0.059333 | lb/MMBtu | Part II | 0 | Lee_Blr_3_Test_7 | 3 |  | 9.2769 | 617 | 0.55043
2709_3 | H.F. Lee Plant |  | 2709 | 3 | Lee_Cfg_3b | Filterable Particulate | 0.061 | lb/MMBtu | Part II | 0 | Lee_Blr_3_Test_6 | 3 |  | 9.2769 | 617 | 0.56589
2709_3 | H.F. Lee Plant |  | 2709 | 3 | Lee_Cfg_3b | Filterable Particulate | 0.067667 | lb/MMBtu | Part II | 0 | Lee_Blr_3_Test_8 | 3 |  | 9.2769 | 617 | 0.62774
3115_2 | Titus |  | 3115 | 2 | TI-2 | Filterable Particulate | 0.039109 | lb/MMBtu | Part II | 0 | T-51 | 4 |  | 10.4408 | 618 | 0.40833
3115_2 | Titus |  | 3115 | 2 | TI-2 | Filterable Particulate | 0.045667 | lb/MMBtu | Part II | 0 | T-58 | 3 |  | 10.4408 | 618 | 0.4768
3115_2 | Titus |  | 3115 | 2 | TI-2 | Filterable Particulate | 0.10103 | lb/MMBtu | Part II | 0 | T-56 | 3 |  | 10.4408 | 618 | 1.0549
3405_1 | John Sevier |  | 3405 | 1 | 1 | Filterable Particulate | 0.041667 | lb/MMBtu | Part II | 0 | JSF1-2 - 2008 | 3 |  | 9.835 | 619 | 0.40979
527_1 | Nucla |  | 527 | 1 | 001 | Filterable Particulate | 0.043795 | lb/MMBtu | ERT | No |  | 6 | 1310 | 9.3818 | 620 | 0.41088
2850_B004 | J M Stuart |  | 2850 | B004 | MS4W | Filterable Particulate | 0.0444 | lb/MMBtu | Part II | 0 | U4PM2009 | 3 |  | 9.3098 | 621 | 0.41335
2721_1 | Cliffside |  | 2721 | 1 | 1 | Filterable Particulate | 0.026367 | lb/MMBtu | Part II | 0 | UNIT1(4/22/08) | 3 |  | 15.9753 | 622 | 0.42122
2721_1 | Cliffside |  | 2721 | 1 | 1 | Filterable Particulate | 0.0284 | lb/MMBtu | Part II | 0 | UNIT1(8/8/06) | 3 |  | 15.9753 | 622 | 0.4537
2721_1 | Cliffside |  | 2721 | 1 | 1 | Filterable Particulate | 0.0413 | lb/MMBtu | Part II | 0 | UNIT1(6/4/09) | 3 |  | 15.9753 | 622 | 0.65978
2721_1 | Cliffside |  | 2721 | 1 | 1 | Filterable Particulate | 0.055267 | lb/MMBtu | Part II | 0 | UNIT1(8/9/05) | 3 |  | 15.9753 | 622 | 0.8829
2721_1 | Cliffside |  | 2721 | 1 | 1 | Filterable Particulate | 0.063233 | lb/MMBtu | Part II | 0 | UNIT1(12/13/07) | 3 |  | 15.9753 | 622 | 1.0102
3178_1 | Armstrong Power Station |  | 3178 | 1 | Unit 1 | Filterable Particulate | 0.044333 | lb/MMBtu | Part II | 0 | 02052010 | 3 |  | 9.5054 | 623 | 0.42141
3178_1 | Armstrong Power Station |  | 3178 | 1 | Unit 1 | Filterable Particulate | 0.084 | lb/MMBtu | Part II | 0 | 06092009 | 3 |  | 9.5054 | 623 | 0.79846
728_Y5BR | Yates |  | 728 | Y5BR | Y5BR | Filterable Particulate | 0.042441 | lb/MMBtu | Part II | 0 | Units 4&5 PM Emissions Test (February 28, 2007) | 3 |  | 9.9358 | 624 | 0.42169
728_Y5BR | Yates |  | 728 | Y5BR | Y5BR | Filterable Particulate | 0.046136 | lb/MMBtu | Part II | 0 | Units 4&5 PM Emissions Test (March 2, 2005) | 3 |  | 9.9358 | 624 | 0.4584
728_Y5BR | Yates |  | 728 | Y5BR | Y5BR | Filterable Particulate | 0.065218 | lb/MMBtu | Part II | 0 | Units 4&5 PM Emissions Test (February 25, 2009) | 3 |  | 9.9358 | 624 | 0.648
889_Unit 2 | Baldwin Energy Complex |  | 889 | Unit 2 | 002 | Filterable Particulate | 0.045 | lb/MMBtu | Part II | 0 | 14 | 1 |  | 9.5478 | 625 | 0.42965
1943_002 | Hoot Lake |  | 1943 | 002 | 2 | Filterable Particulate | 0.035 | lb/MMBtu | Part II | 0 | Particulate Performance Test - Unit 2 | 3 |  | 12.3097 | 626 | 0.43084
1943_002 | Hoot Lake |  | 1943 | 002 | 2 | Filterable Particulate | 0.081055 | lb/MMBtu | ERT | No |  | 6 | 1141 | 12.3097 | 626 | 0.99777
864_5 | Meredosia |  | 864 | 5 | 005 | Filterable Particulate | 0.031807 | lb/MMBtu | ERT | No |  | 3 | 1154 | 13.6471 | 627 | 0.43407
728_Y4BR | Yates |  | 728 | Y4BR | Y4BR | Filterable Particulate | 0.042441 | lb/MMBtu | Part II | 0 | Units 4&5 PM Emissions Test (February 28, 2007) | 3 |  | 10.303 | 628 | 0.43727
728_Y4BR | Yates |  | 728 | Y4BR | Y4BR | Filterable Particulate | 0.046136 | lb/MMBtu | Part II | 0 | Units 4&5 PM Emissions Test (March 2, 2005) | 3 |  | 10.303 | 628 | 0.47535
728_Y4BR | Yates |  | 728 | Y4BR | Y4BR | Filterable Particulate | 0.065218 | lb/MMBtu | Part II | 0 | Units 4&5 PM Emissions Test (February 25, 2009) | 3 |  | 10.303 | 628 | 0.67195
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.044333 | lb/MMBtu | Part II | 0 | PAF2 - 05/23/2007 | 3 |  | 9.8849 | 629 | 0.43823
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.053667 | lb/MMBtu | Part II | 0 | PAF2 - 06/18/2008 | 3 |  | 9.8849 | 629 | 0.53049
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.057 | lb/MMBtu | Part II | 0 | PAF2 - 01/18/2008 | 3 |  | 9.8849 | 629 | 0.56344
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.057333 | lb/MMBtu | Part II | 0 | PAF2 - 08/16/2007 | 3 |  | 9.8849 | 629 | 0.56674
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.058667 | lb/MMBtu | Part II | 0 | PAF2 - 09/20/2006 | 3 |  | 9.8849 | 629 | 0.57992
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.059667 | lb/MMBtu | Part II | 0 | PAF2 - 07/17/2008 | 3 |  | 9.8849 | 629 | 0.5898
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.061667 | lb/MMBtu | Part II | 0 | PAF2 - 03/26-27/2008 | 3 |  | 9.8849 | 629 | 0.60957
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.062 | lb/MMBtu | Part II | 0 | PAF2 - 02/16/2007 | 3 |  | 9.8849 | 629 | 0.61287
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.064333 | lb/MMBtu | Part II | 0 | PAF2 - 12/16/2009 | 3 |  | 9.8849 | 629 | 0.63593
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.065 | lb/MMBtu | Part II | 0 | PAF2 - 07/11/2006 | 3 |  | 9.8849 | 629 | 0.64252
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.066333 | lb/MMBtu | Part II | 0 | PAF2 - 12/15/2005 | 3 |  | 9.8849 | 629 | 0.6557
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.069333 | lb/MMBtu | Part II | 0 | PAF2 - 02/08/2005 | 3 |  | 9.8849 | 629 | 0.68536
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.069333 | lb/MMBtu | Part II | 0 | PAF2 - 06/17/2009 | 3 |  | 9.8849 | 629 | 0.68536
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.074333 | lb/MMBtu | Part II | 0 | PAF2 - 03/09/2006 | 3 |  | 9.8849 | 629 | 0.73478
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.076667 | lb/MMBtu | Part II | 0 | PAF2 - 03/25/2009 | 3 |  | 9.8849 | 629 | 0.75785
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.078 | lb/MMBtu | Part II | 0 | PAF2 - 09/15/2005 | 3 |  | 9.8849 | 629 | 0.77103
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.079667 | lb/MMBtu | Part II | 0 | PAF2 - 12/12/2006 | 3 |  | 9.8849 | 629 | 0.7875
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.085333 | lb/MMBtu | Part II | 0 | PAF2 - 11/05/2008 | 3 |  | 9.8849 | 629 | 0.84352
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.089333 | lb/MMBtu | Part II | 0 | PAF2 - 05/26/2005 | 3 |  | 9.8849 | 629 | 0.88305
1378_2 | Paradise |  | 1378 | 2 | 2 | Filterable Particulate | 0.094667 | lb/MMBtu | Part II | 0 | PAF2 - 09/25/2009 | 3 |  | 9.8849 | 629 | 0.93577
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_2 | 3 |  | 9.4877 | 630 | 0.44592
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.048333 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_2 | 3 |  | 9.4877 | 630 | 0.45857
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_7 | 3 |  | 9.4877 | 630 | 0.47438
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.051667 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_5 | 3 |  | 9.4877 | 630 | 0.4902
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.053 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_6 | 3 |  | 9.4877 | 630 | 0.50285
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_4 | 3 |  | 9.4877 | 630 | 0.52498
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.057667 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_3 | 3 |  | 9.4877 | 630 | 0.54712
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.062 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_6 | 3 |  | 9.4877 | 630 | 0.58823
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.067667 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_1 | 3 |  | 9.4877 | 630 | 0.642
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.070667 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_5 | 3 |  | 9.4877 | 630 | 0.67046
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.073333 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_1 | 3 |  | 9.4877 | 630 | 0.69576
2709_2 | H.F. Lee Plant |  | 2709 | 2 | Lee_Cfg_1 | Filterable Particulate | 0.074 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_3 | 3 |  | 9.4877 | 630 | 0.70209
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_2 | 3 |  | 9.4877 | 631 | 0.44592
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.048333 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_2 | 3 |  | 9.4877 | 631 | 0.45857
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_7 | 3 |  | 9.4877 | 631 | 0.47438
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.051667 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_5 | 3 |  | 9.4877 | 631 | 0.4902
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.053 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_6 | 3 |  | 9.4877 | 631 | 0.50285
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_4 | 3 |  | 9.4877 | 631 | 0.52498
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.057667 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_3 | 3 |  | 9.4877 | 631 | 0.54712
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.062 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_6 | 3 |  | 9.4877 | 631 | 0.58823
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.067667 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_1 | 3 |  | 9.4877 | 631 | 0.642
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.070667 | lb/MMBtu | Part II | 0 | Lee_Blr_2_Test_5 | 3 |  | 9.4877 | 631 | 0.67046
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.073333 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_1 | 3 |  | 9.4877 | 631 | 0.69576
2709_1 | H.F. Lee Plant |  | 2709 | 1 | Lee_Cfg_1 | Filterable Particulate | 0.074 | lb/MMBtu | Part II | 0 | Lee_Blr_1_Test_3 | 3 |  | 9.4877 | 631 | 0.70209
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.045333 | lb/MMBtu | Part II | 0 | PAF1 - 05/24/2007 | 3 |  | 9.8849 | 632 | 0.44812
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.051 | lb/MMBtu | Part II | 0 | PAF1 - 07/18/2008 | 3 |  | 9.8849 | 632 | 0.50413
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.051 | lb/MMBtu | Part II | 0 | PAF1 - 12/17/2009 | 3 |  | 9.8849 | 632 | 0.50413
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.053 | lb/MMBtu | Part II | 0 | PAF1 - 01/17/2008 | 3 |  | 9.8849 | 632 | 0.5239
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.056 | lb/MMBtu | Part II | 0 | PAF1 - 07/15/2009 | 3 |  | 9.8849 | 632 | 0.55356
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.057333 | lb/MMBtu | Part II | 0 | PAF1 - 08/15/2007 | 3 |  | 9.8849 | 632 | 0.56674
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.059667 | lb/MMBtu | Part II | 0 | PAF1 - 09/23/2009 | 3 |  | 9.8849 | 632 | 0.5898
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.060667 | lb/MMBtu | Part II | 0 | PAF1 - 02/14-15/2007 | 3 |  | 9.8849 | 632 | 0.59969
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.062333 | lb/MMBtu | Part II | 0 | PAF1 - 03/31/2008 | 3 |  | 9.8849 | 632 | 0.61616
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.062333 | lb/MMBtu | Part II | 0 | PAF1 - 06/13/2006 | 3 |  | 9.8849 | 632 | 0.61616
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.065333 | lb/MMBtu | Part II | 0 | PAF1 - 12/14/2005 | 3 |  | 9.8849 | 632 | 0.64582
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.065667 | lb/MMBtu | Part II | 0 | PAF1 - 02/09/2005 | 3 |  | 9.8849 | 632 | 0.64911
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.066667 | lb/MMBtu | Part II | 0 | PAF1 - 03/08/2006 | 3 |  | 9.8849 | 632 | 0.659
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.066667 | lb/MMBtu | Part II | 0 | PAF1 - 11/06/2008 | 3 |  | 9.8849 | 632 | 0.659
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.075 | lb/MMBtu | Part II | 0 | PAF1 - 09/19/2006 | 3 |  | 9.8849 | 632 | 0.74137
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.076 | lb/MMBtu | Part II | 0 | PAF1 - 03/26/2009 | 3 |  | 9.8849 | 632 | 0.75126
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.079333 | lb/MMBtu | Part II | 0 | PAF1 - 06/11/2008 | 3 |  | 9.8849 | 632 | 0.78421
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.081667 | lb/MMBtu | Part II | 0 | PAF1 - 12/21/2006 | 3 |  | 9.8849 | 632 | 0.80727
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.085 | lb/MMBtu | Part II | 0 | PAF1 - 05/25/2005 | 3 |  | 9.8849 | 632 | 0.84022
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.089667 | lb/MMBtu | Part II | 0 | PAF1 - 09/14/2005 | 3 |  | 9.8849 | 632 | 0.88635
1378_1 | Paradise |  | 1378 | 1 | 1 | Filterable Particulate | 0.095 | lb/MMBtu | Part II | 0 | PAF1 - 06/18/2009 | 3 |  | 9.8849 | 632 | 0.93907
2723_1 | Dan River |  | 2723 | 1 | 1 | Filterable Particulate | 0.027967 | lb/MMBtu | Part II | 0 | UNIT1(7/18/06) | 3 |  | 16.0563 | 633 | 0.44904
2723_1 | Dan River |  | 2723 | 1 | 1 | Filterable Particulate | 0.035267 | lb/MMBtu | Part II | 0 | UNIT1(9/18/07) | 3 |  | 16.0563 | 633 | 0.56625
2723_1 | Dan River |  | 2723 | 1 | 1 | Filterable Particulate | 0.050433 | lb/MMBtu | Part II | 0 | UNIT1(7/26/05) | 3 |  | 16.0563 | 633 | 0.80977
2723_1 | Dan River |  | 2723 | 1 | 1 | Filterable Particulate | 0.0675 | lb/MMBtu | Part II | 0 | UNIT1(6/23/09) | 3 |  | 16.0563 | 633 | 1.0838
2723_1 | Dan River |  | 2723 | 1 | 1 | Filterable Particulate | 0.13847 | lb/MMBtu | Part II | 0 | UNIT1(4/1/08) | 3 |  | 16.0563 | 633 | 2.2233
2876_1 | Kyger Creek |  | 2876 | 1 | Unit 1 | Filterable Particulate | 0.0463 | lb/MMBtu | Part II | 0 | Unit1Particulate2007 | 1 |  | 9.8664 | 634 | 0.45681
2876_1 | Kyger Creek |  | 2876 | 1 | Unit 1 | Filterable Particulate | 0.0528 | lb/MMBtu | Part II | 0 | Unit1Particulate2005 | 1 |  | 9.8664 | 634 | 0.52095
2872_4 | Muskingum River |  | 2872 | 4 | MR-4 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | 0 | Nov2009PM | 1 |  | 9.0526 | 635 | 0.45806
2872_4 | Muskingum River |  | 2872 | 4 | MR-4 | Filterable Particulate | 0.0533 | lb/MMBtu | Part II | 0 | Sept2008 | 1 |  | 9.0526 | 635 | 0.48251
2872_4 | Muskingum River |  | 2872 | 4 | MR-4 | Filterable Particulate | 0.0576 | lb/MMBtu | Part II | 0 | Jan2007PM | 1 |  | 9.0526 | 635 | 0.52143
2872_4 | Muskingum River |  | 2872 | 4 | MR-4 | Filterable Particulate | 0.064 | lb/MMBtu | Part II | 0 | Nov2006PM | 1 |  | 9.0526 | 635 | 0.57937
2872_4 | Muskingum River |  | 2872 | 4 | MR-4 | Filterable Particulate | 0.0673 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 9.0526 | 635 | 0.60924
2872_4 | Muskingum River |  | 2872 | 4 | MR-4 | Filterable Particulate | 0.08 | lb/MMBtu | Part II | 0 | Dec2008PM | 1 |  | 9.0526 | 635 | 0.72421
2872_3 | Muskingum River |  | 2872 | 3 | MR-3 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | 0 | Nov2009PM | 1 |  | 9.0526 | 636 | 0.45806
2872_3 | Muskingum River |  | 2872 | 3 | MR-3 | Filterable Particulate | 0.0533 | lb/MMBtu | Part II | 0 | Sept2008 | 1 |  | 9.0526 | 636 | 0.48251
2872_3 | Muskingum River |  | 2872 | 3 | MR-3 | Filterable Particulate | 0.0576 | lb/MMBtu | Part II | 0 | Jan2007PM | 1 |  | 9.0526 | 636 | 0.52143
2872_3 | Muskingum River |  | 2872 | 3 | MR-3 | Filterable Particulate | 0.064 | lb/MMBtu | Part II | 0 | Nov2006PM | 1 |  | 9.0526 | 636 | 0.57937
2872_3 | Muskingum River |  | 2872 | 3 | MR-3 | Filterable Particulate | 0.0673 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 9.0526 | 636 | 0.60924
2872_3 | Muskingum River |  | 2872 | 3 | MR-3 | Filterable Particulate | 0.08 | lb/MMBtu | Part II | 0 | Dec2008PM | 1 |  | 9.0526 | 636 | 0.72421
54081_3B | Spruance Genco, LLC |  | 54081 | 3B | GEN3 | Filterable Particulate | 0.035662 | lb/MMBtu | ERT | No |  | 3 | 134611 | 13.0662 | 637 | 0.46597
54081_3A | Spruance Genco, LLC |  | 54081 | 3A | GEN3 | Filterable Particulate | 0.035662 | lb/MMBtu | ERT | No |  | 3 | 134611 | 13.0662 | 638 | 0.46597
2720_Boiler 5 | Buck |  | 2720 | Boiler 5 | 5 | Filterable Particulate | 0.0303 | lb/MMBtu | Part II | 0 | BLR5(3/7/06) | 3 |  | 15.475 | 639 | 0.46889
2720_Boiler 5 | Buck |  | 2720 | Boiler 5 | 5 | Filterable Particulate | 0.033908 | lb/MMBtu | Part II | 0 | BLR5(1/28/09) | 3 |  | 15.475 | 639 | 0.52473
2720_Boiler 5 | Buck |  | 2720 | Boiler 5 | 5 | Filterable Particulate | 0.039567 | lb/MMBtu | Part II | 0 | BLR5(2/8/05) | 3 |  | 15.475 | 639 | 0.61229
2720_Boiler 5 | Buck |  | 2720 | Boiler 5 | 5 | Filterable Particulate | 0.061567 | lb/MMBtu | Part II | 0 | BLR5(3/1/07) | 3 |  | 15.475 | 639 | 0.95274
2720_Boiler 5 | Buck |  | 2720 | Boiler 5 | 5 | Filterable Particulate | 0.0829 | lb/MMBtu | Part II | 0 | BLR5(1/18/08) | 3 |  | 15.475 | 639 | 1.2829
2872_2 | Muskingum River |  | 2872 | 2 | MR-2 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | 0 | Nov2009PM | 1 |  | 9.3352 | 640 | 0.47236
2872_2 | Muskingum River |  | 2872 | 2 | MR-2 | Filterable Particulate | 0.0533 | lb/MMBtu | Part II | 0 | Sept2008 | 1 |  | 9.3352 | 640 | 0.49756
2872_2 | Muskingum River |  | 2872 | 2 | MR-2 | Filterable Particulate | 0.0576 | lb/MMBtu | Part II | 0 | Jan2007PM | 1 |  | 9.3352 | 640 | 0.5377
2872_2 | Muskingum River |  | 2872 | 2 | MR-2 | Filterable Particulate | 0.064 | lb/MMBtu | Part II | 0 | Nov2006PM | 1 |  | 9.3352 | 640 | 0.59745
2872_2 | Muskingum River |  | 2872 | 2 | MR-2 | Filterable Particulate | 0.0673 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 9.3352 | 640 | 0.62826
2872_2 | Muskingum River |  | 2872 | 2 | MR-2 | Filterable Particulate | 0.08 | lb/MMBtu | Part II | 0 | Dec2008PM | 1 |  | 9.3352 | 640 | 0.74681
2872_1 | Muskingum River |  | 2872 | 1 | MR-1 | Filterable Particulate | 0.0506 | lb/MMBtu | Part II | 0 | Nov2009PM | 1 |  | 9.3352 | 641 | 0.47236
2872_1 | Muskingum River |  | 2872 | 1 | MR-1 | Filterable Particulate | 0.0533 | lb/MMBtu | Part II | 0 | Sept2008 | 1 |  | 9.3352 | 641 | 0.49756
2872_1 | Muskingum River |  | 2872 | 1 | MR-1 | Filterable Particulate | 0.0576 | lb/MMBtu | Part II | 0 | Jan2007PM | 1 |  | 9.3352 | 641 | 0.5377
2872_1 | Muskingum River |  | 2872 | 1 | MR-1 | Filterable Particulate | 0.064 | lb/MMBtu | Part II | 0 | Nov2006PM | 1 |  | 9.3352 | 641 | 0.59745
2872_1 | Muskingum River |  | 2872 | 1 | MR-1 | Filterable Particulate | 0.0673 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 9.3352 | 641 | 0.62826
2872_1 | Muskingum River |  | 2872 | 1 | MR-1 | Filterable Particulate | 0.08 | lb/MMBtu | Part II | 0 | Dec2008PM | 1 |  | 9.3352 | 641 | 0.74681
1733_1 | Monroe Power Plant |  | 1733 | 1 | MN1-Config | Filterable Particulate | 0.055 | lb/MMBtu | Part II | 0 | PM2005_Apr_1 | 2 |  | 8.8148 | 642 | 0.48481
1733_1 | Monroe Power Plant |  | 1733 | 1 | MN1-Config | Filterable Particulate | 0.074333 | lb/MMBtu | Part II | 0 | PM2009_Aug12 | 3 |  | 8.8148 | 642 | 0.65523
3775_1 | Clinch River |  | 3775 | 1 | CR-1 | Filterable Particulate | 0.05312 | lb/MMBtu | ERT | No |  | 6 | 10040002 | 9.1343 | 643 | 0.48522
2720_Boiler 7 | Buck |  | 2720 | Boiler 7 | 7 | Filterable Particulate | 0.031367 | lb/MMBtu | Part II | 0 | BLR7(6/1/05) | 3 |  | 15.475 | 644 | 0.4854
2720_Boiler 7 | Buck |  | 2720 | Boiler 7 | 7 | Filterable Particulate | 0.056167 | lb/MMBtu | Part II | 0 | BLR7(3/1/07) | 3 |  | 15.475 | 644 | 0.86918
2720_Boiler 7 | Buck |  | 2720 | Boiler 7 | 7 | Filterable Particulate | 0.0745 | lb/MMBtu | Part II | 0 | BLR7(3/14/06) | 3 |  | 15.475 | 644 | 1.1529
2720_Boiler 7 | Buck |  | 2720 | Boiler 7 | 7 | Filterable Particulate | 0.085933 | lb/MMBtu | Part II | 0 | BLR7(1/17/08) | 3 |  | 15.475 | 644 | 1.3298
2720_Boiler 7 | Buck |  | 2720 | Boiler 7 | 7 | Filterable Particulate | 0.53813 | lb/MMBtu | Part II | 0 | BLR7(1/29/09) | 3 |  | 15.475 | 644 | 8.3276
2049_5 | Jack Watson |  | 2049 | 5 | Unit 5 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | PM Reports (2008) | 1 |  | 9.5057 | 645 | 0.4943
2049_5 | Jack Watson |  | 2049 | 5 | Unit 5 | Filterable Particulate | 0.061 | lb/MMBtu | Part II | 0 | PM Reports (2006) | 1 |  | 9.5057 | 645 | 0.57985
1364_1 | Mill Creek |  | 1364 | 1 | MC1 | Filterable Particulate | 0.044 | lb/MMBtu | Part II | 0 | MC1-PM-2006 | 1 |  | 11.2818 | 646 | 0.4964
1364_1 | Mill Creek |  | 1364 | 1 | MC1 | Filterable Particulate | 0.057 | lb/MMBtu | Part II | 0 | MC1-PM-2009 | 1 |  | 11.2818 | 646 | 0.64306
1364_1 | Mill Creek |  | 1364 | 1 | MC1 | Filterable Particulate | 0.065 | lb/MMBtu | Part II | 0 | MC1-PM-2005 | 1 |  | 11.2818 | 646 | 0.73332
1364_1 | Mill Creek |  | 1364 | 1 | MC1 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | MC1-PM-2007 | 1 |  | 11.2818 | 646 | 0.75588
889_Unit 1 | Baldwin Energy Complex |  | 889 | Unit 1 | 001 | Filterable Particulate | 0.054 | lb/MMBtu | Part II | 0 | 13 | 1 |  | 9.4121 | 647 | 0.50826
1364_2 | Mill Creek |  | 1364 | 2 | MC2 | Filterable Particulate | 0.045 | lb/MMBtu | Part II | 0 | MC2-PM-2009 | 1 |  | 11.4788 | 648 | 0.51655
1364_2 | Mill Creek |  | 1364 | 2 | MC2 | Filterable Particulate | 0.049 | lb/MMBtu | Part II | 0 | MC2-PM-2006 | 1 |  | 11.4788 | 648 | 0.56246
1364_2 | Mill Creek |  | 1364 | 2 | MC2 | Filterable Particulate | 0.052 | lb/MMBtu | Part II | 0 | MC2-PM-2007 | 1 |  | 11.4788 | 648 | 0.5969
1364_2 | Mill Creek |  | 1364 | 2 | MC2 | Filterable Particulate | 0.057 | lb/MMBtu | Part II | 0 | MC2-PM-2005 | 1 |  | 11.4788 | 648 | 0.65429
1364_2 | Mill Creek |  | 1364 | 2 | MC2 | Filterable Particulate | 0.066 | lb/MMBtu | Part II | 0 | MC2-PM-2008 | 1 |  | 11.4788 | 648 | 0.7576
2712_3B | Roxboro Steam Electric Plant |  | 2712 | 3B | Rox_Cfg_3b | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | 0 | Rox_Unit_3_Test_5 | 3 |  | 9.3387 | 649 | 0.51674
2712_3B | Roxboro Steam Electric Plant |  | 2712 | 3B | Rox_Cfg_3b | Filterable Particulate | 0.074833 | lb/MMBtu | Part II | 0 | Rox_Unit_3_Test_7p | 3 |  | 9.3387 | 649 | 0.69885
2712_3A | Roxboro Steam Electric Plant |  | 2712 | 3A | Rox_Cfg_3b | Filterable Particulate | 0.055333 | lb/MMBtu | Part II | 0 | Rox_Unit_3_Test_5 | 3 |  | 9.3387 | 650 | 0.51674
2712_3A | Roxboro Steam Electric Plant |  | 2712 | 3A | Rox_Cfg_3b | Filterable Particulate | 0.074833 | lb/MMBtu | Part II | 0 | Rox_Unit_3_Test_7p | 3 |  | 9.3387 | 650 | 0.69885
4078_1 | Weston |  | 4078 | 1 | W1 | Filterable Particulate | 0.038333 | lb/MMBtu | Part II | 0 | W1 PM 2009 | 3 |  | 13.4906 | 651 | 0.51714
4078_1 | Weston |  | 4078 | 1 | W1 | Filterable Particulate | 0.064333 | lb/MMBtu | Part II | 0 | W1 PM 2005 | 3 |  | 13.4906 | 651 | 0.86789
2721_2 | Cliffside |  | 2721 | 2 | 2 | Filterable Particulate | 0.0328 | lb/MMBtu | Part II | 0 | UNIT2(4/24/08) | 3 |  | 15.8578 | 652 | 0.52014
2721_2 | Cliffside |  | 2721 | 2 | 2 | Filterable Particulate | 0.043867 | lb/MMBtu | Part II | 0 | UNIT2(8/14/07) | 3 |  | 15.8578 | 652 | 0.69563
2721_2 | Cliffside |  | 2721 | 2 | 2 | Filterable Particulate | 0.046333 | lb/MMBtu | Part II | 0 | UNIT2(6/4/09) | 3 |  | 15.8578 | 652 | 0.73475
2721_2 | Cliffside |  | 2721 | 2 | 2 | Filterable Particulate | 0.0621 | lb/MMBtu | Part II | 0 | UNIT2(8/10/06) | 3 |  | 15.8578 | 652 | 0.98477
2721_2 | Cliffside |  | 2721 | 2 | 2 | Filterable Particulate | 0.071067 | lb/MMBtu | Part II | 0 | UNIT2(8/11/05) | 3 |  | 15.8578 | 652 | 1.127
2790_B1 | R.M. Heskett Station |  | 2790 | B1 | B1 | Filterable Particulate | 0.036 | lb/MMBtu | Part II | 0 | 2 | 1 |  | 14.5455 | 653 | 0.52364
1831_EUBoiler6 | Otto E. Eckert Station |  | 1831 | EUBoiler6 | 006 | Filterable Particulate | 0.047 | lb/MMBtu | Part II | 0 | PM-6-9/05 | 3 |  | 11.3662 | 654 | 0.53421
883_8 | Waukegan |  | 883 | 8 | WK8CONFIG | Filterable Particulate | 0.051664 | lb/MMBtu | ERT | No |  | 6 | 2013 | 10.3418 | 655 | 0.5343
6639_G2 | R D Green |  | 6639 | G2 | 2 | Filterable Particulate | 0.046919 | lb/MMBtu | ERT | No |  | 6 | 1276 | 11.4084 | 656 | 0.53527
997_12 | Michigan City |  | 997 | 12 | 12 | Filterable Particulate | 0.057922 | lb/MMBtu | Part II | 0 | MCGS U#12 M5 06/03/08 | 1 |  | 9.3939 | 657 | 0.54412
997_12 | Michigan City |  | 997 | 12 | 12 | Filterable Particulate | 0.09173 | lb/MMBtu | Part II | 0 | MCGS U#12 M5 04/11/2006 | 1 |  | 9.3939 | 657 | 0.8617
997_12 | Michigan City |  | 997 | 12 | 12 | Filterable Particulate | 0.10031 | lb/MMBtu | ERT | No |  | 6 | 828 | 9.3939 | 657 | 0.94232
2721_4 | Cliffside |  | 2721 | 4 | 4 | Filterable Particulate | 0.0442 | lb/MMBtu | Part II | 0 | UNIT4(6/2/09) | 3 |  | 12.4424 | 658 | 0.54995
2721_4 | Cliffside |  | 2721 | 4 | 4 | Filterable Particulate | 0.051867 | lb/MMBtu | Part II | 0 | UNIT4(4/29/08) | 3 |  | 12.4424 | 658 | 0.64535
2721_4 | Cliffside |  | 2721 | 4 | 4 | Filterable Particulate | 0.052033 | lb/MMBtu | Part II | 0 | UNIT4(8/9/07) | 3 |  | 12.4424 | 658 | 0.64742
2721_4 | Cliffside |  | 2721 | 4 | 4 | Filterable Particulate | 0.068567 | lb/MMBtu | Part II | 0 | UNIT4(8/18/05) | 3 |  | 12.4424 | 658 | 0.85313
2721_4 | Cliffside |  | 2721 | 4 | 4 | Filterable Particulate | 0.15243 | lb/MMBtu | Part II | 0 | UNIT4(8/15/06) | 3 |  | 12.4424 | 658 | 1.8966
8023_1 | Columbia |  | 8023 | 1 | Unit 1 | Filterable Particulate | 0.0539 | lb/MMBtu | Part II | 0 | COL1-PM-20070907 | 1 |  | 10.3168 | 659 | 0.55607
6147_2 | Monticello |  | 6147 | 2 | 2 | Filterable Particulate | 0.047418 | lb/MMBtu | ERT | No |  | 6 | 879456 | 12.0069 | 660 | 0.56934
2716_3 | W.H. Weatherspoon Plant |  | 2716 | 3 | Wea_Cfg_3 | Filterable Particulate | 0.047333 | lb/MMBtu | Part II | 0 | Wea_Blr_3_Test_6 | 3 |  | 12.1772 | 661 | 0.57639
2716_3 | W.H. Weatherspoon Plant |  | 2716 | 3 | Wea_Cfg_3 | Filterable Particulate | 0.065333 | lb/MMBtu | Part II | 0 | Wea_Blr_3_Test_3 | 3 |  | 12.1772 | 661 | 0.79558
2716_3 | W.H. Weatherspoon Plant |  | 2716 | 3 | Wea_Cfg_3 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | Wea_Blr_3_Test_4 | 3 |  | 12.1772 | 661 | 0.86864
2716_3 | W.H. Weatherspoon Plant |  | 2716 | 3 | Wea_Cfg_3 | Filterable Particulate | 0.073667 | lb/MMBtu | Part II | 0 | Wea_Blr_3_Test_1 | 3 |  | 12.1772 | 661 | 0.89705
2716_3 | W.H. Weatherspoon Plant |  | 2716 | 3 | Wea_Cfg_3 | Filterable Particulate | 0.073667 | lb/MMBtu | Part II | 0 | Wea_Blr_3_Test_5 | 3 |  | 12.1772 | 661 | 0.89705
2716_3 | W.H. Weatherspoon Plant |  | 2716 | 3 | Wea_Cfg_3 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | 0 | Wea_Blr_3_Test_2 | 3 |  | 12.1772 | 661 | 1.0959
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.0661 | lb/MMBtu | Part II | 0 | Dec2009PM | 1 |  | 8.9554 | 662 | 0.59195
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1072 | lb/MMBtu | Part II | 0 | March2009PM | 1 |  | 8.9554 | 662 | 0.96002
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1133 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 8.9554 | 662 | 1.0147
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1277 | lb/MMBtu | Part II | 0 | May2009PM | 1 |  | 8.9554 | 662 | 1.1436
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1567 | lb/MMBtu | Part II | 0 | Dec2009nonCOMP2 | 1 |  | 8.9554 | 662 | 1.4033
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1688 | lb/MMBtu | Part II | 0 | July2008PM2 | 1 |  | 8.9554 | 662 | 1.5117
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1692 | lb/MMBtu | Part II | 0 | Sept2008 | 1 |  | 8.9554 | 662 | 1.5153
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1741 | lb/MMBtu | Part II | 0 | Sept2009nonCOMP2 | 1 |  | 8.9554 | 662 | 1.5591
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1757 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 8.9554 | 662 | 1.5735
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.1983 | lb/MMBtu | Part II | 0 | June2008PM | 1 |  | 8.9554 | 662 | 1.7759
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.207 | lb/MMBtu | Part II | 0 | Oct2008nonCOMP2 | 1 |  | 8.9554 | 662 | 1.8538
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.2548 | lb/MMBtu | Part II | 0 | Sept2009nonCOMP | 1 |  | 8.9554 | 662 | 2.2818
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.2646 | lb/MMBtu | Part II | 0 | Oct2008PMnonCOMP | 1 |  | 8.9554 | 662 | 2.3696
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.2653 | lb/MMBtu | Part II | 0 | July2008PM1 | 1 |  | 8.9554 | 662 | 2.3759
1353_BSU1 | Big Sandy |  | 1353 | BSU1 | BSU-1 | Filterable Particulate | 0.2702 | lb/MMBtu | Part II | 0 | Dec2009nonCOMP | 1 |  | 8.9554 | 662 | 2.4198
1010_6 | Wabash River |  | 1010 | 6 | 6 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | STACKA091509 | 3 |  | 8.9446 | 663 | 0.59929
1010_6 | Wabash River |  | 1010 | 6 | 6 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | STACKA091807 | 3 |  | 8.9446 | 663 | 0.63805
1010_6 | Wabash River |  | 1010 | 6 | 6 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | 0 | STACKA09202005 | 3 |  | 8.9446 | 663 | 0.80502
1010_6 | Wabash River |  | 1010 | 6 | 6 | Filterable Particulate | 0.10993 | lb/MMBtu | ERT | No |  | 3 | 1636 | 8.9446 | 663 | 0.98331
1891_2 | Laskin Energy Center |  | 1891 | 2 | LEC2 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | 0 | GE-PM_CO-7-2009 | 1 |  | 12 | 664 | 0.6
1891_2 | Laskin Energy Center |  | 1891 | 2 | LEC2 | Filterable Particulate | 0.075 | lb/MMBtu | Part II | 0 | GE_PM-2-7-2007 | 2 |  | 12 | 664 | 0.9
1891_1 | Laskin Energy Center |  | 1891 | 1 | LEC1 | Filterable Particulate | 0.05 | lb/MMBtu | Part II | 0 | GE-PM_CO-7-2009 | 1 |  | 12.0833 | 665 | 0.60417
1891_1 | Laskin Energy Center |  | 1891 | 1 | LEC1 | Filterable Particulate | 0.075 | lb/MMBtu | Part II | 0 | GE_PM-2-7-2007 | 2 |  | 12.0833 | 665 | 0.90625
1893_4 | Boswell Energy Center |  | 1893 | 4 | BEC4 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | 1,2,3,4-May2007-PM | 1 |  | 10.1226 | 666 | 0.60735
728_Y2BR | Yates |  | 728 | Y2BR | Y2BR | Filterable Particulate | 0.056667 | lb/MMBtu | Part II | 0 | Units 2&3 PM Emissions Test (2/28/07) | 3 |  | 11.16 | 667 | 0.63241
728_Y2BR | Yates |  | 728 | Y2BR | Y2BR | Filterable Particulate | 0.09356 | lb/MMBtu | Part II | 0 | Units 2&3 PM Emissions Test (March 1, 2005) | 3 |  | 11.16 | 667 | 1.0441
728_Y2BR | Yates |  | 728 | Y2BR | Y2BR | Filterable Particulate | 0.097634 | lb/MMBtu | Part II | 0 | Units 2&3 PMEmissions Test (February 25, 2009) | 3 |  | 11.16 | 667 | 1.0896
874_5 | Joliet 9 |  | 874 | 5 | JOL5 CONFIG | Filterable Particulate | 0.058706 | lb/MMBtu | ERT | No |  | 6 | 2009 | 10.9582 | 668 | 0.64332
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.0661 | lb/MMBtu | Part II | 0 | Dec2009PM | 1 |  | 9.8925 | 669 | 0.65389
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1072 | lb/MMBtu | Part II | 0 | March2009PM | 1 |  | 9.8925 | 669 | 1.0605
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1133 | lb/MMBtu | Part II | 0 | Feb2009PM | 1 |  | 9.8925 | 669 | 1.1208
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1277 | lb/MMBtu | Part II | 0 | May2009PM | 1 |  | 9.8925 | 669 | 1.2633
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1567 | lb/MMBtu | Part II | 0 | Dec2009nonCOMP2 | 1 |  | 9.8925 | 669 | 1.5502
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1688 | lb/MMBtu | Part II | 0 | July2008PM2 | 1 |  | 9.8925 | 669 | 1.6699
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1692 | lb/MMBtu | Part II | 0 | Sept2008 | 1 |  | 9.8925 | 669 | 1.6738
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1741 | lb/MMBtu | Part II | 0 | Sept2009nonCOMP2 | 1 |  | 9.8925 | 669 | 1.7223
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1757 | lb/MMBtu | Part II | 0 | Sept2009PM | 1 |  | 9.8925 | 669 | 1.7381
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.1983 | lb/MMBtu | Part II | 0 | June2008PM | 1 |  | 9.8925 | 669 | 1.9617
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.207 | lb/MMBtu | Part II | 0 | Oct2008nonCOMP2 | 1 |  | 9.8925 | 669 | 2.0477
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.2548 | lb/MMBtu | Part II | 0 | Sept2009nonCOMP | 1 |  | 9.8925 | 669 | 2.5206
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.2646 | lb/MMBtu | Part II | 0 | Oct2008PMnonCOMP | 1 |  | 9.8925 | 669 | 2.6176
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.2653 | lb/MMBtu | Part II | 0 | July2008PM1 | 1 |  | 9.8925 | 669 | 2.6245
1353_BSU2 | Big Sandy |  | 1353 | BSU2 | BSU-2 | Filterable Particulate | 0.2702 | lb/MMBtu | Part II | 0 | Dec2009nonCOMP | 1 |  | 9.8925 | 669 | 2.673
3992_9 | Blount Street |  | 3992 | 9 | 9B7T | Filterable Particulate | 0.0608 | lb/MMBtu | Part II | 0 | M083603 | 3 |  | 10.8083 | 670 | 0.65714
2187_2 | JE Corette Plant |  | 2187 | 2 | Corette1 | Filterable Particulate | 0.061333 | lb/MMBtu | Part II | 0 | Dec2009_PM | 3 |  | 10.7362 | 671 | 0.65849
3131_2 | Shawville |  | 3131 | 2 | SHAW2-2 | Filterable Particulate | 0.0612 | lb/MMBtu | Part II | 0 | SH-184-U2 | 3 |  | 10.792 | 672 | 0.66047
728_Y3BR | Yates |  | 728 | Y3BR | Y3BR | Filterable Particulate | 0.056667 | lb/MMBtu | Part II | 0 | Units 2&3 PM Emissions Test (2/28/07) | 3 |  | 11.9115 | 673 | 0.67499
728_Y3BR | Yates |  | 728 | Y3BR | Y3BR | Filterable Particulate | 0.09356 | lb/MMBtu | Part II | 0 | Units 2&3 PM Emissions Test (March 1, 2005) | 3 |  | 11.9115 | 673 | 1.1144
728_Y3BR | Yates |  | 728 | Y3BR | Y3BR | Filterable Particulate | 0.097634 | lb/MMBtu | Part II | 0 | Units 2&3 PMEmissions Test (February 25, 2009) | 3 |  | 11.9115 | 673 | 1.163
3942_1 | Albright Power Station |  | 3942 | 1 | Unit_1 | Filterable Particulate | 0.069563 | lb/MMBtu | ERT | No |  | 3 | 1111 | 9.7037 | 674 | 0.67502
2721_3 | Cliffside |  | 2721 | 3 | 3 | Filterable Particulate | 0.054633 | lb/MMBtu | Part II | 0 | UNIT3(8/16/05) | 3 |  | 12.4043 | 675 | 0.67769
2721_3 | Cliffside |  | 2721 | 3 | 3 | Filterable Particulate | 0.070633 | lb/MMBtu | Part II | 0 | UNIT3(8/7/07) | 3 |  | 12.4043 | 675 | 0.87616
2721_3 | Cliffside |  | 2721 | 3 | 3 | Filterable Particulate | 0.0746 | lb/MMBtu | Part II | 0 | UNIT3(4/30/08) | 3 |  | 12.4043 | 675 | 0.92536
2721_3 | Cliffside |  | 2721 | 3 | 3 | Filterable Particulate | 0.075533 | lb/MMBtu | Part II | 0 | UNIT3(8/22/06) | 3 |  | 12.4043 | 675 | 0.93694
2721_3 | Cliffside |  | 2721 | 3 | 3 | Filterable Particulate | 0.090233 | lb/MMBtu | Part II | 0 | UNIT3(6/2/09) | 3 |  | 12.4043 | 675 | 1.1193
1010_4 | Wabash River |  | 1010 | 4 | 4 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | STACKA091509 | 3 |  | 10.2633 | 676 | 0.68764
1010_4 | Wabash River |  | 1010 | 4 | 4 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | STACKA091807 | 3 |  | 10.2633 | 676 | 0.73211
1010_4 | Wabash River |  | 1010 | 4 | 4 | Filterable Particulate | 0.10993 | lb/MMBtu | ERT | No |  | 3 | 1636 | 10.2633 | 676 | 1.1283
1010_3 | Wabash River |  | 1010 | 3 | 3 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | STACKA091509 | 3 |  | 10.2633 | 677 | 0.68764
1010_3 | Wabash River |  | 1010 | 3 | 3 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | STACKA091807 | 3 |  | 10.2633 | 677 | 0.73211
1010_3 | Wabash River |  | 1010 | 3 | 3 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | 0 | STACKA09202005 | 3 |  | 10.2633 | 677 | 0.9237
1010_2 | Wabash River |  | 1010 | 2 | 2 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | STACKA091509 | 3 |  | 10.2633 | 678 | 0.68764
1010_2 | Wabash River |  | 1010 | 2 | 2 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | STACKA091807 | 3 |  | 10.2633 | 678 | 0.73211
1010_2 | Wabash River |  | 1010 | 2 | 2 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | 0 | STACKA09202005 | 3 |  | 10.2633 | 678 | 0.9237
1004_7-2 | Edwardsport |  | 1004 | 7-2 | 7-2 | Filterable Particulate | 0.058 | lb/MMBtu | Part II | 0 | UNIT7-2(12/7/06) | 3 |  | 11.9298 | 679 | 0.69193
1004_7-2 | Edwardsport |  | 1004 | 7-2 | 7-2 | Filterable Particulate | 0.127 | lb/MMBtu | Part II | 0 | UNIT7-2(4/8/08) | 3 |  | 11.9298 | 679 | 1.5151
1010_5 | Wabash River |  | 1010 | 5 | 5 | Filterable Particulate | 0.067 | lb/MMBtu | Part II | 0 | STACKA091509 | 3 |  | 10.4766 | 680 | 0.70193
1010_5 | Wabash River |  | 1010 | 5 | 5 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | STACKA091807 | 3 |  | 10.4766 | 680 | 0.74733
1010_5 | Wabash River |  | 1010 | 5 | 5 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | 0 | STACKA09202005 | 3 |  | 10.4766 | 680 | 0.9429
59_1 | Platte |  | 59 | 1 | 1 | Filterable Particulate | 0.076767 | lb/MMBtu | Part II | 0 | Particulate Emission Compliance Study 2006 | 3 |  | 9.5273 | 681 | 0.73138
1058_5 | Sixth Street |  | 1058 | 5 | Unit 5 | Filterable Particulate | 0.0613 | lb/MMBtu | Part II | 0 | SXTH5-PM-20050419 | 1 |  | 12.0433 | 682 | 0.73826
1091_2 | George Neal North |  | 1091 | 2 | 2 | Filterable Particulate | 0.078311 | lb/MMBtu | Part II | 0 | 7/13/2006-PM | 1 |  | 9.48 | 683 | 0.74239
1091_2 | George Neal North |  | 1091 | 2 | 2 | Filterable Particulate | 0.094067 | lb/MMBtu | Part II | 0 | 7/16/2008-PM | 1 |  | 9.48 | 683 | 0.89175
3295_URQ3 | Urquhart |  | 3295 | URQ3 | URQ003 | Filterable Particulate | 0.0761 | lb/MMBtu | Part II | 0 | PM-02/05 | 1 |  | 10.1748 | 684 | 0.7743
3295_URQ3 | Urquhart |  | 3295 | URQ3 | URQ003 | Filterable Particulate | 0.0903 | lb/MMBtu | Part II | 0 | PM-11/06 | 1 |  | 10.1748 | 684 | 0.91878
3295_URQ3 | Urquhart |  | 3295 | URQ3 | URQ003 | Filterable Particulate | 0.14648 | lb/MMBtu | ERT | No |  | 3 | 1455 | 10.1748 | 684 | 1.4904
3295_URQ3 | Urquhart |  | 3295 | URQ3 | URQ003 | Filterable Particulate | 0.2058 | lb/MMBtu | Part II | 0 | PM-09/08 | 1 |  | 10.1748 | 684 | 2.094
3295_URQ3 | Urquhart |  | 3295 | URQ3 | URQ003 | Filterable Particulate | 0.2276 | lb/MMBtu | Part II | 0 | PM-08/09 | 1 |  | 10.1748 | 684 | 2.3158
3295_URQ3 | Urquhart |  | 3295 | URQ3 | URQ003 | Filterable Particulate | 0.2671 | lb/MMBtu | Part II | 0 | PM-11/07 | 1 |  | 10.1748 | 684 | 2.7177
3264_1 | W. S. Lee |  | 3264 | 1 | 1 | Filterable Particulate | 0.069233 | lb/MMBtu | Part II | 0 | UNIT1(3/10/09) | 3 |  | 11.4731 | 685 | 0.79432
3264_1 | W. S. Lee |  | 3264 | 1 | 1 | Filterable Particulate | 0.078267 | lb/MMBtu | Part II | 0 | UNIT1(2/21/07) | 3 |  | 11.4731 | 685 | 0.89796
3264_1 | W. S. Lee |  | 3264 | 1 | 1 | Filterable Particulate | 0.084833 | lb/MMBtu | Part II | 0 | UNIT1(2/26/08) | 3 |  | 11.4731 | 685 | 0.9733
3264_1 | W. S. Lee |  | 3264 | 1 | 1 | Filterable Particulate | 0.13477 | lb/MMBtu | Part II | 0 | UNIT1(4/26/05) | 3 |  | 11.4731 | 685 | 1.5462
3264_1 | W. S. Lee |  | 3264 | 1 | 1 | Filterable Particulate | 0.22187 | lb/MMBtu | Part II | 0 | UNIT1(3/14/06) | 3 |  | 11.4731 | 685 | 2.5455
1361_5 | Tyrone |  | 1361 | 5 | TY3 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | TY3-PM-06272008 | 1 |  | 13.2667 | 686 | 0.796
1361_5 | Tyrone |  | 1361 | 5 | TY3 | Filterable Particulate | 0.07 | lb/MMBtu | Part II | 0 | TY3-PM-07082008 | 1 |  | 13.2667 | 686 | 0.92867
1361_5 | Tyrone |  | 1361 | 5 | TY3 | Filterable Particulate | 0.24 | lb/MMBtu | Part II | 0 | TY3-PM-06252008 | 1 |  | 13.2667 | 686 | 3.184
3264_2 | W. S. Lee |  | 3264 | 2 | 2 | Filterable Particulate | 0.0714 | lb/MMBtu | Part II | 0 | UNIT2(4/19/05) | 3 |  | 11.4839 | 687 | 0.81995
3264_2 | W. S. Lee |  | 3264 | 2 | 2 | Filterable Particulate | 0.0992 | lb/MMBtu | Part II | 0 | UNIT2(3/12/09) | 3 |  | 11.4839 | 687 | 1.1392
3264_2 | W. S. Lee |  | 3264 | 2 | 2 | Filterable Particulate | 0.11717 | lb/MMBtu | Part II | 0 | UNIT2(2/27/08) | 3 |  | 11.4839 | 687 | 1.3455
3264_2 | W. S. Lee |  | 3264 | 2 | 2 | Filterable Particulate | 0.13377 | lb/MMBtu | Part II | 0 | UNIT2(3/9/06) | 3 |  | 11.4839 | 687 | 1.5362
3264_2 | W. S. Lee |  | 3264 | 2 | 2 | Filterable Particulate | 0.1458 | lb/MMBtu | Part II | 0 | UNIT2(2/23/07) | 3 |  | 11.4839 | 687 | 1.6744
3122_2 | Homer City Station |  | 3122 | 2 | HC2CONFIG | Filterable Particulate | 0.095333 | lb/MMBtu | Part II | 0 | HC2 Apr 2009 PM Test | 3 |  | 8.6879 | 688 | 0.82824
3122_2 | Homer City Station |  | 3122 | 2 | HC2CONFIG | Filterable Particulate | 0.11033 | lb/MMBtu | Part II | 0 | HC2 Jan 2009 PM Test | 3 |  | 8.6879 | 688 | 0.95856
1695_5 | B.C. Cobb |  | 1695 | 5 | BCCobb5-Conf | Filterable Particulate | 0.086633 | lb/MMBtu | Part II | 0 | BCC5 - 2009 PM Testing | 3 |  | 9.6896 | 689 | 0.83944
1695_5 | B.C. Cobb |  | 1695 | 5 | BCCobb5-Conf | Filterable Particulate | 0.14523 | lb/MMBtu | Part II | 0 | BCC5-2006 PM Testing | 3 |  | 9.6896 | 689 | 1.4072
1252_10 | Tecumseh Energy Center |  | 1252 | 10 | 10 | Filterable Particulate | 0.08577 | lb/MMBtu | Part II | 0 | CAM 0507/10 | 10 |  | 9.8138 | 690 | 0.84173
1384_2 | Cooper Station. |  | 1384 | 2 | Unit 02 | Filterable Particulate | 0.083667 | lb/MMBtu | Part II | 0 | U2_PM_05/22/07 | 3 |  | 10.075 | 691 | 0.84294
1384_2 | Cooper Station. |  | 1384 | 2 | Unit 02 | Filterable Particulate | 0.099 | lb/MMBtu | Part II | 0 | U1&2_PM_10/10/07 | 3 |  | 10.075 | 691 | 0.99743
1831_EUBoiler2 | Otto E. Eckert Station |  | 1831 | EUBoiler2 | 002 | Filterable Particulate | 0.0617 | lb/MMBtu | Part II | 0 | PM-2-9/05 | 3 |  | 13.7368 | 692 | 0.84756
1004_8-1 | Edwardsport |  | 1004 | 8-1 | 8-1 | Filterable Particulate | 0.071333 | lb/MMBtu | Part II | 0 | UNIT8-1(4/9/08) | 3 |  | 11.9298 | 693 | 0.85099
1004_8-1 | Edwardsport |  | 1004 | 8-1 | 8-1 | Filterable Particulate | 0.104 | lb/MMBtu | Part II | 0 | UNIT8-1(12/7/06) | 3 |  | 11.9298 | 693 | 1.2407
1357_4 | Green River |  | 1357 | 4 | GR03 | Filterable Particulate | 0.06 | lb/MMBtu | Part II | 0 | GR3-PM-2008 | 1 |  | 14.5417 | 694 | 0.8725
1046_1 | Dubuque |  | 1046 | 1 | Unit 1 | Filterable Particulate | 0.0558 | lb/MMBtu | Part II | 0 | DBQ1-PM-20051206 | 1 |  | 16.1117 | 695 | 0.89903
1046_1 | Dubuque |  | 1046 | 1 | Unit 1 | Filterable Particulate | 0.1562 | lb/MMBtu | Part II | 0 | DBQ1-PM-20051026 | 1 |  | 16.1117 | 695 | 2.5166
1250_4 | Lawrence Energy Center |  | 1250 | 4 | 4 | Filterable Particulate | 0.089552 | lb/MMBtu | Part II | 0 | CAM 1007/4 | 58 |  | 10.127 | 696 | 0.90689
1897_3 | Hibbard Energy Center |  | 1897 | 3 | HREC3 | Filterable Particulate | 0.061333 | lb/MMBtu | Part II | 0 | PM_CO-Boiler3 | 3 |  | 14.8 | 697 | 0.90773
1058_4 | Sixth Street |  | 1058 | 4 | Unit 4 | Filterable Particulate | 0.0445 | lb/MMBtu | Part II | 0 | SXTH4-PM-20060623 | 1 |  | 20.5405 | 698 | 0.91405
1058_4 | Sixth Street |  | 1058 | 4 | Unit 4 | Filterable Particulate | 0.0516 | lb/MMBtu | Part II | 0 | SXTH4-PM-20050420 | 1 |  | 20.5405 | 698 | 1.0599
963_33 | Dallman |  | 963 | 33 | 33 | Filterable Particulate | 0.096 | lb/MMBtu | Part II | 0 | Dallman 33 PM.CO Test | 1 |  | 10.0471 | 699 | 0.96452
3122_1 | Homer City Station |  | 3122 | 1 | HC1CONFIG | Filterable Particulate | 0.108 | lb/MMBtu | Part II | 0 | HC1 Jan 2009 PM Test | 3 |  | 9.0056 | 700 | 0.97261
3319_3 | Jefferies |  | 3319 | 3 | J3 | Filterable Particulate | 0.09 | lb/MMBtu | Part II | 0 | J3PM2005 | 1 |  | 10.8537 | 701 | 0.97683
3319_3 | Jefferies |  | 3319 | 3 | J3 | Filterable Particulate | 0.092 | lb/MMBtu | Part II | 0 | J3PM2006R | 1 |  | 10.8537 | 701 | 0.99854
3319_3 | Jefferies |  | 3319 | 3 | J3 | Filterable Particulate | 0.095 | lb/MMBtu | Part II | 0 | J3PM2006 | 1 |  | 10.8537 | 701 | 1.0311
3319_3 | Jefferies |  | 3319 | 3 | J3 | Filterable Particulate | 0.228 | lb/MMBtu | Part II | 0 | J3PM2008 | 1 |  | 10.8537 | 701 | 2.4746
3319_3 | Jefferies |  | 3319 | 3 | J3 | Filterable Particulate | 0.29 | lb/MMBtu | Part II | 0 | J3PM2007 | 1 |  | 10.8537 | 701 | 3.1476
3319_3 | Jefferies |  | 3319 | 3 | J3 | Filterable Particulate | 0.486 | lb/MMBtu | Part II | 0 | J3PM2009 | 1 |  | 10.8537 | 701 | 5.2749
1058_3 | Sixth Street |  | 1058 | 3 | Unit 3 | Filterable Particulate | 0.0449 | lb/MMBtu | Part II | 0 | SXTH3-PM-20060412 | 1 |  | 21.8705 | 702 | 0.98199
2169_2 | Chamois Power Plant |  | 2169 | 2 | Unit 2 | Filterable Particulate | 0.091667 | lb/MMBtu | Part II | 0 | PM052005 | 3 |  | 11.26 | 703 | 1.0322
1357_5 | Green River |  | 1357 | 5 | GR04 | Filterable Particulate | 0.08 | lb/MMBtu | Part II | 0 | GR4-PM-2008 | 1 |  | 13.4706 | 704 | 1.0776
1239_39 | Riverton |  | 1239 | 39 | 039 | Filterable Particulate | 0.1012 | lb/MMBtu | Part II | 0 | 1 | 1 |  | 10.65 | 705 | 1.0778
1384_1 | Cooper Station. |  | 1384 | 1 | Unit 01 | Filterable Particulate | 0.099 | lb/MMBtu | Part II | 0 | U1&2_PM_10/10/07 | 3 |  | 11.1371 | 706 | 1.1026
1384_1 | Cooper Station. |  | 1384 | 1 | Unit 01 | Filterable Particulate | 0.11433 | lb/MMBtu | Part II | 0 | U1_PM_05/08/07 | 3 |  | 11.1371 | 706 | 1.2733
1831_EUBoiler3 | Otto E. Eckert Station |  | 1831 | EUBoiler3 | 003 | Filterable Particulate | 0.0914 | lb/MMBtu | Part II | 0 | PM-3-9/05 | 3 |  | 13.05 | 707 | 1.1928
3317_2 | Dolphus M Grainger |  | 3317 | 2 | G2 | Filterable Particulate | 0.11 | lb/MMBtu | Part II | 0 | G2PM2007 | 1 |  | 11.1724 | 708 | 1.229
3317_2 | Dolphus M Grainger |  | 3317 | 2 | G2 | Filterable Particulate | 0.247 | lb/MMBtu | Part II | 0 | G2PM2008 | 1 |  | 11.1724 | 708 | 2.7596
3317_2 | Dolphus M Grainger |  | 3317 | 2 | G2 | Filterable Particulate | 0.247 | lb/MMBtu | Part II | 0 | G2PM2009 | 1 |  | 11.1724 | 708 | 2.7596
3317_2 | Dolphus M Grainger |  | 3317 | 2 | G2 | Filterable Particulate | 0.253 | lb/MMBtu | Part II | 0 | G2PM2006 | 1 |  | 11.1724 | 708 | 2.8266
3317_2 | Dolphus M Grainger |  | 3317 | 2 | G2 | Filterable Particulate | 0.36 | lb/MMBtu | Part II | 0 | G2PM2005 | 1 |  | 11.1724 | 708 | 4.0221
1385_2 | Dale Station |  | 1385 | 2 | 02 | Filterable Particulate | 0.109 | lb/MMBtu | Part II | 0 | U1_2_PM_12/20/06 | 3 |  | 11.5833 | 709 | 1.2626
1385_1 | Dale Station |  | 1385 | 1 | 01 | Filterable Particulate | 0.109 | lb/MMBtu | Part II | 0 | U1_2_PM_12/20/06 | 3 |  | 11.5833 | 710 | 1.2626
2098_6 | Lake Road |  | 2098 | 6 | 6 | Filterable Particulate | 0.12926 | lb/MMBtu | ERT | No |  | 3 | 892 | 9.899 | 711 | 1.2795
3280_CAN1 | Canadys Steam |  | 3280 | CAN1 | CAN001 | Filterable Particulate | 0.1431 | lb/MMBtu | Part II | 0 | PM-02/06-CAN1 | 1 |  | 9.4339 | 712 | 1.35
3280_CAN1 | Canadys Steam |  | 3280 | CAN1 | CAN001 | Filterable Particulate | 0.1453 | lb/MMBtu | Part II | 0 | PM-12/08-CAN1 | 1 |  | 9.4339 | 712 | 1.3707
3280_CAN1 | Canadys Steam |  | 3280 | CAN1 | CAN001 | Filterable Particulate | 0.2586 | lb/MMBtu | Part II | 0 | PM-03/05-CAN1 | 1 |  | 9.4339 | 712 | 2.4396
3280_CAN1 | Canadys Steam |  | 3280 | CAN1 | CAN001 | Filterable Particulate | 0.2955 | lb/MMBtu | Part II | 0 | PM-01/07-CAN1 | 1 |  | 9.4339 | 712 | 2.7877
3317_1 | Dolphus M Grainger |  | 3317 | 1 | G1 | Filterable Particulate | 0.13 | lb/MMBtu | Part II | 0 | G1PM2005 | 1 |  | 10.8046 | 713 | 1.4046
3317_1 | Dolphus M Grainger |  | 3317 | 1 | G1 | Filterable Particulate | 0.23 | lb/MMBtu | Part II | 0 | G1PM2007 | 1 |  | 10.8046 | 713 | 2.4851
3317_1 | Dolphus M Grainger |  | 3317 | 1 | G1 | Filterable Particulate | 0.252 | lb/MMBtu | Part II | 0 | G1PM2009 | 1 |  | 10.8046 | 713 | 2.7228
3317_1 | Dolphus M Grainger |  | 3317 | 1 | G1 | Filterable Particulate | 0.29 | lb/MMBtu | Part II | 0 | G1PM2008 | 1 |  | 10.8046 | 713 | 3.1333
3317_1 | Dolphus M Grainger |  | 3317 | 1 | G1 | Filterable Particulate | 0.337 | lb/MMBtu | Part II | 0 | G1PM2006 | 1 |  | 10.8046 | 713 | 3.6411
1043_2SG1 | Frank E. Ratts |  | 1043 | 2SG1 | 2SG1conf1 | Filterable Particulate | 0.167 | lb/MMBtu | Part II | 0 | 2008R2PM | 3 |  | 8.7176 | 714 | 1.4558
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.15 | lb/MMBtu | Part II | 0 | J4PM2005 | 1 |  | 9.8889 | 715 | 1.4833
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.188 | lb/MMBtu | Part II | 0 | J4PM2005R | 1 |  | 9.8889 | 715 | 1.8591
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.192 | lb/MMBtu | Part II | 0 | J4PM2009 | 1 |  | 9.8889 | 715 | 1.8987
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.206 | lb/MMBtu | Part II | 0 | J4PM2005RR | 1 |  | 9.8889 | 715 | 2.0371
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.24 | lb/MMBtu | Part II | 0 | J4PM2007 | 1 |  | 9.8889 | 715 | 2.3733
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.313 | lb/MMBtu | Part II | 0 | J4PM2008 | 1 |  | 9.8889 | 715 | 3.0952
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.32 | lb/MMBtu | Part II | 0 | J4PM2006 | 1 |  | 9.8889 | 715 | 3.1644
3319_4 | Jefferies |  | 3319 | 4 | J4 | Filterable Particulate | 0.36 | lb/MMBtu | Part II | 0 | J4PM2006R | 1 |  | 9.8889 | 715 | 3.56
3992_8 | Blount Street |  | 3992 | 8 | 8B6T | Filterable Particulate | 0.14437 | lb/MMBtu | Part II | 0 | M083808 | 3 |  | 10.7678 | 716 | 1.5545
1082_1 | Walter Scott Jr. Energy Center |  | 1082 | 1 | 1 | Filterable Particulate | 0.10687 | lb/MMBtu | Part II | 0 | 6/2006 PM3 | 1 |  | 14.5778 | 717 | 1.5579
1082_1 | Walter Scott Jr. Energy Center |  | 1082 | 1 | 1 | Filterable Particulate | 0.16215 | lb/MMBtu | Part II | 0 | 11/2008 PM1 | 1 |  | 14.5778 | 717 | 2.3638
1943_003 | Hoot Lake |  | 1943 | 003 | 3 | Filterable Particulate | 0.13467 | lb/MMBtu | Part II | 0 | Particulate Engineering/Parametric Test | 3 |  | 11.721 | 718 | 1.5784
1943_003 | Hoot Lake |  | 1943 | 003 | 3 | Filterable Particulate | 0.22667 | lb/MMBtu | Part II | 0 | Particulate Performance Test - Unit 3 | 3 |  | 11.721 | 718 | 2.6568
1091_1 | George Neal North |  | 1091 | 1 | 1 | Filterable Particulate | 0.17052 | lb/MMBtu | Part II | 0 | 7/17/2008 | 1 |  | 9.4 | 719 | 1.6029
1091_1 | George Neal North |  | 1091 | 1 | 1 | Filterable Particulate | 0.2754 | lb/MMBtu | Part II | 0 | 7/12/2006-PM | 1 |  | 9.4 | 719 | 2.5887
1383_R1 | Robert A Reid |  | 1383 | R1 | 1 | Filterable Particulate | 0.195 | lb/MMBtu | Part II | 0 | R1 Compliance 2006 | 3 |  | 8.5639 | 720 | 1.67
2161_3 | James River Power Station |  | 2161 | 3 | Unit_3_JRPS | Filterable Particulate | 0.15331 | lb/MMBtu | Part II | 0 | PM Emissions\181-020 | 13 |  | 11.2727 | 721 | 1.7282
1239_40 | Riverton |  | 1239 | 40 | 040 | Filterable Particulate | 0.1827 | lb/MMBtu | Part II | 0 | 3 | 1 |  | 10.3448 | 722 | 1.89
1047_3 | Lansing |  | 1047 | 3 | Unit 3 | Filterable Particulate | 0.1461 | lb/MMBtu | Part II | 0 | LANS3-PM-20060427 | 1 |  | 14.1975 | 723 | 2.0743
1047_3 | Lansing |  | 1047 | 3 | Unit 3 | Filterable Particulate | 0.242 | lb/MMBtu | Part II | 0 | LANS3-PM-20080618 | 1 |  | 14.1975 | 723 | 3.4358
1218_1 | Fair Station |  | 1218 | 1 | U1 | Filterable Particulate | 0.17 | lb/MMBtu | Part II | 0 | TITLEV09U1 | 1 |  | 13.4694 | 724 | 2.2898
1218_1 | Fair Station |  | 1218 | 1 | U1 | Filterable Particulate | 0.27 | lb/MMBtu | Part II | 0 | TITLEV07U1 | 1 |  | 13.4694 | 724 | 3.6367
1058_2 | Sixth Street |  | 1058 | 2 | Unit 2 | Filterable Particulate | 0.1157 | lb/MMBtu | Part II | 0 | SXTH2-PM-20060406 | 1 |  | 22.8571 | 725 | 2.6446
1131_7 | Streeter Station |  | 1131 | 7 | 7 | Filterable Particulate | 0.219 | lb/MMBtu | Part II | 0 | 2006 Stack Test | 3 |  | 12.3177 | 726 | 2.6976
3982_5 | Bay Front |  | 3982 | 5 | 5 | Filterable Particulate | 0.225 | lb/MMBtu | Part II | 0 | PM Compliance 2006 | 1 |  | 12.1562 | 727 | 2.7352
3982_5 | Bay Front |  | 3982 | 5 | 5 | Filterable Particulate | 0.2536 | lb/MMBtu | Part II | 0 | PM Compliance 2008 | 1 |  | 12.1562 | 727 | 3.0828

## Lognormal Template
Emissions (lb/MW)
Averages | 8223 Springerville 3
1 | 0.0054331
2 | 0.0093333
3 | 0.016707
4 | 0.0168
5 | 0.041067
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
Use for small sample sets that are Lognormal.
Testing Normality | Raw Data | Log Data
Sample Size | 5 | 5
Kurtosis | 2.8081 | 0.27582
SE Kurtosis | 1.0954 | 1.0954
Result Kurtosis | non normal | normal
Skewness | 1.556 | 0.22168
SE Skewness | 0.91287 | 0.91287
Result Skewness | normal | normal
1. Take LN( ) of Raw Data
Averages
1 | -5.2153
2 | -4.6742
3 | -4.0919
4 | -4.0864
5 | -3.1926
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
2. Calculate sample size, n= |  | 5
Average of Raw Data |  | 0.017868
3. Calculate |  |  | -4.2521
0.57038
4. Calculate
5. m |  | 1
6. Calculate
a- Numerator first term |  |  |  |  | 27.2499
b- denominator first term |  |  |  |  | 0.59128
46.0864
7. Calculate
3.305
8. Go to tab distribution for 99 percentile "lognormal distribution 99%"
9. substitue the values of |  |  |  | in cell D7 and F7 respectively
10. In column AE indentify the value that is the smallest value that is larger than 0.99, note what row number this is. | [6 empty] | 93 | is the Row number in Column AE with the first value > 0.99.
11. In column B, go down to the row number from Step 10. above, and copy the z value. | [6 empty] | 3.484 | z value from "lognormal distribution 99%"
12. calculate the UPL using the formula
a- Calculate |  |  | 0.018933
b- Calculate |  |  | 0.00035845
c- Calculate |  |  | 0.76895
d-calculate |  |  |  | 0.15474
e- Calculate | [5 empty] | 0.018196
f- Calculate UPL |  |  | 0.082327 | lb fPM/MW

## lognormal distribution 99 %
distribution of Z
Normal
distribution
∆z | z | [6 empty] | Absolute values
[10 empty] | Cumulative | normalization
0.101 |  |  | 46.0864 | 3.305
| -5 | =f(a) |  |  | 798.5459 | 1.4867e-06 | 0.0011872 | 0.0011872 | 5.9954e-05 | 5.9954e-05 | 1.1407e-05 |  | 9
1 | -4.899 |  |  |  | 725.2865 | 2.4509e-06 | 0.0017776 | 0.0017776 | 0.00017954 | 0.0002395 | 4.5567e-05 |  | 10
2 | -4.798 |  |  |  | 656.9169 | 3.9995e-06 | 0.0026273 | 0.0026273 | 0.00026536 | 0.00050486 | 9.6055e-05 |  | 11
3 | -4.697 |  |  |  | 593.2253 | 6.4602e-06 | 0.0038324 | 0.0038324 | 0.00038707 | 0.00089193 | 0.0001697 |  | 12
4 | -4.596 |  |  |  | 534.0043 | 1.0329e-05 | 0.0055158 | 0.0055158 | 0.00055709 | 0.001449 | 0.00027569 |  | 13
5 | -4.495 |  |  |  | 479.051 | 1.6347e-05 | 0.0078312 | 0.0078312 | 0.00079095 | 0.00224 | 0.00042618 |  | 14
6 | -4.394 |  |  |  | 428.1671 | 2.5609e-05 | 0.010965 | 0.010965 | 0.0011075 | 0.0033474 | 0.00063689 |  | 15
7 | -4.293 |  |  |  | 381.1586 | 3.9712e-05 | 0.015136 | 0.015136 | 0.0015288 | 0.0048762 | 0.00092776 |  | 16
8 | -4.192 |  |  |  | 337.8362 | 6.0955e-05 | 0.020593 | 0.020593 | 0.0020799 | 0.0069561 | 0.0013235 |  | 17
9 | -4.091 |  |  |  | 298.015 | 9.2613e-05 | 0.0276 | 0.0276 | 0.0027876 | 0.0097437 | 0.0018539 |  | 18
10 | -3.99 |  |  |  | 261.5144 | 0.00013928 | 0.036425 | 0.036425 | 0.0036789 | 0.013423 | 0.0025538 |  | 19
11 | -3.889 |  |  |  | 228.1586 | 0.00020735 | 0.047309 | 0.047309 | 0.0047782 | 0.018201 | 0.0034629 |  | 20
12 | -3.788 |  |  |  | 197.776 | 0.00030555 | 0.06043 | 0.06043 | 0.0061034 | 0.024304 | 0.0046242 |  | 21
13 | -3.687 |  |  |  | 170.1996 | 0.00044567 | 0.075854 | 0.075854 | 0.0076612 | 0.031965 | 0.0060818 |  | 22
14 | -3.586 |  |  |  | 145.267 | 0.00064347 | 0.093475 | 0.093475 | 0.009441 | 0.041406 | 0.0078781 |  | 23
15 | -3.485 |  |  |  | 122.8202 | 0.00091962 | 0.11295 | 0.11295 | 0.011408 | 0.052814 | 0.010049 |  | 24
16 | -3.384 |  |  |  | 102.7055 | 0.0013009 | 0.13361 | 0.13361 | 0.013495 | 0.066309 | 0.012616 |  | 25
17 | -3.283 |  |  |  | 84.7739 | 0.0018217 | 0.15443 | 0.15443 | 0.015598 | 0.081907 | 0.015584 |  | 26
18 | -3.182 |  |  |  | 68.8809 | 0.002525 | 0.17393 | 0.17393 | 0.017567 | 0.099473 | 0.018926 |  | 27
19 | -3.081 |  |  |  | 54.8863 | 0.0034644 | 0.19015 | 0.19015 | 0.019205 | 0.11868 | 0.02258 |  | 28
20 | -2.98 |  |  |  | 42.6546 | 0.004705 | 0.20069 | 0.20069 | 0.020269 | 0.13895 | 0.026436 |  | 29
21 | -2.879 |  |  |  | 32.0546 | 0.0063249 | 0.20274 | 0.20274 | 0.020477 | 0.15942 | 0.030332 |  | 30
22 | -2.778 |  |  |  | 22.9596 | 0.0084163 | 0.19324 | 0.19324 | 0.019517 | 0.17894 | 0.034046 |  | 31
23 | -2.677 |  |  |  | 15.2476 | 0.011086 | 0.16903 | 0.16903 | 0.017072 | 0.19601 | 0.037294 |  | 32
24 | -2.576 |  |  |  | 8.8009 | 0.014453 | 0.1272 | 0.1272 | 0.012847 | 0.20886 | 0.039738 |  | 33
25 | -2.475 |  |  |  | 3.5061 | 0.018653 | 0.0654 | 0.0654 | 0.0066054 | 0.21547 | 0.040995 |  | 34
26 | -2.374 |  |  |  | -0.74522 | 0.023828 | -0.017757 | 0.017757 | 0.0017935 | 0.21726 | 0.041336 |  | 35
27 | -2.273 |  |  |  | -4.0575 | 0.030131 | -0.12226 | 0.12226 | 0.012348 | 0.22961 | 0.043686 |  | 36
28 | -2.172 |  |  |  | -6.5303 | 0.037714 | -0.24628 | 0.24628 | 0.024875 | 0.25448 | 0.048418 |  | 37
29 | -2.071 |  |  |  | -8.259 | 0.046726 | -0.38591 | 0.38591 | 0.038977 | 0.29346 | 0.055834 |  | 38
30 | -1.97 |  |  |  | -9.3344 | 0.057304 | -0.5349 | 0.5349 | 0.054024 | 0.34748 | 0.066113 |  | 39
31 | -1.869 |  |  |  | -9.8427 | 0.069563 | -0.68469 | 0.68469 | 0.069154 | 0.41664 | 0.07927 |  | 40
32 | -1.768 |  |  |  | -9.8657 | 0.083588 | -0.82466 | 0.82466 | 0.083291 | 0.49993 | 0.095117 |  | 41
33 | -1.667 |  |  |  | -9.4808 | 0.099422 | -0.9426 | 0.9426 | 0.095202 | 0.59513 | 0.11323 |  | 42
34 | -1.566 |  |  |  | -8.7608 | 0.11705 | -1.0255 | 1.0255 | 0.10357 | 0.6987 | 0.13294 |  | 43
35 | -1.465 |  |  |  | -7.774 | 0.13642 | -1.0605 | 1.0605 | 0.10711 | 0.80581 | 0.15332 |  | 44
36 | -1.364 |  |  |  | -6.5844 | 0.15737 | -1.0361 | 1.0361 | 0.10465 | 0.91047 | 0.17323 |  | 45
37 | -1.263 |  |  |  | -5.2512 | 0.17969 | -0.94359 | 0.94359 | 0.095303 | 1.0058 | 0.19136 |  | 46
38 | -1.162 |  |  |  | -3.8295 | 0.2031 | -0.77776 | 0.77776 | 0.078554 | 1.0843 | 0.20631 |  | 47
39 | -1.061 |  |  |  | -2.3696 | 0.22723 | -0.53844 | 0.53844 | 0.054382 | 1.1387 | 0.21665 |  | 48
40 | -0.96 |  |  |  | -0.91745 | 0.25164 | -0.23087 | 0.23087 | 0.023318 | 1.162 | 0.22109 |  | 49
41 | -0.859 |  |  |  | 0.48546 | 0.27586 | 0.13392 | 0.13392 | 0.013526 | 1.1755 | 0.22366 |  | 50
42 | -0.758 |  |  |  | 1.8022 | 0.29933 | 0.53944 | 0.53944 | 0.054483 | 1.23 | 0.23403 |  | 51
43 | -0.657 |  |  |  | 3.0002 | 0.3215 | 0.96456 | 0.96456 | 0.097421 | 1.3275 | 0.25256 |  | 52
44 | -0.556 |  |  |  | 4.0516 | 0.34181 | 1.3849 | 1.3849 | 0.13987 | 1.4673 | 0.27918 |  | 53
45 | -0.455 |  |  |  | 4.9327 | 0.35971 | 1.7744 | 1.7744 | 0.17921 | 1.6465 | 0.31327 |  | 54
46 | -0.354 |  |  |  | 5.6247 | 0.37471 | 2.1076 | 2.1076 | 0.21287 | 1.8594 | 0.35377 |  | 55
47 | -0.253 |  |  |  | 6.1128 | 0.38638 | 2.3619 | 2.3619 | 0.23855 | 2.098 | 0.39916 |  | 56
48 | -0.152 |  |  |  | 6.3871 | 0.39436 | 2.5188 | 2.5188 | 0.2544 | 2.3524 | 0.44756 |  | 57
49 | -0.051 |  |  |  | 6.442 | 0.39842 | 2.5666 | 2.5666 | 0.25923 | 2.6116 | 0.49689 |  | 58
50 | 0.05 |  |  |  | 6.2763 | 0.39844 | 2.5008 | 2.5008 | 0.25258 | 2.8642 | 0.54494 |  | 59
51 | 0.151 |  |  |  | 5.8935 | 0.39442 | 2.3245 | 2.3245 | 0.23478 | 3.0989 | 0.58961 |  | 60
52 | 0.252 |  |  |  | 5.3014 | 0.38647 | 2.0488 | 2.0488 | 0.20693 | 3.3059 | 0.62898 |  | 61
53 | 0.353 |  |  |  | 4.5123 | 0.37484 | 1.6914 | 1.6914 | 0.17083 | 3.4767 | 0.66149 |  | 62
54 | 0.454 |  |  |  | 3.5432 | 0.35988 | 1.2751 | 1.2751 | 0.12879 | 3.6055 | 0.68599 |  | 63
55 | 0.555 |  |  |  | 2.4152 | 0.342 | 0.82601 | 0.82601 | 0.083427 | 3.6889 | 0.70186 |  | 64
56 | 0.656 |  |  |  | 1.1543 | 0.32171 | 0.37136 | 0.37136 | 0.037507 | 3.7264 | 0.709 |  | 65
57 | 0.757 |  |  |  | -0.2093 | 0.29955 | -0.062697 | 0.062697 | 0.0063323 | 3.7328 | 0.7102 |  | 66
58 | 0.858 |  |  |  | -1.6409 | 0.27609 | -0.45303 | 0.45303 | 0.045756 | 3.7785 | 0.71891 |  | 67
59 | 0.959 |  |  |  | -3.1011 | 0.25189 | -0.78112 | 0.78112 | 0.078893 | 3.8574 | 0.73392 |  | 68
60 | 1.06 |  |  |  | -4.5463 | 0.22747 | -1.0341 | 1.0341 | 0.10445 | 3.9619 | 0.75379 |  | 69
61 | 1.161 |  |  |  | -5.9282 | 0.20334 | -1.2054 | 1.2054 | 0.12175 | 4.0836 | 0.77695 |  | 70
62 | 1.262 |  |  |  | -7.1941 | 0.17992 | -1.2943 | 1.2943 | 0.13073 | 4.2143 | 0.80183 |  | 71
63 | 1.363 |  |  |  | -8.2869 | 0.15758 | -1.3058 | 1.3058 | 0.13189 | 4.3462 | 0.82692 |  | 72
64 | 1.464 |  |  |  | -9.1448 | 0.13662 | -1.2493 | 1.2493 | 0.12618 | 4.4724 | 0.85093 |  | 73
65 | 1.565 |  |  |  | -9.7018 | 0.11724 | -1.1374 | 1.1374 | 0.11488 | 4.5873 | 0.87279 |  | 74
66 | 1.666 |  |  |  | -9.8871 | 0.099588 | -0.98464 | 0.98464 | 0.099448 | 4.6867 | 0.89171 |  | 75
67 | 1.767 |  |  |  | -9.6257 | 0.083736 | -0.80602 | 0.80602 | 0.081408 | 4.7681 | 0.9072 |  | 76
68 | 1.868 |  |  |  | -8.838 | 0.069693 | -0.61595 | 0.61595 | 0.062211 | 4.8303 | 0.91903 |  | 77
69 | 1.969 |  |  |  | -7.4398 | 0.057417 | -0.42717 | 0.42717 | 0.043144 | 4.8735 | 0.92724 |  | 78
70 | 2.07 |  |  |  | -5.3426 | 0.046823 | -0.25015 | 0.25015 | 0.025266 | 4.8988 | 0.93205 |  | 79
71 | 2.171 |  |  |  | -2.4534 | 0.037796 | -0.092727 | 0.092727 | 0.0093654 | 4.9081 | 0.93383 |  | 80
72 | 2.272 |  |  |  | 1.3255 | 0.030199 | 0.040029 | 0.040029 | 0.0040429 | 4.9122 | 0.9346 |  | 81
73 | 2.373 |  |  |  | 6.0959 | 0.023885 | 0.1456 | 0.1456 | 0.014706 | 4.9269 | 0.9374 |  | 82
74 | 2.474 |  |  |  | 11.9645 | 0.018699 | 0.22373 | 0.22373 | 0.022596 | 4.9495 | 0.9417 |  | 83
75 | 2.575 |  |  |  | 19.0422 | 0.014491 | 0.27593 | 0.27593 | 0.027869 | 4.9773 | 0.947 |  | 84
76 | 2.676 |  |  |  | 27.4445 | 0.011115 | 0.30506 | 0.30506 | 0.030811 | 5.0081 | 0.95286 |  | 85
77 | 2.777 |  |  |  | 37.2913 | 0.0084397 | 0.31473 | 0.31473 | 0.031788 | 5.0399 | 0.95891 |  | 86
78 | 2.878 |  |  |  | 48.7071 | 0.0063431 | 0.30896 | 0.30896 | 0.031205 | 5.0711 | 0.96485 |  | 87
79 | 2.979 |  |  |  | 61.8208 | 0.004719 | 0.29173 | 0.29173 | 0.029465 | 5.1006 | 0.97045 |  | 88
80 | 3.08 |  |  |  | 76.7658 | 0.0034751 | 0.26677 | 0.26677 | 0.026943 | 5.1276 | 0.97558 |  | 89
81 | 3.181 |  |  |  | 93.6801 | 0.0025331 | 0.2373 | 0.2373 | 0.023967 | 5.1515 | 0.98014 |  | 90
82 | 3.282 |  |  |  | 112.7059 | 0.0018277 | 0.20599 | 0.20599 | 0.020805 | 5.1723 | 0.9841 |  | 91
83 | 3.383 |  |  |  | 133.9901 | 0.0013054 | 0.1749 | 0.1749 | 0.017665 | 5.19 | 0.98746 |  | 92
84 | 3.484 |  |  |  | 157.6841 | 0.00092283 | 0.14552 | 0.14552 | 0.014697 | 5.2047 | 0.99025 | x | 93
85 | 3.585 |  |  |  | 183.9437 | 0.00064578 | 0.11879 | 0.11879 | 0.011998 | 5.2167 | 0.99254 | x | 94
86 | 3.686 |  |  |  | 212.9292 | 0.00044732 | 0.095247 | 0.095247 | 0.00962 | 5.2263 | 0.99437 | x | 95
87 | 3.787 |  |  |  | 244.8054 | 0.00030671 | 0.075083 | 0.075083 | 0.0075834 | 5.2339 | 0.99581 | x | 96
88 | 3.888 |  |  |  | 279.7416 | 0.00020816 | 0.058231 | 0.058231 | 0.0058813 | 5.2398 | 0.99693 | x | 97
89 | 3.989 |  |  |  | 317.9115 | 0.00013984 | 0.044457 | 0.044457 | 0.0044902 | 5.2443 | 0.99778 | x | 98
90 | 4.09 |  |  |  | 359.4934 | 9.2993e-05 | 0.03343 | 0.03343 | 0.0033765 | 5.2476 | 0.99843 | x | 99
91 | 4.191 |  |  |  | 404.67 | 6.1211e-05 | 0.02477 | 0.02477 | 0.0025018 | 5.2501 | 0.9989 | x | 100
92 | 4.292 |  |  |  | 453.6286 | 3.9883e-05 | 0.018092 | 0.018092 | 0.0018273 | 5.252 | 0.99925 | x | 101
93 | 4.393 |  |  |  | 506.5607 | 2.5722e-05 | 0.01303 | 0.01303 | 0.001316 | 5.2533 | 0.9995 | x | 102
94 | 4.494 |  |  |  | 563.6626 | 1.6421e-05 | 0.0092558 | 0.0092558 | 0.00093484 | 5.2542 | 0.99968 | x | 103
95 | 4.595 |  |  |  | 625.135 | 1.0377e-05 | 0.0064868 | 0.0064868 | 0.00065517 | 5.2549 | 0.9998 | x | 104
96 | 4.696 |  |  |  | 691.1829 | 6.4907e-06 | 0.0044862 | 0.0044862 | 0.00045311 | 5.2553 | 0.99989 | x | 105
97 | 4.797 |  |  |  | 762.0161 | 4.0187e-06 | 0.0030623 | 0.0030623 | 0.0003093 | 5.2556 | 0.99995 | x | 106
98 | 4.898 |  |  |  | 837.8486 | 2.463e-06 | 0.0020636 | 0.0020636 | 0.00020842 | 5.2558 | 0.99999 | x | 107
99 | 4.999 |  |  |  | 918.899 | 1.4942e-06 | 0.001373 | 0.001373 | 6.9336e-05 | 5.2559 | 1 | x | 108
261.3984

## fPM_QA_Calcs
[8 empty] | Anthracite |  | Anthracite |  |  | fPM | 30B |  | μg/dscm | No |  | μg/dscm | 2.2046e-09 | lbs/μg | 0.028317 |  |  |  | cm/cf | [5 empty] | lb/hr |  |  | lb/MMBtu | [6 empty] | Round to |  |  |  | From |  | original database export===>
[8 empty] | Bituminous |  | Bituminous |  |  | Se | M5 |  | lb/dscf | Yes |  | ppm | 2.2046e-12 | lb/mg | [20 empty] | Same |  |  |  | Min |  | original database export===>
[8 empty] | Lignite |  | Lignite |  |  | Pb | M5B |  | ppm |  |  |  |  | lb/scf | [20 empty] | Sig Figs |  |  |  | Test |  | original database export===>
[8 empty] | Oil |  | Oil |  |  | Hg | M29 |  | ppm @ 3% O2 | [25 empty] | as Submitted |  |  |  | Sheet |  | original database export===>
[8 empty] | Pet Coke |  | Pet Coke |  |  | HCl | OTM27 |  | ppm @ 7% O2 | [25 empty] | prior to | [5 empty] | original database export===>
[8 empty] | Subbituminous |  | Sub Bituminous |  |  | SO2 | 26A | [27 empty] | Calc % Diff. | [5 empty] | original database export===>
[14 empty] | M6C | [33 empty] | original database export===>
original database export===>
RTI | [5 empty] | As Submitted | [11 empty] | 1 mg fPM basis per EPA |  | RTI-QA | [7 empty] | As Submitted | [8 empty] | RTI-QA | [7 empty] | Final for UPL |  | Final for UPL | original database export===>
Comments |  | Use Run in UPL Calc? | Grade | Key | Facility_Name | Facility_ID | Boiler_ID | Fuel1 Used | Fuel1 Fraction | Fuel2 Used | Fuel2 Fraction | "Fuel Used/Fraction" Data Source | Pollutant | Reference Method | Concentration | Concentration UOM | Non-Detect? | 1 x MDL | 1 x MDL UOM | HAP Conversion Value to lbs | HAP Conversion UOM | Volume Conversion Value to cubic feet | Reserve | Reserve | Reserve | Volume Conversion UOM | Submitted F Factor | Bws (percent) | %O2d | %CO2d | Emission Rate Value | Emission Rate UOM | Emission Rate MDL | Emission Factor Value | Emission Factor UOM | Emission Factor MDL | Fd | Fw | Fc | Calculated conc lb/dscf | 19-1 lb/MMBtu | %diff 19-1 | 19-6 lb/MMBtu | %diff 19-6 | lb/MMBtu Value Used for UPL Calcs | Unit Heat Rate (MMBtu/MWh) | lb/MWh Value Used in UPL Calcs | original database export===> | Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | configuration_id | submittal_id | Compound | RunDate | Method | RunNumber | RunStartTime | RunEndTime | NetTravPts | Mass_TOOL | mass | units | Vmstd | Cd | Vwstd | PercH20 | PercCO2 | PercO2 | Fd | 19-1 | 19-5 | Fc | 19-6 | 19-9 | Fw | FuelType | lb/mmBtuO2 | CountOfComments | AvgOfStackTemp | AvgOfDryGasInlet | AvgOfDryGasOutlet | AvgOfOrificePresDesired | AvgOfOrificePresActual | AvgOfProbeTemp | AvgOfFilterTemp | AvgOfImpingTemp | CountOfNotes | M29 Isokinetic (+/- 10%) | OTM27 includes all fractions? | QA Comment | Questions for EPA
The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. |  | Yes | A | 1_fPM_T1_R1 | Springerville | 8223 | 3 | Bituminous |  |  |  | ERT | fPM | M29 | 5.0952e-08 | lb/dscf |  | 0.00020715 | lb fPM/MMBtu | [7 empty] | 9780 | 13.34 | 5.5 | 14 |  |  |  | 0.00067689 | lb/MMBtu |  | 9780 | 10640 | 1800 |  | 0.00067689 | 0% | 0.0006551 | -3.219% | 0.00067689 | 9.3333 | 0.0063176 | original database export===> | 1_fPM_T1_R1 | 0.00067628 | A | 0.00067689 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-25 | Method 29 | 2 | 13:10 | 18:05 | 50 | 3.2 | 0.0032 | gm | 138.335 | 5.0952e-08 | 21.29 | 13.34 | 14 | 5.5 | 9780 | 0.00067628 | 0.00058606 | 1800 | 6.551e-06 | 0.00056771 | 10640 | Coal - Bituminous | 0.00067689 | 50 | 196.9792 | 69.875 | 58.1458 | 1.3521 | 1.3521 | 331.9792 | 337.75 | 56.0833 | 0 | 100.9
The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. |  | Yes | A | 1_fPM_T1_R2 | Springerville | 8223 | 3 | Bituminous |  |  |  | ERT | fPM | M29 | 3.937e-08 | lb/dscf |  | 0.00020581 | lb fPM/MMBtu | [7 empty] | 9780 | 14.36 | 5.4 | 14.1 |  |  |  | 0.00051965 | lb/MMBtu |  | 9780 | 10640 | 1800 |  | 0.00051965 | 0% | 0.0005026 | -3.282% | 0.00051965 | 9.3333 | 0.0048501 | original database export===> | 1_fPM_T1_R2 | 0.00051918 | A | 0.00051965 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-26 | Method 29 | 3 | 07:45 | 12:22 | 52 | 2.4 | 0.0024 | gm | 134.273 | 3.937e-08 | 22.52 | 14.36 | 14.1 | 5.4 | 9780 | 0.00051918 | 0.00044463 | 1800 | 5.026e-06 | 0.00043042 | 10640 | Coal - Bituminous | 0.00051965 | 52 | 196.8333 | 65.4375 | 52.7292 | 1.25 | 1.25 | 329.6667 | 333.4583 | 43.5 | 0 | 101.3
The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. |  | Yes | A | 1_fPM_T1_R3 | Springerville | 8223 | 3 | Bituminous |  |  |  | ERT | fPM | M29 | 4.2746e-08 | lb/dscf |  | 0.00020449 | lb fPM/MMBtu | [7 empty] | 9780 | 14.35 | 5.3 | 14.2 |  |  |  | 0.00056059 | lb/MMBtu |  | 9780 | 10640 | 1800 |  | 0.00056059 | 0% | 0.00054185 | -3.343% | 0.00056059 | 9.3333 | 0.0052322 | original database export===> | 1_fPM_T1_R3 | 0.00056009 | A | 0.00056059 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-26 | Method 29 | 4 | 13:28 | 17:38 | 28 | 2.6 | 0.0026 | gm | 133.974 | 4.2746e-08 | 22.45 | 14.35 | 14.2 | 5.3 | 9780 | 0.00056009 | 0.00047972 | 1800 | 5.4185e-06 | 0.0004641 | 10640 | Coal - Bituminous | 0.00056059 | 28 | 197.4583 | 73.2083 | 60.25 | 1.2542 | 1.2542 | 1698.5833 | 338.625 | 46.4167 | 0 | 101.2
The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. |  | Yes | A | 1_fPM_T1_R4 | Springerville | 8223 | 3 | Bituminous |  |  |  | ERT | fPM | OTM27 | 4.9501e-08 | lb/dscf |  | 0.0001381 | lb fPM/MMBtu | [7 empty] | 9780 | 14.13 | 5.5 | 14 |  |  |  | 0.00065761 | lb/MMBtu |  | 9780 | 10640 | 1800 |  | 0.00065761 | 0% | 0.00063645 | -3.219% | 0.00065761 | 9.3333 | 0.0061377 | original database export===> | 1_fPM_T1_R4 | 0.00065702 | A | 0.00065761 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-24 | OTM - 27/28 | 1 | 10:05 | 19:35 | 13 | 3 | 0.003 | gm | 133.490 | 4.9501e-08 | 21.97 | 14.13 | 14 | 5.5 | 9780 | 0.00065702 | 0.00056419 | 1800 | 6.3645e-06 | 0.00054652 | 10640 | Coal - Bituminous | 0.00065761 | 13 | 196.75 | 65.2292 | 65.2292 | 0.35 | 0.35 |  |  |  | 0 |  | Yes, includes >2.5 acetone rinse, filter, and <2.5 acetone rinse |  | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis.
The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. |  | Yes | A | 1_fPM_T1_R5 | Springerville | 8223 | 3 | Bituminous |  |  |  | ERT | fPM | OTM27 | 5.1824e-08 | lb/dscf |  | 0.000139 | lb fPM/MMBtu | [7 empty] | 9780 | 14.11 | 5.6 | 14 |  |  |  | 0.00069297 | lb/MMBtu |  | 9780 | 10640 | 1800 |  | 0.00069297 | 0% | 0.00066631 | -3.848% | 0.00069297 | 9.3333 | 0.0064677 | original database export===> | 1_fPM_T1_R5 | 0.00069235 | A | 0.00069297 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-25 | OTM - 27/28 | 2 | 07:25 | 16:48 | 13 | 3.4 | 0.0034 | gm | 144.508 | 5.1824e-08 | 23.74 | 14.11 | 14 | 5.6 | 9780 | 0.00069235 | 0.00059466 | 1800 | 6.6631e-06 | 0.00057229 | 10640 | Coal - Bituminous | 0.00069297 | 13 | 196.6 | 61.75 | 61.75 | 0.36 | 0.36 |  |  |  | 0 |  | Yes, includes >2.5 acetone rinse, filter, and <2.5 acetone rinse
The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. |  | Yes | A | 1_fPM_T1_R6 | Springerville | 8223 | 3 | Bituminous |  |  |  | ERT | fPM | OTM27 | 2.8978e-08 | lb/dscf |  | 0.0001381 | lb fPM/MMBtu | [7 empty] | 9780 | 14.17 | 5.5 | 13.9 |  |  |  | 0.00038497 | lb/MMBtu |  | 9780 | 10640 | 1800 |  | 0.00038497 | 0% | 0.00037526 | -2.523% | 0.00038497 | 9.3333 | 0.0035931 | original database export===> | 1_fPM_T1_R6 | 0.00038463 | A | 0.00038497 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-26 | OTM - 27/28 | 3 | 07:25 | 16:41 | 13 | 1.9 | 0.0019 | gm | 144.419 | 2.8978e-08 | 23.85 | 14.17 | 13.9 | 5.5 | 9780 | 0.00038463 | 0.00033012 | 1800 | 3.7526e-06 | 0.00032208 | 10640 | Coal - Bituminous | 0.00038497 | 13 | 196.6417 | 61.2 | 61.2 | 0.36 | 0.36 |  |  |  | 0 |  | Yes, includes >2.5 acetone rinse, filter, and <2.5 acetone rinse
[5 empty] | Springerville |  | 3 | [40 empty] | original database export===> | Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | report_id | sampling_port_id | pollutant_id | pollutant_name | run_id | start_datetime | end_datetime | unit_load | fuel_flow_rate | fuel_heating_value | fg_moisture_content | fg_oxygen_content | fg_CO2_content | fg_temperature | test_method | conc | conc_units | conc_ND | conc_MDL | conc2 | conc2_units | emission_rate | emission_rate_units | emission_rate_ND | emission_rate_MDL | emission_factor | emission_factor_units | emission_factor_ND | emission_factor_MDL | run_pollutant_comment | Fuel1 | Fuel1%Btu | Fuel2 | Fuel2%Btu | QA Comment | Questions for EPA
Insufficient data submitted. |  | Yes | G | 1_fPM_T2 | Springerville | 8223 | 3 | Subbituminous |  |  |  | Part II | fPM | M5B |  |  | No | 0.0004358 | lb fPM/MMBtu | [8 empty] | 11.7 | 6.2 | 13.9 |  |  |  | 0.0018 | lb/MMBtu |  | 9820 | 11295 | 1840 |  | 0.0018 |  | 0 |  | 0.0018 | 9.3333 | 0.0168 | original database export===> | 1_fPM_T2 | Insufficient data submitted. | G | 0.0018 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 06NOV20 (PM RETEST) | STK3 | 1 | PM (Filterable) | average | 2006-11-20 07:38 | 2006-11-20 17:13 | 450 |  | 12065 | 11.7 | 6.2 | 13.9 | 217 | Method 5B |  |  | FALSE | [5 empty] | FALSE |  | 0.0018 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
Insufficient data submitted. |  | Yes | G | 1_fPM_T3 | Springerville | 8223 | 3 | Subbituminous |  |  |  | Part II | fPM | M29 |  |  | No | 0.00042995 | lb fPM/MMBtu | [8 empty] | 14.51 | 6 | 14 |  |  |  | 0.0044 | lb/MMBtu |  | 9820 | 11295 | 1840 |  | 0.0044 |  | 0 |  | 0.0044 | 9.3333 | 0.041067 | original database export===> | 1_fPM_T3 | Insufficient data submitted. | G | 0.0044 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 07JUL09 | STK3 | 1 | PM (Filterable) | average | 2007-06-08 11:46 | 2007-06-09 09:59 | 437 | 443317 | 11913 | 14.51 | 6 | 14 | 202.5 | Method 201/202 and 29 |  |  | FALSE | [5 empty] | FALSE |  | 0.0044 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
Insufficient data submitted. |  | Yes | G | 1_fPM_T4 | Springerville | 8223 | 3 | Subbituminous |  |  |  | Part II | fPM | M29 |  |  | No | 0.00042709 | lb fPM/MMBtu | [8 empty] | 12.3 | 5.9 | 13.9 |  |  |  | 0.001 | lb/MMBtu |  | 9820 | 11295 | 1840 |  | 0.001 |  | 0 |  | 0.001 | 9.3333 | 0.0093333 | original database export===> | 1_fPM_T4 | Insufficient data submitted. | G | 0.001 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 08MAY07 | STK3 | 1 | PM (Filterable) | average | 2008-05-07 10:20 | 2008-05-08 12:05 | 430 | 454000 | 11958 | 12.3 | 5.9 | 13.9 | 198 | method 201/202 and 29 |  |  | FALSE | [5 empty] | FALSE |  | 0.001 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
Insufficient data submitted. |  | Yes | G | 1_fPM_T5 | Springerville | 8223 | 3 | Subbituminous |  |  |  | Part II | fPM | M29 |  |  | No | 0.00040727 | lb fPM/MMBtu | [8 empty] | 13.63 | 5.17 | 14.1 |  |  |  | 0.00179 | lb/MMBtu |  | 9820 | 11295 | 1840 |  | 0.00179 |  | 0 |  | 0.00179 | 9.3333 | 0.016707 | original database export===> | 1_fPM_T5 | Insufficient data submitted. | G | 0.00179 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 09MAY18 | STK3 | 1 | PM (Filterable) | average | 2009-05-15 08:00 | 2009-05-18 18:33 | 434 | 442868 | 11907 | 13.63 | 5.17 | 14.1 | 196 | Method 201/202 and 29 |  |  | FALSE | [5 empty] | FALSE |  | 0.00179 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[47 empty] | 1_fPM_T1 | 0.0054331 | 6 Runs with simultaneous M5 and OTM27. | [13 empty] | 3.1667
[47 empty] | 1_fPM_T2 | 0.0168 | [14 empty] | 7.3778
[47 empty] | 1_fPM_T3 | 0.041067 | [14 empty] | 8.5556 |  | 12.0852
[47 empty] | 1_fPM_T4 | 0.0093333 | [14 empty] | 27.4889 |  | 12.6254
[47 empty] | 1_fPM_T5 | 0.016707 | [16 empty] | 12.1503
Springerville 3 is subject to NSPS Subpart Da; the Part II submittal indicates that compliance with the initial NSPS performance testing requirement for fPM ocurred in November of 2006.
The Part II submittal also indicates NSPS compliance tests were conducted in 2007, 2008, and 2009.
The Part II submittal did not provide run-level data nor run duration. The NSPS requires 120 minute runs as a minimum. Therefore the MDL for Springerville for the NSPS compliance tests is based on 2 hour runs.
§ 60.50Da Compliance determination procedures and methods.
(a) In conducting the performance tests required in §60.8, the owner or operator shall use as reference methods and procedures the methods in appendix A of this part or the methods and procedures as specified in this section, except as provided in §60.8(b). Section 60.8(f) does not apply to this section for SO2and NOX. Acceptable alternative methods are given in paragraph (e) of this section.
(b) In conducting the performance tests to determine compliance with the PM emissions limits in §60.42Da, the owner or operator shall meet the requirements specified in paragraphs (b)(1) through (3) of this section.
(1) The owner or operator shall measure filterable PM to determine compliance with the applicable PM emissions limit in §60.42Da as specified in paragraphs (b)(1)(i) through (ii) of this section.
(i) The dry basis F factor (O2) procedures in Method 19 of appendix A of this part shall be used to compute the emission rate of PM.
(ii) For the PM concentration, Method 5 of appendix A of this part shall be used for an affected facility that does not use a wet FGD. For an affected facility that uses a wet FGD, Method 5B of appendix A of this part shall be used downstream of the wet FGD.
(A) The sampling time and sample volume for each run shall be at least 120 minutes and 1.70 dscm (60 dscf). The probe and filter holder heating system in the sampling train may be set to provide an average gas temperature of no greater than 160 ± 14 °C (320 ± 25 °F).
Conversions
1 |  | ppm SO2= | 1.66e-07 | lb/scf
1 |  | ppm Hg= | 5.1979e-07 | lb/scf
1000 |  | mg= | 1 | g
1000000 |  | ug= | 1 | g
454 |  | g= | 1 | lb
1 |  | m^3= | 35.3145 | ft^3
200.59 |  | Hg molecular weight
64.06 |  | SO2 molecular weight
Table 19-2 |  | Fd | Fw | Fc
Fuel Type |  | dscf/MMBtu | wscf/MMBtu | scf/MMBtu
Coal
Anthracite |  | 10100 | 10540 | 1970
Bituminous |  | 9780 | 10640 | 1800
Lignite |  | 9860 | 11950 | 1910
Oil |  | 9190 | 10320 | 1420
Subbituminous |  | 9820 | 11295 | 1840
Petroleum Coke |  | 9830 |  | 1850
QA Calcs
RTI | [6 empty] | As Submitted | [13 empty] | RTI-QA | [7 empty] | Using Available Representative Diluent Per Comment | [8 empty] | RTI-QA | [7 empty] | Final for UPL |  | Final for UPL
Comments |  |  | Use Run in UPL Calc? | Grade |  |  | Facility_ID | Boiler_ID | Fuel1 Used | Fuel1 Fraction | Fuel2 Used | Fuel2 Fraction | "Fuel Used/Fraction" Data Source | Pollutant | Reference Method | Concentration | Concentration UOM | Non-Detect? | MDL |  | Mass Conversion Value to lbs | Mass Conversion UOM | Volume Conversion Value to cubic feet | Reserve | Reserve | Reserve |  | Volume Conversion UOM | Bws (percent) | %O2d | %CO2d | Emission Rate Value | Emission Rate UOM | Emission Rate MDL | Emission Factor Value | Emission Factor UOM | Emission Factor MDL | Fd | Fw | Fc | Calculated conc lb/dscf | 19-1 lb/MMBtu | %diff 19-1 | 19-6 lb/MMBtu | %diff 19-6 | lb/MMBtu Value Used for UPL Calcs | Unit Heat Rate (MMBtu/MWh) | lb/MWh Value Used in UPL Calcs
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47
| Column Source==> | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
| Test Avgs for UPL | R1 | R2 | R3 | R4 | R5 | R6 | R7 | R8 | R9 | R10
Test_IDs | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | lb/MW | Test_IDs
1_fPM_T1 | 0.0054331 | 0.0063176 | 0.0048501 | 0.0052322 | 0.0061377 | 0.0064677 | 0.0035931 |  |  |  |  | 1_fPM_T1
1_fPM_T2 | 0.0168 | R1: 0.0168 | 1_fPM_T2
1_fPM_T3 | 0.041067 | R1: 0.041067 | 1_fPM_T3
1_fPM_T4 | 0.0093333 | R1: 0.0093333 | 1_fPM_T4
1_fPM_T5 | 0.016707 | R1: 0.016707 | 1_fPM_T5
QA of "1 x MDL" Calculation Function in Cell R11
Term in Row 11, Column R ==> |  | R2: IF(BM11<>"",ROUND((BM11-BL11)*24,0),1); R5: x; R6: 2.20462E-06*0.028317; R8: x; R9: IF(AA11<>"",AA11,AK11) | *20.9/IF(AC11<>"",(20.9-AC11),(20.9-6))
Purpose of Term===> |  | R2: This function determines the duration of the run. If the start time was not provided, the function returns a duration of 1 hour. For a 1 hour run the assumed sample volume is 1 dscm. The units of measure of this term are therefore dscm.; R6: constant; R7: constant; R9: If the submittal specified an F factor the submitted value is used. | If the submittal specified a %O2 the submitted value is used.
|  | R9: Otherwise, the default F factor for the submitted fuel type is used. | Otherwise, the following default %O2 was used==> |  | 6
=ROUND((BM11-BL11)*24,0)*0.00000220462*0.028317*IF(AA11<>"",AA11,AK11)*20.9/IF(AC11<>"",(20.9-AC11),(20.9-$N$302))
|  | R2: Use 1 in this QA Calc to determine the MDL for a 1 mg catch weight. |  |  | 0.97941 | This is the line that shows implementation of the formula used in cells AA11. Select in the formula bar beside the "fx" symbol at the top of the Excel screen; then select the length of the formula in the formula bar. Then paste this formula into Cell A11.
|  |  | 1 | mg fPM | 2.2046e-06 | lb fPM | 0.028317 | dscm flue gas | 9780 | dscf flue gas |  | 20.9 | %O2 = | 0.0004143 | lb fPM
|  | R2: 2; R3: dscm flue gas; R5: mg; R7: dscf flue gas; R9: MMBtu | 15.4 | %O2 = |  | MMBtu
Note on S11: stboone: 1/X at the beginning of the calculation indicates 1 mg catch / the run duration.
Note on S18: stboone: See comment below regarding assumption of 2 hour runs. Part II submittal did not specify run duration. 1/2 is (1 mg catch / 2 cubic meters of sample) for a 2 hour run.
Note on S19: stboone: See comment below regarding assumption of 2 hour runs. Part II submittal did not specify run duration.
Note on S20: stboone: See comment below regarding assumption of 2 hour runs. Part II submittal did not specify run duration.
Note on S21: stboone: See comment below regarding assumption of 2 hour runs. Part II submittal did not specify run duration.
Note on D101: stboone: interpolated F factor value.

## UPL Normal
Emissions (lb/MW) | fPM
8223
ORIS/Facility/Unit | Springerville
Averages | 3
1 | 0.0054331
2 | 0.0093333
3 | 0.016707
4 | 0.0168
5 | 0.041067
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test Averages = | 5
Total Number of sources = |  | 1
n =Total # test Averages = |  | 5
4
This step is for QC only:
means | 0.017868
0.017868
UPL Mean =
Pooled Variance = |  | 0.00019203
m= number future Averages = |  | 1
Term1 |  | 1.2
Term2 |  | 0.00023044
Squared root Term2 |  | 0.01518
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.7469
UPL POOLED VARIANCE = |  | 0.074748 | lb/MW
| Normal UPL | 0.074748 | lb/MW
| Lognormal UPL | 0.082327 | lb/MW
| Final UPL | 0.082327 | lb/MW

## UPL Pooled Template
Emissions (lb/MW)
Averages | 8223 Springerville 3
1 | 0.0054331
2 | 0.0093333
3 | 0.016707
4 | 0.0168
5 | 0.041067
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
Use for large sample sets and small sample sets that are Normal.
Testing Normality | Raw Data
Sample Size | 5
Kurtosis | 2.8081
SE Kurtosis | 1.0954
Result Kurtosis | non normal
Skewness | 1.556
SE Skewness | 0.91287
Result Skewness | normal
ni = number test Averages = | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Number of sources = | 1
n =Total # test Averages = | 5
4
This step is for QC only:
means | 0.017868 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
0.017868
Mean =
Pooled Variance = |  |  | 0.00019203
m= number future Averages = | 1
Term1 | 1.2
Term2 | 0.00023044
Squared root Term2 |  | 0.01518
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | [5 empty] | 3.7469
UPL POOLED VARIANCE = |  |  |  |  | 0.074748

## ERT
Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | configuration_id | submittal_id | Compound | RunDate | Method | RunNumber | RunStartTime | RunEndTime | NetTravPts | Mass_TOOL | mass | units | Vmstd | Cd | Vwstd | PercH20 | PercCO2 | PercO2 | Fd | 19-1 | 19-5 | Fc | 19-6 | 19-9 | Fw | FuelType | lb/mmBtuO2 | CountOfComments | AvgOfStackTemp | AvgOfDryGasInlet | AvgOfDryGasOutlet | AvgOfOrificePresDesired | AvgOfOrificePresActual | AvgOfProbeTemp | AvgOfFilterTemp | AvgOfImpingTemp | CountOfNotes | M29 Isokinetic (+/- 10%) | OTM27 includes all fractions? | QA Comment | Questions for EPA
[20 empty] | DSCF | lb/dscf
1_fPM_T1_R1 | 0.00067628 | A | 0.00067689 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-25 | Method 29 | 2 | 13:10 | 18:05 | 50 | 3.2 | 0.0032 | gm | 138.335 | 5.0952e-08 | 21.29 | 13.34 | 14 | 5.5 | 9780 | 0.00067628 | 0.00058606 | 1800 | 6.551e-06 | 0.00056771 | 10640 | Coal - Bituminous | 0.00067689 | 50 | 196.9792 | 69.875 | 58.1458 | 1.3521 | 1.3521 | 331.9792 | 337.75 | 56.0833 | 0 | 100.9
1_fPM_T1_R2 | 0.00051918 | A | 0.00051965 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-26 | Method 29 | 3 | 07:45 | 12:22 | 52 | 2.4 | 0.0024 | gm | 134.273 | 3.937e-08 | 22.52 | 14.36 | 14.1 | 5.4 | 9780 | 0.00051918 | 0.00044463 | 1800 | 5.026e-06 | 0.00043042 | 10640 | Coal - Bituminous | 0.00051965 | 52 | 196.8333 | 65.4375 | 52.7292 | 1.25 | 1.25 | 329.6667 | 333.4583 | 43.5 | 0 | 101.3
1_fPM_T1_R3 | 0.00056009 | A | 0.00056059 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-26 | Method 29 | 4 | 13:28 | 17:38 | 28 | 2.6 | 0.0026 | gm | 133.974 | 4.2746e-08 | 22.45 | 14.35 | 14.2 | 5.3 | 9780 | 0.00056009 | 0.00047972 | 1800 | 5.4185e-06 | 0.0004641 | 10640 | Coal - Bituminous | 0.00056059 | 28 | 197.4583 | 73.2083 | 60.25 | 1.2542 | 1.2542 | 1698.5833 | 338.625 | 46.4167 | 0 | 101.2
1_fPM_T1_R4 | 0.00065702 | A | 0.00065761 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-24 | OTM - 27/28 | 1 | 10:05 | 19:35 | 13 | 3 | 0.003 | gm | 133.490 | 4.9501e-08 | 21.97 | 14.13 | 14 | 5.5 | 9780 | 0.00065702 | 0.00056419 | 1800 | 6.3645e-06 | 0.00054652 | 10640 | Coal - Bituminous | 0.00065761 | 13 | 196.75 | 65.2292 | 65.2292 | 0.35 | 0.35 |  |  |  | 0 |  | Yes, includes >2.5 acetone rinse, filter, and <2.5 acetone rinse |  | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis.
1_fPM_T1_R5 | 0.00069235 | A | 0.00069297 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-25 | OTM - 27/28 | 2 | 07:25 | 16:48 | 13 | 3.4 | 0.0034 | gm | 144.508 | 5.1824e-08 | 23.74 | 14.11 | 14 | 5.6 | 9780 | 0.00069235 | 0.00059466 | 1800 | 6.6631e-06 | 0.00057229 | 10640 | Coal - Bituminous | 0.00069297 | 13 | 196.6 | 61.75 | 61.75 | 0.36 | 0.36 |  |  |  | 0 |  | Yes, includes >2.5 acetone rinse, filter, and <2.5 acetone rinse
1_fPM_T1_R6 | 0.00038463 | A | 0.00038497 | lb/mmBtuO2 | Yes | The Part III M29 and OTM 27 tests overlap in time over the course of 3 days of ICR testing. The current UPL analysis treats this concurrent testing event as a single data point when assessing the variability of the unts performance based on stack test averages, but the runs are treated separately for the run by run variability analysis. | 8223 | 3 | 1133 | Filterable Particulate | 2010-02-26 | OTM - 27/28 | 3 | 07:25 | 16:41 | 13 | 1.9 | 0.0019 | gm | 144.419 | 2.8978e-08 | 23.85 | 14.17 | 13.9 | 5.5 | 9780 | 0.00038463 | 0.00033012 | 1800 | 3.7526e-06 | 0.00032208 | 10640 | Coal - Bituminous | 0.00038497 | 13 | 196.6417 | 61.2 | 61.2 | 0.36 | 0.36 |  |  |  | 0 |  | Yes, includes >2.5 acetone rinse, filter, and <2.5 acetone rinse
[35 empty] | Header tab comments | [8 empty] | Point tab notes
Conversions Used
[7 empty] | 1000 | mg= | 1 | g
[7 empty] | 1000000 | ug= | 1 | g
[7 empty] | 454 | g= | 1 | lb

## 8223_PartII
Nothing to compare
Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | report_id | sampling_port_id | pollutant_id | pollutant_name | run_id | start_datetime | end_datetime | unit_load | fuel_flow_rate | fuel_heating_value | fg_moisture_content | fg_oxygen_content | fg_CO2_content | fg_temperature | test_method | conc | conc_units | conc_ND | conc_MDL | conc2 | conc2_units | emission_rate | emission_rate_units | emission_rate_ND | emission_rate_MDL | emission_factor | emission_factor_units | emission_factor_ND | emission_factor_MDL | run_pollutant_comment | Fuel1 | Fuel1%Btu | Fuel2 | Fuel2%Btu | QA Comment | Questions for EPA
1_fPM_T2 | Insufficient data submitted. | G | 0.0018 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 06NOV20 (PM RETEST) | STK3 | 1 | PM (Filterable) | average | 2006-11-20 07:38 | 2006-11-20 17:13 | 450 |  | 12065 | 11.7 | 6.2 | 13.9 | 217 | Method 5B |  |  | FALSE | [5 empty] | FALSE |  | 0.0018 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U3 PERF 06NOV20 (PM RETEST) | STK3 |  | PM (Filterable) | average | 2006-11-20 07:38 | 2006-11-20 17:13 | 450 | ND | 12065 | 11.7 | 6.2 | 13.9 | 217 | Method 5B | ND |  | FALSE | [5 empty] | FALSE |  | 0.0018 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100 |  |  | Avg only | Do we keep data we cannot validate? Do we request copies of emission test reports?
1_fPM_T3 | Insufficient data submitted. | G | 0.0044 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 07JUL09 | STK3 | 1 | PM (Filterable) | average | 2007-06-08 11:46 | 2007-06-09 09:59 | 437 | 443317 | 11913 | 14.51 | 6 | 14 | 202.5 | Method 201/202 and 29 |  |  | FALSE | [5 empty] | FALSE |  | 0.0044 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U3 PERF 07JUL09 | STK3 |  | PM (Filterable) | average | 2007-06-08 11:46 | 2007-06-09 09:59 | 437 | 443317 | 11913 | 14.51 | 6 | 14 | 202.5 | Method 201/202 and 29 | ND |  | FALSE | [5 empty] | FALSE |  | 0.0044 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100 |  |  | Avg only | Do we keep data we cannot validate? Do we request copies of emission test reports?
1_fPM_T4 | Insufficient data submitted. | G | 0.001 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 08MAY07 | STK3 | 1 | PM (Filterable) | average | 2008-05-07 10:20 | 2008-05-08 12:05 | 430 | 454000 | 11958 | 12.3 | 5.9 | 13.9 | 198 | method 201/202 and 29 |  |  | FALSE | [5 empty] | FALSE |  | 0.001 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U3 PERF 08MAY07 | STK3 |  | PM (Filterable) | average | 2008-05-07 10:20 | 2008-05-08 12:05 | 430 | 454000 | 11958 | 12.3 | 5.9 | 13.9 | 198 | method 201/202 and 29 | ND |  | FALSE | [5 empty] | FALSE |  | 0.001 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100 |  |  | Avg only | Do we keep data we cannot validate? Do we request copies of emission test reports?
1_fPM_T5 | Insufficient data submitted. | G | 0.00179 | lb/MMBtu | Yes | No run data provided. | 8223 | U3 PERF 09MAY18 | STK3 | 1 | PM (Filterable) | average | 2009-05-15 08:00 | 2009-05-18 18:33 | 434 | 442868 | 11907 | 13.63 | 5.17 | 14.1 | 196 | Method 201/202 and 29 |  |  | FALSE | [5 empty] | FALSE |  | 0.00179 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U3 PERF 09MAY18 | STK3 |  | PM (Filterable) | average | 2009-05-15 08:00 | 2009-05-18 18:33 | 434 | 442868 | 11907 | 13.63 | 5.17 | 14.1 | 196 | Method 201/202 and 29 | ND |  | FALSE | [5 empty] | FALSE |  | 0.00179 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100 |  |  | Avg only | Do we keep data we cannot validate? Do we request copies of emission test reports?
Data for Units 1, 2, and 4
[7 empty] | 8223 | U1 PERF 06JUN01 (PM RETEST) | STK1 | 1 | PM (Filterable) | average | 2006-06-01 07:14 | 2006-06-01 13:45 | 406 |  | 10890 | 11.54 | 6 | 12.6 | 173 | Method 5B |  |  | FALSE | [5 empty] | FALSE |  | 0.003 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U1 PERF 07JUN06 | STK1 | 1 | PM (Filterable) | average | 39239.4535 | 39240.5576 | 411 | 379420 | 11028 | 13.13 | 6.88 | 12.9 | 171.92 | METHOD 5B, 6C, 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.075 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U1 PERF 08JUN09 | STK1 | 1 | PM (Filterable) | average | 39576.8104 | 2008-05-12 15:28 | 1901-02-12 | 388667 | 10550 | 12.47 | 7.98 | 11.42 | 181 | METHOD 5B, 6C AND 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.0058 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U1 PERF 09MAY20 | STK1 | 1 | PM (Filterable) | average | 2009-05-20 11:31 | 2009-05-21 12:45 | 411 | 390308 | 11004 | 12.79 | 6.98 | 12.32 | 178 | METHOD 5B, 6C AND 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.0069 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U2 PERF 05JUN05 | STK2 | 1 | PM (Filterable) | average | 2005-06-05 07:53 | 2005-06-05 18:40 | 412 |  | 10880 | 13.9 | 5.6 | 13.7 | 174.6 | METHOD 5B, 3A, 6C, 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.0083 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U2 PERF 06JUN05 | STK2 | 1 | PM (Filterable) | average | 2006-06-05 07:52 | 2006-06-05 15:49 | 408 |  | 10890 | 13.23 | 6.61 | 12.68 | 176.6 | Ref Methods 3A, 6C, 7E and 5B |  |  | FALSE | [5 empty] | FALSE |  | 0.0027 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U2 PERF 07JUN5-8 | STK2 | 1 | PM (Filterable) | average | 2007-06-05 09:31 | 2007-06-08 13:46 | 422 | 374160 | 11007 | 13.91 | 6.48 | 12.8 | 185 | METHOD 5B, 3A, 6C, 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.0073 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U2 PERF 08MAY13 | STK2 | 1 | PM (Filterable) | average | 2008-05-13 12:21 | 2008-05-14 00:41 | 412 | 402508 | 10619 | 14.39 | 7.4 | 12 | 193.3 | METHOD 5B, 3A, 6C, 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.0069 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U2 PERF 09MAY19 | STK2 | 1 | PM (Filterable) | average | 2009-05-19 12:50 | 2009-05-20 10:54 | 412 | 385418 | 11027 | 13.72 | 8.03 | 11.5 | 181.8 | METHOD 5B, 3A, 6C, 7E |  |  | FALSE | [5 empty] | FALSE |  | 0.0149 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U4 INITIAL PERF 09DEC15 (PM, HF) | STK4 | 1 | PM (Filterable) | average | 2009-12-16 06:45 | 2009-12-16 16:54 | 446 | 479002 | 11927 | 13.5 | 5.4 | 13.8 | 196.5 | Method 5B, Method 26 |  |  | FALSE | [5 empty] | FALSE |  | 0.001 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 8223 | U4 PERF DEC09 (ALT PM10) | STK4 | 1 | PM (Filterable) | average | 2009-12-12 08:25 | 2009-12-12 18:00 | 451 |  | 11889 | 13.4 | 5.53 | 13.8 |  | METHOD 201A/OTM 28 |  |  | FALSE | [5 empty] | FALSE |  | 0.0019 | pound per million British Thermal Unit (lb/MMBtu) | FALSE