## Emissions Calcs
Natural Gas Distribution
2013-11-29
INSTRUCTIONS: This sheet provides a simple tool for estimating equipment leak and combustion emissions from natural gas distribution. Enter the required information into the “Input Data” field for each source of emissions at your facility. The tool will automatically sum emissions from each input and provide a total estimate of annual CO2e equipment leak and combustion emissions. Enter this total into the CO2e emissions field for natural gas distribution in the applicability tool. Data Collection Year 2014 and later - This tool has been updated from previous versions to account for a change in the global warming potential (GWP) of methane (CH4) that is applicable in 2014 and later years. This tool should not be used for years 2011 to 2013. For years 2011 to 2013, use the version of the tool that is in the GHGRP Applicability Tool archive. For screening purposes related to co-located industry segments, emissions from all applicable industry segments should be combined to determine whether the emissions from the facility with the co-located industry segments would exceed the 25,000 metric ton CO2e reporting threshold.
Methane Emissions Source | Input Data | Units | Emissions (metric tons CO2e/year)
Above ground meters and regulators (at custody and non-custody transfer city gate stations) |  | number of stations with inlet pressure >300 psig | 0
|  | number of stations with inlet pressure 100-300 psig | 0
|  | number of stations with inlet pressure <100 psig | 0
Below ground meters and regulators and vault equipment leaks |  | number of stations in vaults with inlet pressure >300 psig | 0
|  | number of stations in vaults with inlet pressure 100-300 psig | 0
|  | number of stations in vaults with inlet pressure <100 psig | 0
Pipeline main equipment leaks |  | miles of cast iron pipeline mains | 0
|  | miles of unprotected steel pipeline mains | 0
|  | miles of pipeline mains for all other materials | 0
Service line equipment leaks |  | number of unprotected steel services | 0
|  | number of services for all other materials | 0
Combustion emissions:
Compressor engine exhaust |  | total million horsepower hours for all compressors in one year (MMHPhr) | 0
|  | Distribution Total (metric tons CO2e/year) | 0
Please see the "Guidance & Sources" tab for further information on the calculation methodologies of the above emissions sources.
Note:
The emissions factors and calculation methods used in this tool are based on publicly available sources including: the Technical Support Document for Subpart W; the U.S. GHG Inventory; and the 2009 API Compendium. More details can be found in the Guidance and Sources tab of this worksheet. This tool is only a guide to help companies determine their Subpart W applicability. The results of this tool are not legally binding. A reporter must make the final determination regarding their Subpart W applicability.
Applicability Tool Disclaimer The content provided in the applicability tool is intended solely as compliance assistance for potential reporters to aid in assessing whether they are required to report under the Greenhouse Gas Mandatory Reporting Rule. Any variation between the rule and the information provided in this tool is unintentional, and, in the case of such variations, the requirements of the rule govern. The applicability tool and its contents do not constitute rulemaking or a decision by EPA and may not be relied upon to create a substantive or procedural right or benefit enforceable by law, or in equity, by any person. While this tool is designed to help potential reporters comply with the rule, compliance with all Federal, State, and Local laws and regulations remains the sole responsibility of each facility owner or operator subject to those laws and regulations. Use of this tool does not constitute an assessment by EPA of the applicability of the rule to any particular facility. In any particular case, EPA will make its assessment by applying the law and regulations to the specific facts of the case. No information entered by the user is maintained by EPA, and any results generated by the applicability tool, along with additional information entered by the user, do not constitute a submission for purposes of compliance with the rule.

## Guidance & Sources
Guidance for Natural Gas Distribution Tool (Subpart W)
2013-11-29
This sheet provides details on the data sources, equations and emission calculation methodologies, and conversions used in this screening tool.
Data Collection Year 2014 and later - This tool has been updated from previous versions to account for a change in the global warming potential (GWP) of methane (CH4) that is applicable in 2014 and later years. This tool should not be used for years 2011 to 2013. For years 2011 to 2013, use the version of the tool that is in the GHGRP Applicability Tool archive.
Emission Source | Activity Factor (Input Required) | General Methodology/Equation | Default Methane EF | Methane EF Units | Methane EF Sources | Methane EF Comments | Default CO2 EF | CO2 EF Units | CO2 EF Sources | CO2 EF Comments
Above ground meters and regulators (at custody and non-custody transfer city gate stations) 98.232 (i)(1) and 98.232 (i)(2) | Number of stations with inlet pressure >300 psig | CH4 EF * Number of >300 psig stations | 179.8 | scfh CH4/station | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 10, page no. 15, table 5-1 | For inlet pressure >300 psig EF is for metering/pressure regulating stations located aboveground | N/A | N/A | N/A | N/A
| Number of stations with inlet pressure 100-300 psig | CH4 EF * Number of 100-300 psig stations | 95.6 | scfh CH4/station | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 10, page no. 15, table 5-1 | For inlet pressure 100-300 psig EF is for metering/pressure regulating stations located aboveground | N/A | N/A | N/A | N/A
| Number of stations with inlet pressure <100 psig | CH4 EF * Number of <100 psig stations | 4.31 | scfh CH4/station | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 10, page no. 15, table 5-1 | For inlet pressure <100 psig EF is for metering/pressure regulating stations located aboveground | N/A | N/A | N/A | N/A
Below ground meters and regulators and vault equipment leaks 98.232 (i)(3) | Number of stations in vaults with inlet pressure >300 psig | CH4 EF * Number of >300 psig stations | 1.3 | scfh CH4/station | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 10, page no. 15, table 5-1 EPA. Background Technical Support Document (docket # EPA-HQ-OAR-2009-0923) for Subpart W. <www.regulations.gov>. | For inlet pressure >300 psig EF is for regulating stations located in vaults | N/A | N/A | N/A | N/A
| Number of stations in vaults with inlet pressure 100-300 psig | CH4 EF * Number of 100-300 psig stations | 0.2 | scfh CH4/station | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 10, page no. 15, table 5-1 EPA. Background Technical Support Document (docket # EPA-HQ-OAR-2009-0923) for Subpart W. <www.regulations.gov>. | For inlet pressure 100-300 psig EF is for regulating stations located in vaults | N/A | N/A | N/A | N/A
| Number of stations in vaults with inlet pressure <100 psig | CH4 EF * Number of <100 psig stations | 0.1 | scfh CH4/station | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 10, page no. 15, table 5-1 EPA. Background Technical Support Document (docket # EPA-HQ-OAR-2009-0923) for Subpart W. <www.regulations.gov>. | For inlet pressure <100 psig EF is for regulating stations located in vaults | N/A | N/A | N/A | N/A
Pipeline main equipment leaks 98.232 (i)(4) | Miles of cast iron pipeline mains | CH4 EF * miles of cast iron pipeline mains | 238.7 | Mscf CH4/mile-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39, table 8-2 | For cast iron | N/A | N/A | N/A | N/A
| Miles of unprotected steel pipeline mains | CH4 EF * miles of unprotected steel pipeline mains | 110.19 | Mscf CH4/mile-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39,42, 56, table 8-2, 8-4, 9-2 | For unprotected steel | N/A | N/A | N/A | N/A
| Miles of protected steel pipeline mains | CH4 EF * miles of protected steel pipeline mains | 3.07 | Mscf CH4/mile-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39,42, 56, table 8-2, 8-4, 9-2 | For protected steel | N/A | N/A | N/A | N/A
| Miles of plastic pipeline mains | CH4 EF * miles of plastic pipeline mains | 9.91 | Mscf CH4/mile-year | ICF memo on plastic pipe EF dated June 30, 2005. This EF is an average of GRI and SoCal emissions estimates | For plastic | N/A | N/A | N/A | N/A
Service line equipment leaks 98.232 (i)(5) | Number of unprotected steel services | CH4 EF * number of unprotected steel services | 1.7 | Mscf CH4/service-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39,42, 56, table 8-2, 8-4, 9-2 | For unprotected steel | N/A | N/A | N/A | N/A
| Number of protected steel services | CH4 EF * number of protected steel services | 0.18 | Mscf CH4/service-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39,42, 56, table 8-2, 8-4, 9-2 | For protected steel | N/A | N/A | N/A | N/A
| Number of plastic services | CH4 EF * number of plastic services | 0.01 | Mscf CH4/service-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39,42, 56, table 8-2, 8-4, 9-2 | For plastic | N/A | N/A | N/A | N/A
| Number of copper services | CH4 EF * number of copper services | 0.25 | Mscf CH4/service-year | GRI - 94 - Methane Emissions from the Natural Gas Industry, Volume 9, page no. 39,42, 56, table 8-2, 8-4, 9-2 | For copper | N/A | N/A | N/A | N/A
Compressor engine exhaust (combustion emissions: CH4 and CO2) 98.232 (i)(6) | Total horsepower hours for all compressors in one year | (CH4 EF + CO2 EF) * Total horsepower hours for all compressors in one year | 0.24 | scf CH4/HPhr | GRI/EPA, Methane Emissions from the Natural Gas Industry, Vol.11, April 1996. pg 11 | 2006 Petroleum ("Gas Engines") & NG ("Gas Engines", all regions) Inventories | 719.3988 | tCO2/MMHPhr | 0.0531 tonnes CO2/10^6 BTU [EF for "Natural Gas (Pipeline)" fuel; Low Heating Value] 2004 API Compendium. Table 4-1. pg 4-8 (PDF pg 81) | CO2 EF per rig calculated from original combustion EF in Table 4-1 assuming: 1) 0.24 scf CH4/HPhr (1996 GRI. Vol: 11) 2) 98% combustion efficiency 3) 0.93 methane content in gas 4) 12.90 scf natural gas/HPhr 5) 1,050 BTU/scf gas 6) 13,548 BTU/HPhr
Notes:
1) Customer meters (residential, commercial, industrial) are excluded from this screening tool. Neither above nor below ground meters and regulators include them.
2) Because of their minimal emissions, miles of protected steel and plastic pipeline mains were combined into one source in the "Emissions Calcs" tab. This was done using an average of the 2 EFs from the 1996 GRI study.
3) Because of their minimal emissions, number of protected steel, plastic, and copper services were combined into one source in the "Emissions Calcs" tab. This was done using an average of the 3 EFs from the 1996 GRI study.
4) Combustion emissions from compressor engine exhaust are calculated using CO2 and CH4 EFs with the assumption of 98% efficiency. N2O emissions are excluded.
Conversions:
From | To | Factor
scf CH4 | tCO2e | 0.000479
Applicability Tool Disclaimer The content provided in the applicability tool is intended solely as compliance assistance for potential reporters to aid in assessing whether they are required to report under the Greenhouse Gas Mandatory Reporting Rule. Any variation between the rule and the information provided in this tool is unintentional, and, in the case of such variations, the requirements of the rule govern. The applicability tool and its contents do not constitute rulemaking or a decision by EPA and may not be relied upon to create a substantive or procedural right or benefit enforceable by law, or in equity, by any person. While this tool is designed to help potential reporters comply with the rule, compliance with all Federal, State, and Local laws and regulations remains the sole responsibility of each facility owner or operator subject to those laws and regulations. Use of this tool does not constitute an assessment by EPA of the applicability of the rule to any particular facility. In any particular case, EPA will make its assessment by applying the law and regulations to the specific facts of the case. No information entered by the user is maintained by EPA, and any results generated by the applicability tool, along with additional information entered by the user, do not constitute a submission for purposes of compliance with the rule.