## Table 1
Case-By-Case (Appendix E) Lookup Table, MASSACHUSETTS Criteria are found in 314 CMR 4.00: https://www.mass.gov/doc/314-cmr-400/download
Please note: this lookup table is not for use for applying wastewater limits under Part 2.1.1 or impaired waters limits under Appendix G
Steps for use:
1. Input highlighted values to adjust water quality criteria for water chemistry and/or dilution
Dilution Factor (must be ≥1) | Critical Low Flow (MGD) | Discharge Flow (MGD) | Hardness mg/L | pH (SU)
1 | 0 | 0.144 | 20 | 7
2. If a POLLUTANT listed below is present at any concentration in your source water (i.e., groundwater,stormwater, potable water, surface water), your treatment system (i.e., chemicals),
the discharge (based on existing monitoring data), or soil/sediment, complete steps 3 and 4; enter these values in your NOI tables for Case-by-Case Limits; if a POLLUTANT is not listed, skip to step 5
3. Select the lowest value for your WATERBODY and POLLUTANT for "Daily Max"; multiply this value by your dilution factor (do not multiply by dilution if the POLLUTANT is connected to an impairment, e.g., metals impairment and the POLLUTANT is any metal) - this is your daily max limit
4. Select the lowest "Monthly Avg" value for your WATERBODY and POLLUTANT; multiply this value by your dilution factor (do not multiply by dilution if the POLLUTANT is connected to an impairment) - this is your monthly avg limit only if it is < "Daily Max" or if there is no "Daily Max" limit
5. For any "Monthly Avg" or "Daily Max" value that is below the minimum level of detection for the POLLUTANT, enter the compliance level shown for that POLLUTANT.
6. If the POLLUTANT is present in SOIL-ONLY, select the box for "present in soil-only." If the POLLUTANT is not listed in Part 2.1.1 or Appendix E, select the box for "Required Monitoring" for Daily Max only (do not select "Required Monitoring" for any POLLUTANT with limit(s) because this applies monitoring only, no limits)
WATERBODY | Freshwater Class A/B |  | Coastal and Marine Class SA/SB |  | Drinking Water Supplies Only | Class A/SA/B/SB | Class A/SA/B/SB | Only if taste/odor impairment is caused by the pollutant | Limits |  |  |  | Compliance Level
POLLUTANT | Acute Aquatic Life (Daily Max) µg/L | Chronic Aquatic Life (Monthly Avg) µg/L | Acute Aquatic Life (Daily Max) µg/L | Chronic Aquatic Life (Monthly Avg) µg/L | Drinking Water Plus Fish and Shellfish Consumption (Monthly Avg) µg/L | Fish and Shellfish Consumption (Monthly Avg) µg/L | Maximum Value (TBEL) (Daily Max) µg/L | Organoleptic Effect Criteria (Daily Max) µg/L | Daily Max Criteria (See Step 3) | Daily Max Criteria x DF | Monthly Avg Criteria (See Step 4) | Monthly Avg Criteria x DF | If any limit is below the lowest analytical minimum level for a parameter, enter the compliance level shown, rather than the limit
Acenaphthene | -- | -- | -- | -- | 70 | 90 |  | 20 |  | 0 |  | 0
Acetone | -- | -- | -- | -- | -- | -- | 7970 | -- |  | 0 |  | 0
Acrolein | 3 | 3 | -- | -- | 3 | 400 | -- | -- |  | 0 |  | 0
Acrylonitrile | -- | -- | -- | -- | 0.061 | 7 | -- | -- |  | 0 |  | 0
Aldrin | 1.5 | -- | 0.65 | -- | 7.7e-07 | 7.7e-07 | -- | -- |  | 0 |  | 0
Alkalinity | -- | 20000 | -- | -- | -- | -- | -- | --
Aluminum (Default Criteria by Watershed) | -- | -- | -- | -- | -- | -- | -- | --
Blackstone | 532 | 262 | -- | -- | -- | -- | -- | --
Boston Harbor/Charles | 978 | 380 | -- | -- | -- | -- | -- | --
Buzzards Bay/Mt Hope Bay/Narragansett Bay/Ten Mile | 451 | 230 | -- | -- | -- | -- | -- | --
Cape Cod Coastal32 | -- | -- | -- | -- | -- | -- | -- | --
Chicopee (5th percentile) | 290 | 170 | -- | -- | -- | -- | -- | --
Connecticut (5th percentile) | 600 | 290 | -- | -- | -- | -- | -- | --
Deerfield | 440 | 220 | -- | -- | -- | -- | -- | --
Farmington/Westfield (5th percentile) | 299 | 169 | -- | -- | -- | -- | -- | --
French/Quinebaug | 570 | 270 | -- | -- | -- | -- | -- | --
Housatonic/Hudson | 1400 | 515 | -- | -- | -- | -- | -- | --
Ipswich/North Coastal/Parker | 932 | 396 | -- | -- | -- | -- | -- | --
Islands Coastal32 | -- | -- | -- | -- | -- | -- | -- | --
Merrimack/Shawsheen (5th percentile) | 460 | 249 | -- | -- | -- | -- | -- | --
Millers | 329 | 200 | -- | -- | -- | -- | -- | --
Nashua (5th percentile) | 368 | 200 | -- | -- | -- | -- | -- | --
South Coastal | 1200 | 460 | -- | -- | -- | -- | -- | --
Sudbury, Assabet, and Concord (SuAsCo) | 940 | 394 | -- | -- | -- | -- | -- | --
Taunton (5th percentile) | 300 | 190 | -- | -- | -- | -- | -- | --
Ammonia | the calculated concentration using the applicable equation provided in Appendix B | the calculated concentration using the applicable equation provided in Appendix B | 0.233 mg/L (as un-ionized (NH3) ammonia) or the concentration of total ammonia (NH3 + NH4+) as provided in Table 2 of EPA's "Ambient Water Quality Criteria for Ammonia (Saltwater) - 1989", EPA 440/5-88-004 (Ammonia Criteria, 1989)3 However the criterion is determined, the Standard CMC Frequency & Duration applies | 0.035 mg/L (as un-ionized (NH3) ammonia) or the concentration of total ammonia (NH3 + NH4+), as provided in Table 3 of EPA's Ammonia Criteria, 19893 However the criterion is determined, the Standard CCC Frequency & Duration applies | -- | -- | -- | --
Anthracene | -- | -- | -- | -- | 300 | 400 | -- | --
Antimony | -- | -- | -- | -- | 5.6 | 640 | 206 | --
Arsenic | 340 | 150 | 69 | 36 | 0.018 | 0.14 | 104 | --
Asbestos | -- | -- | -- | -- | 7 million fibers/L | -- | -- | --
Bacteria (Pathogens) | -- | -- | -- | -- | See 314 CMR 4.05(3), (4), and (5)(f) | -- | -- | --
Barium | -- | -- | -- | -- | 1000 | -- | -- | --
Benzene | -- | -- | -- | -- | 0.58-2.1 | 16-58 | 5 | --
Benzidine | -- | -- | -- | -- | 0.00014 | 0.011 | -- | --
Benzo(a)anthracene (PAH) | -- | -- | -- | -- | 0.0012 | 0.0013 | -- | --
Benzo(a)pyrene (PAH) | -- | -- | -- | -- | 0.00012 | 0.00013 | -- | --
Benzo(b)fluoranthene (PAH) (also known as 3,4-benzofluoranthene) | -- | -- | -- | -- | 0.0012 | 0.0013 | -- | --
Benzo(k)fluoranthene (PAH) | -- | -- | -- | -- | 0.012 | 0.013 | -- | --
Beryllium | -- | -- | -- | -- | 3.7 ng/L | 64 ng/L | -- | --
Bis(2-Chloroethyl) Ether | -- | -- | -- | -- | 0.03 | 2.2 | -- | --
Bis(Chloromethyl) Ether | -- | -- | -- | -- | 0.00015 | 0.017 | -- | --
Bis(2-Chloro-1-methylethyl) Ether (also known as Bis(2-Chloroisopropyl) Ether) | -- | -- | -- | -- | 200 | 4000 | -- | --
Bis(2-Ethylhexyl) Phthalate (also known as Di(2-Ethylhexyl)-Phthalate) | -- | -- | -- | -- | 0.32 | 0.37 | 101 | --
Bromoform36 (also known as tribromomethane) | -- | -- | -- | -- | 7 | 120 | -- | --
Butylbenzyl Phthalate | -- | -- | -- | -- | 0.1 | 0.1 | -- | --
Cadmium | 0.41539 | 0.082129 | 33.1992 | 7.9477 | 5 | -- | 10.2 | --
Carbon Tetrachloride | -- | -- | -- | -- | 0.4 | 5 | 4.4 | --
Carbaryl | 2.1 | 2.1 | 1.6 | -- | -- | -- | -- | --
Chlordane | 1.2 | 0.0043 | 0.045 | 0.004 | 0.00031 | 0.00032 | -- | --
Chloride | 860000 | 230000 | -- | -- | -- | -- | -- | --
Chlorine | 19 | 11 | 13 | 7.5 | -- | -- | 200 | --
Chlorobenzene (also known as monochlorobenzene) | -- | -- | -- | -- | 100 | 800 | -- | 20
Chlorodibromomethane36 (also known as dibromochloromethane) | -- | -- | -- | -- | 0.8 | 21 | -- | --
Chloroform36 (also known as trichloromethane) | -- | -- | -- | -- | 60 | 2000 | -- | --
2-Chloronaphthalene | -- | -- | -- | -- | 800 | 1000 | -- | --
2-Chlorophenol | -- | -- | -- | -- | 30 | 800 | -- | 0.1
3-Chlorophenol | -- | -- | -- | -- | -- | -- | -- | 0.1
4-Chlorophenol | -- | -- | -- | -- | -- | -- | -- | 0.1
Chlorophenoxy Herbicide (also known as 2,4-D) | -- | -- | -- | -- | 70 | 12000 | -- | --
Chlorophenoxy Herbicide (also known as 2,4,5-TP or Silvex) | -- | -- | -- | -- | 50 | 400 | -- | --
Chlorpyrifos | 0.083 | 0.041 | 0.011 | 0.0056 | -- | -- | -- | --
Chromium (III) | 482.5597 | 23.0647 | -- | -- | -- | -- | 323 | --
Chromium (VI) | 16.2933 | 11.4345 | 1107.7543 | 50.3525 | -- | -- | 323 | --
Chromium (total) | -- | -- | -- | -- | 100 | -- | -- | --
Chrysene (PAH) | -- | -- | -- | -- | 0.12 | 0.13 | -- | --
cis-1,2-Dichloroethylene | -- | -- | -- | -- | -- | -- | 70 | --
Copper | 3.0728 | 2.3581 | 5.7831 | 3.7349 | 1300 | -- | 242 | 1000
Cyanide | 22 | 5.2 | 1 | 1 | 4 | 400 | 178000 | --
4,4'-DDT | 0.4 | 0.001 | 0.07 | 0.001 | -- | -- | -- | --
Demeton | -- | 0.1 | -- | 0.1 | -- | -- | -- | --
Diazinon | 0.17 | 0.17 | 0.82 | 0.82 | -- | -- | -- | --
Dibenzo(a,h)anthracene | -- | -- | -- | -- | 0.00012 | 0.00013 | -- | --
1,2-Dichlorobenzene (also known as o-DCB) | -- | -- | -- | -- | 600 | 3000 | 600 | --
1,3-Dichlorobenzene | -- | -- | -- | -- | 7 | 10 | 320 | --
1,4-Dichlorobenzene (also known as p-DCB) | -- | -- | -- | -- | 5 | 900 | 5 | --
3,3'-Dichlorobenzidine | -- | -- | -- | -- | 0.049 | 0.15 | -- | --
Dichlorobromomethane36 (also known as Bromodichloromethane) | -- | -- | -- | -- | 0.95 | 27 | -- | --
p,p'-Dichlorodiphenyldichloroethane (also known as DDD) | -- | -- | -- | -- | 0.00012 | 0.00012 | -- | --
p,p'-Dichlorodiphenyldichloroethylene (also known as DDE) | -- | -- | -- | -- | 1.8e-05 | 1.8e-05 | -- | --
p,p'-Dichlorodiphenyltrichloroethane (also known as DDT) | -- | -- | -- | -- | 3e-05 | 3e-05 | -- | --
1,1-Dichloroethane | -- | -- | -- | -- | -- | -- | 70 | --
1,2-Dichloroethane | -- | -- | -- | -- | 5 | 650 | 5 | --
1,1-Dichloroethylene | -- | -- | -- | -- | 7 | 20000 | 3.2 | --
2,3-Dichlorophenol | -- | -- | -- | -- | -- | -- | -- | 0.04
2,4-Dichlorophenol | -- | -- | -- | -- | 10 | 60 | -- | 0.3
2,5-Dichlorophenol | -- | -- | -- | -- | -- | -- | -- | 0.5
2,6-Dichlorophenol | -- | -- | -- | -- | -- | -- | -- | 0.2
1,2-Dichloropropane | -- | -- | -- | -- | 0.9 | 31 | -- | --
1,3-Dichloropropene | -- | -- | -- | -- | 0.27 | 12 | -- | --
Dieldrin | 0.12 | 0.05614 | 0.36 | -- | 1.2e-06 | 1.2e-06 | -- | --
Diethyl Phthalate | -- | -- | -- | -- | 600 | 600 | -- | --
2,4-Dimethylphenol | -- | -- | -- | -- | 100 | 3000 | -- | 400
Dimethyl Phthalate | -- | -- | -- | -- | 2000 | 2000 | -- | --
Di-n-Butyl Phthalate | -- | -- | -- | -- | 20 | 30 | -- | --
Dinitrophenols | -- | -- | -- | -- | 10 | 1000 | -- | --
2,4-Dinitrophenol | -- | -- | -- | -- | 10 | 300 | -- | --
2,4-Dinitrotoluene | -- | -- | -- | -- | 0.049 | 1.7 | -- | --
Dioxin (also known as 2,3,7,8- Tetrachloro-dibenzo-p-dioxin or TCDD) | -- | -- | -- | -- | 5e-09 | 5.1e-09 | -- | --
1,4-Dioxane | -- | -- | -- | -- | -- | -- | 200 | --
1,2-Diphenylhydrazine | -- | -- | -- | -- | 0.03 | 0.2 | -- | --
alpha-Endosulfan beta-Endosulfan | 0.11 | 0.056 | 0.017 | -- | -- | -- | -- | --
alpha-Endosulfan | -- | -- | -- | -- | 20 | 30 | -- | --
beta-Endosulfan | -- | -- | -- | -- | 20 | 40 | -- | --
Endosulfan Sulfate | -- | -- | -- | -- | 20 | 40 | -- | --
Endrin | 0.086 | 0.036 | 0.018 | -- | 0.03 | 0.03 | -- | --
Endrin Aldehyde | -- | -- | -- | -- | 1 | 1 | -- | --
Ethylbenzene | -- | -- | -- | -- | 68 | 130 | -- | --
Ethylene Dibromide | -- | -- | -- | -- | -- | -- | 0.05 | --
Fluoranthene | -- | -- | -- | -- | 20 | 20 | -- | --
Fluorene (PAH) | -- | -- | -- | -- | 50 | 70 | -- | --
Guthion | -- | 0.01 | -- | 0.01 | -- | -- | -- | --
Heptachlor | 0.3 | 0.0038 | 0.03 | 0.0036 | 5.9e-06 | 5.9e-06 | -- | --
Heptachlor Epoxide | 0.3 | 0.0038 | 0.03 | 0.0036 | 3.2e-05 | 3.2e-05 | -- | --
Hexachlorobenzene | -- | -- | -- | -- | 7.9e-05 | 7.9e-05 | -- | --
Hexachlorobutadiene | -- | -- | -- | -- | 0.01 | 0.01 | -- | --
alpha-Hexachlorocyclohexane (also known as alpha-HCH) | -- | -- | -- | -- | 0.00036 | 0.00039 | -- | --
beta-Hexachlorocyclohexane (also known as beta-HCH) | -- | -- | -- | -- | 0.008 | 0.014 | -- | --
gamma-Hexachl orocyclohexane (also known as gamma-HCH, gamma-BHC, or Lindane) | 0.95 | -- | 0.08 | -- | -- | -- | -- | --
gamma-Hexachlorocyclohexane (also known as gamma-HCH or Lindane) | -- | -- | -- | -- | 0.2 | 4.4 | -- | --
Hexachlorocyclohexane -Technical (also known as technical HCH) | -- | -- | -- | -- | 0.0066 | 0.01 | -- | --
Hexachlorocyclopentadiene | -- | -- | -- | -- | 4 | 4 | -- | 1
Hexachloroethane | -- | -- | -- | -- | 0.1 | 0.1 | -- | --
Indeno(1,2,3-cd) pyrene (PAH) | -- | -- | -- | -- | 0.0012 | 0.0013 | -- | --
Iron | -- | 1000 | -- | -- | -- | -- | 5000 | 300
Isophorone | -- | -- | -- | -- | 34 | 1800 | --
Lead | 10.523 | 0.41007 | 220.8202 | 8.5174 | -- | -- | 160
Malathion | -- | 0.1 | -- | 0.1 | -- | -- | --
Manganese | -- | -- | -- | -- | 50 | 100 | --
Mercury | 1.6471 | 0.90588 | 2.1176 | 1.1059 | 2 | -- | 0.739
Methylmercury | -- | -- | -- | -- | -- | 0.3 mg/kg | --
Methoxychlor | -- | 0.03 | -- | 0.03 | 0.02 | 0.02 | --
2-Methyl-4-Chlorophenol | -- | -- | -- | -- | -- | -- | -- | 1800
3-Methyl-4-Chlorophenol (also known as p-chloro-m-cresol) | -- | -- | -- | -- | 500 | 2000 | -- | 3000
3-Methyl-6-Chlorophenol | -- | -- | -- | -- | -- | -- | -- | 20
2-Methyl-4,6-Dinitrophenol | -- | -- | -- | -- | 2 | 30 | --
Methyl Bromide | -- | -- | -- | -- | 100 | 10000 | --
Methyl-tert-butyl-Ether | [6 empty] | 70 | 20
Methylene Chloride (also known as Dichloromethane) | -- | -- | -- | -- | 5 | 1000 | 4.6 | --
Mirex | -- | 0.001 | -- | 0.001 |  |  | -- | --
Naphthalene | -- | -- | -- | -- | -- | -- | 20 | --
Nickel | 120.2279 | 13.367 | 74.7475 | 8.2828 | 100 | 4600 | 1450 | --
Nitrate (as N) (criterion also applies to total nitrate/nitrite) | -- | -- | -- | -- | 10000 | -- | -- | --
Nitrite | -- | -- | -- | -- | 1000 | -- | -- | --
Nitrobenzene | -- | -- | -- | -- | 10 | 600 | -- | 30
Nitrogen/Phosphorus | See 314 CMR 4.05(5)(e) |  |  |  | -- | -- | -- | --
Nitrosamines | -- | -- | -- | -- | 0.0008 | 1.24 | -- | --
Nitrosodibutylamine | -- | -- | -- | -- | 0.0063 | 0.22 | -- | --
Nitrosodiethylamine | -- | -- | -- | -- | 0.0008 | 1.24 | -- | --
Nitrosopyrrolidine | -- | -- | -- | -- | 0.016 | 34 | -- | --
N-Nitrosodimethylamine (also known as NDMA) | -- | -- | -- | -- | 0.00069 | 3 | -- | --
N-Nitrosodi-n-Propylamine | -- | -- | -- | -- | 0.005 | 0.51 | -- | --
N-Nitrosodiphenylamine | -- | -- | -- | -- | 3.3 | 6 | -- | --
Nonylphenol | 28 | 6.6 | 7 | 1.7 | -- | -- | -- | --
Parathion | 0.065 | 0.013 | -- | -- | -- | -- | -- | --
Pentachlorobenzene | -- | -- | -- | -- | 0.1 | 0.1 | -- | --
Pentachlorophenol | 8.7233 | 6.6926 | 13 | 7.9 | 0.03 | 0.04 | 1 | 30
pH | 6.5-8.3 |  | 6.5-8.5 |  | -- | -- | 6.0-9.0 | --
Phenol | -- | -- | -- | -- | 4000 | 300000 | 1080 | 300
Phosphorus, Elemental | -- | -- | -- | 0.1 | -- | -- | -- | --
Polychlorinated Biphenyls (PCBs) | -- | 0.014 | -- | 0.03 | 6.4e-05 | 6.4e-05 | 0.5 | -- |  |  |  |  | 0.1
Pyrene (PAH) | -- | -- | -- | -- | 20 | 30 | -- | --
Selenium | 1/[(f1/185.9) + (f2/12.82)], where f1 and f2 are the fractions of total selenium as selenite and selenate, respectively | 5 | 290.5812 | 71.1423 | 50 | 4200 | 235.8 | --
Silver | 0.23756 | -- | 1.1176 | -- | -- | -- | 35.1 | --
Solids (Dissolved) and Salinity |  |  |  |  | 250000 | -- | -- | --
Sulfide- Hydrogen Sulfide | -- | 2 | -- | 2 | -- | -- | -- | --
Temperature | See Part 6 of the DRGP | [5 empty] | -- | --
tert-Butyl Alcohol | -- | -- | -- | -- | -- | -- | 120 | --
tert-Amyl Methyl Ether | -- | -- | -- | -- | -- | -- | 90 | --
1,2,4,5-Tetrachlorobenzene | -- | -- | -- | -- | 0.03 | 0.03 | -- | --
Tetrachloroethylene | -- | -- | -- | -- | 10 | 29 | 5 | --
1,1,2,2-Tetrachloroethane | -- | -- | -- | -- | 0.2 | 3 | -- | --
2,3,4,6-Tetrachlorophenol | -- | -- | -- | -- | -- | -- | -- | 1
Thallium | -- | -- | -- | -- | 0.24 | 0.47 | -- | --
Toluene | -- | -- | -- | -- | 57 | 520 | -- | --
Total BTEX (sum of benzene, toluene, ethylbenzene and xylenes) | -- | -- | -- | -- | -- | -- | 100 | --
Total Group I PAHs | -- | -- | -- | -- | -- | -- | 0.35 | -- |  |  |  |  | 0.05
Total Group II PAHs | -- | -- | -- | -- | -- | -- | 100 | --
Total Petroleum Hydrocarbons | -- | -- | -- | -- | -- | -- | 5000 | --
Total Phthalates | -- | -- | -- | -- | -- | -- | 190 | --
Total Trihalomethanes (TTHM) (the sum of bromodichloromethane, dibromochloro- methane, bromoform (tribromomethane) and chloroform (trichloromethane)) | -- | -- | -- | -- | 80 | -- | -- | --
Toxaphene | 0.73 | 0.0002 | 0.21 | 0.0002 | 0.0007 | 0.00071 | -- | --
Tributyltin (TBT) | 0.46 | 0.072 | 0.42 | 0.0074 |  |  | -- | --
Trans-1,2-Dichloroethylene | -- | -- | -- | -- | 100 | 4000 | -- | --
1,2,4-Trichlorobenzene | -- | -- | -- | -- | 0.071 | 0.076 | -- | --
Trichloroethylene | -- | -- | -- | -- | 0.6 | 7 | 5 | --
1,1,1-Trichloroethane | -- | -- | -- | -- | 200 | 200000 | 200 | --
1,1,2-Trichloroethane | -- | -- | -- | -- | 0.55 | 8.9 | 5 | --
2,3,4,6-Trichlorophenol | -- | -- | -- | -- | -- | -- | -- | 1
2,4,5-Trichlorophenol | -- | -- | -- | -- | 300 | 600 | -- | 1
2,4,6-Trichlorophenol | -- | -- | -- | -- | 1.5 | 2.8 | -- | 2
Vinyl Chloride | -- | -- | -- | -- | 0.022 | 1.6 | 2 | --
Zinc | 30.6393 | 30.6393 | 95.1374 | 85.6237 | 7400 | 26000 | 420 | 5000