MEMORANDUM

May 28, 2002

TO: 		Environmental Caucus of MACT WG

Bill O’ Sullivan

John Paul

FROM:	 Martha Keating

Re: 		Non-Hg HAPs Analysis

Using the data provided to the Utility MACT subgroup, I have compiled and sorted the data for the metals (other than mercury) from the utility boiler stack tests.  I have also compiled the limited data for the acid gases.  The conclusions I drew from the data are presented below. In addition, I have included a number of suggestions concerning surrogate measures, and the rationale for these suggestions, provided to me by Bill O’ Sullivan.  I hope this information will further the WG’s discussion of these pollutants.

# Metals

I looked at the metals data 2 different ways. First, I compiled the percent removal data for each tested boiler (see file metals_by_site.xcl). Then I sorted the data by metal across sites (see file metals_by_pollutant.xcl) and looked at the range of percent removal. (Note that I deleted data points where there was not both inlet and outlet data.) Several things immediately jump out:

- Removal efficiencies for all of the metals except selenium are, in most cases, in excess of 90% and typically 95% or higher.

- There is a range of removal efficiency for some of the metals, however when the data are grouped by boiler, you can clearly see that the poor removal efficiencies are limited to certain test sites. In other words, certain sites clearly stand out as having lower removal efficiencies regardless of the metal. Adding the fuel type and control device to the data set revealed that the boilers with the poor removal efficiencies were more likely to burn either lignite or subbituminous coal (except 3 fired bituminous coal and had either an FGD (2) or a CS-ESP (1)).

- Selenium removal efficiencies vary across the tested sites. These date were looked at separately (see file selenium removal.xcl).

- There are 34 tests. Therefore, calculating a MACT floor would mean taking the average removal efficiency of the top 12% or 4 sites.

- For every metal, including selenium, the average of the top 12% is 99 percent removal.  (Note that even though there is a range of removal efficiencies for selenium, the top 12% still achieve 99% removal.)

I conclude from these data that grouping the metals is appropriate, because their removal efficiencies are so similar, and further that separate categories for some metals are not needed.  It is also apparent that if EPA subcategorizes by fuel type, the floor for metals would not be 99%. In fact the data are far more variable for different metals when lignite and subbituminous coal are burned. In the event of fuel subcategories, we may need to look again at grouping the metals differently.

# Acid Gases

I also compiled just the data for the acid gases (see file HCL_HF rmoval.xcl). There are just a few data points with both inlet and outlet data, and in my opinion they are inadequate for a floor calculation. Most have outlet concentrations higher than the inlet.

# Surrogate Measures

The following suggestions (and supporting rationale) are put forth by Bill O’Sullivan and get to the heart of the next question: how to we measure the removal of the metals and other pollutants? Bill makes specific suggestions for surrogate pollutants and what their levels could be. A couple of issues that remain in my mind is first, for the metals, does the surrogate measure represent 99% removal which would be the MACT floor? Second, for the other pollutants, how do we justify stringent levels, even with a surrogate measure, if the emissions test data are not adequate to set a floor?

From Bill O’ Sullivan:

Following up on the 5/13/2002 utility MACT workgroup meeting, here is a state air regulator (who is also a mechanical engineer) common sense proposal for dealing with other HAPs from coal fired power plants. This proposal uses surrogates for all HAPs (other than Hg) and recognizes that existing air pollution control technology and methods in common use for the criteria air pollutants also reduce HAP emissions from coal boilers. 

1. Particulate HAPs - Use particulate NSPS as MACT surrogate. 

Particulate HAP emissions from coal firing are primarily metals, and also include polycyclic organic matter (POM). Coal combustion is the largest, or amongst the largest, source category for emission of many heavy metal HAPs in the USA. Coal combustion is generally not a large emitter of POMs, provided good combustion is maintained. (See 3 below.)

The existing NSPS for particulates can be applied to all coal plants as a minimum MACT requirement for particulate HAPs. The NSPS is 0.030 lbs. per million Btu. Actual particulate levels with large ESPs or baghouses are typically under 0.010 lbs. per million Btu. Older non-NSPS units emit near 0.100 lb./million Btu or higher particulate levels. Hence, applying the NSPS can get 90% or greater particulate reduction and similar particulate HAP reductions for non-NSPS units. To the extent that certain particulate HAPs are concentrated in the finest particulates (i.e. lead, arsenic and cadmium), increasing the effectiveness of total particulate control could provide a proportionally higher level of particulate HAP control.

Applying the existing particulate NSPS would likely result in emissions of significant amounts of heavy metals being reduced by 90% or greater from non-NSPS coal units. Better particulate control would also reduce mercury emissions and POM emissions.

2. Acid Gas HAPs - Use SO2 NSPS as MACT surrogate.

Hydrochloric acid (HCl) and hydroflouric acid (HF) are the primary HAP acid gases emitted by coal fired power plants. Hydrochloric acid is the HAP emitted in highest amount in the USA, and coal combustion emits more hydrochloric acid than any other source category in the USA. 

Hydrochloric acid is readily controlled by scrubber technology for sulfur dioxide control. It is usually controlled at higher removal efficiency than SO2. Greater than 95% reduction of HCl can be expected with either a wet or wet/dry scrubber. 

Hence, NSPS control of SO2 is an appropriate baseline for MACT control of HCl. In addition to use of SO2 control as an initial surrogate for acid gas HAPs (especially HCl), periodic testing of HCl and HF should be required to ensure that low levels result from SO2 scrubbing. Based on this information, more specific HCl or HF MACT limits can be set in the future if significant levels of these remain after scrubbing for acid gases. 

3. Organic HAPs - Use Carbon Monoxide as MACT surrogate. 

Organic HAPs include polycyclic organic matter (POM), polyaromatic hydrocarbons (PAH), and dioxin. With good combustion these should be emitted at insignificant levels. However, there are currently little or no requirements for good combustion from coal burning utility boilers. Furthermore, NOx control requirements have sometimes encouraged the modification of combustion processes in ways that have increased CO and other products of incomplete combustion. 

Good combustion practice is to use carbon monoxide as the principle indicator of incomplete combustion since it is emitted in relatively high amounts when combustion is poor and can be accurately and inexpensively measured. Continuous monitoring of carbon monoxide is used to trim the air to fuel ratio to ensure maximum combustion of fuel, which in turn ensures minimum organic emissions, including organic HAPs. Carbon monoxide monitoring is also a good indicator of other combustion problems, such as poor fuel atomization (oil) or coal distribution in the boiler. 

There is already precedent in state reasonably available control technology (RACT) rules for using carbon monoxide as a surrogate for VOC emissions from boilers. NJ requires CO continuous monitors and has a limit of 100 ppmv at 7% oxygen, daily average for VOC RACT for utility boilers. Typical actual CO levels for well-controlled coal boilers are less than 10 ppmv. Similarly, CO can be used as a surrogate for minimization of organic HAP emissions. 

Given that there is sparse data correlating organic HAP emissions to CO, a prudent first step would be to set a fairly liberal MACT limit of between 10 and 100 ppmv CO at 7% oxygen, require periodic HAP testing as part of the MACT, and update the MACT limit in the future to reflect best combustion control methods. 

OIL NOTE: The above recommendations for particulate and organic HAPs can also be applied to heavy oil combustion which emits significant amounts of certain heavy metals (nickel) and can emit significant amounts of organic HAPs if the combustion control is poor. The recommendations for organic HAPs can apply to light oil combustion as well.