## Summary
Summary of UPLs using emissions test averages -- Coal
| Existing | [7 empty] | New
Pollutant | Mean (lb/MMBtu) | UPL (lb/MMBtu) | Number of units in the floor | Floor value (lb/MMBtu) |  |  |  | Is Floor = 3 x RDL? | Mean (lb/MMBtu) | UPL (lb/MMBtu) | Number of units in the floor
HCl | 0.00019044 | 0.0015864 | 130 | 0.0015864 | 0.002 | 0.002 | lb/MMBtu | No | 1.2873e-05 | 2.7289e-05 | 1
HF | 8.1873e-05 | 0.00023237 | 130 | 0.0004 | 0.0004 | 0.0004 | lb/MMBtu | 3 x RDL | 5.6867e-06 | 6.7295e-06 | 1
SO2 | 0.063421 | 0.1448 | 130 | 0.1448 | 0.2 | 0.2 | lb/MMBtu | NA | 0.008 | 0.034059 | 1
| Existing | [7 empty] | New
Pollutant | Mean (lb/MWh) | UPL (lb/MWh) | Number of units in the floor | Floor value (lb/MWh) |  |  | Floor value (lb/GWh) | Is Floor = 3 x RDL? | Mean (lb/MWh) | UPL (lb/MWh) | Number of units in the floor | Floor value (lb/MWh) |  |  |  | Is Floor = 3 x RDL?
HCl | 0.0019178 | 0.016199 | 130 | 0.016199 | 0.02 | 0.02 | lb/MWh | No | 0.0001127 | 0.00023891 | 1 | 0.0004 | 0.0004 | 0.0004 | lb/MWh | 3 x RDL
HF | 0.0008284 | 0.0023884 | 130 | 0.0023884 | 0.003 | 0.003 | lb/MWh | No | 5.898e-05 | 8.37e-05 | 1 | 0.0004 | 0.0004 | 0.0004 | lb/MWh | 3 x RDL
SO2 | 0.64215 | 1.4441 | 130 | 1.4441 | 1.5 | 1.5 | lb/MWh | NA | 0.0912 | 0.38827 | 1 | 0.38827 | 0.4 | 0.4 | lb/MWh | NA
Calculation of 3 x RDL (lb/MMBTU) based on conversion of 3 x RDL (ug/dscm)
PET COKE
E = Cd*Fd*(20.9/(20.9-%O2))
Fd(pet coke) = | 9780
lb/scf = | 16020000000000 | ng/scm
lb/scf = | 16020000000 | ug/scm
Corrected for 4 dscm sample volume
3xRDL, 4dscm sample volume
Method 29 Metals |  |  | ug/dscm | lb/dscf |  |  | lb/MMBtu @ 6% O2 | lb/MW @ 6% O2, 10 MMBtu/MW
Antimony |  |  | 0.825 | 5.1498e-11 |  |  | 7.0646e-07 | 7.0646e-06
Arsenic |  |  | 0.3 | 1.8727e-11 |  |  | 2.569e-07 | 2.569e-06
Beryllium |  |  | 0.06 | 3.7453e-12 |  |  | 5.1379e-08 | 5.1379e-07
Cadmium |  |  | 0.0225 | 1.4045e-12 |  |  | 1.9267e-08 | 1.9267e-07
Chromium |  |  | 0.225 | 1.4045e-11 |  |  | 1.9267e-07 | 1.9267e-06
Cobalt |  |  | 0.225 | 1.4045e-11 |  |  | 1.9267e-07 | 1.9267e-06
Lead |  |  | 0.225 | 1.4045e-11 |  |  | 1.9267e-07 | 1.9267e-06
Manganese |  |  | 0.225 | 1.4045e-11 |  |  | 1.9267e-07 | 1.9267e-06
Nickel |  |  | 4.05 | 2.5281e-10 |  |  | 3.4681e-06 | 3.4681e-05
Selenium |  |  | 0.6 | 3.7453e-11 |  |  | 5.1379e-07 | 5.1379e-06
Total | [6 empty] | 5.7866e-06 | 5.7866e-05
fPM | Method 29 | [5 empty] | 0.00064 | 0.0064
HCl | Method 26a | [5 empty] | 4e-05 | 0.0004
HF | Method 26a | [5 empty] | 4e-05 | 0.0004

## HCl_Avg_MMBtu
Emissions (lb/MMBtu)
| Logan Generating Plant | Seward | Seward | Sandow Station | Hatfield's Ferry Power Station | Sandow Station | HOLCOMB | Roanoke Valley II | Spruance Genco, LLC | Spruance Genco, LLC | Spruance Genco, LLC | Spruance Genco, LLC | INDIANTOWN COGENERATION L.P. | Rawhide | Walter Scott Jr. Energy Center | Cross | Chambers Cogeneration LP | Navajo Generating Station | Hardin Generator Project | Chambers Cogeneration LP | Roxboro Steam Electric Plant | Colstrip | TS Power Plant | Navajo Generating Station | Cross | Hawthorn | Roanoke Valley I | H L Spurlock Station | Marshall | J K Spruce | Elm Road Generating Station | Weston | Spruance Genco, LLC | Spruance Genco, LLC | Hammond | Hammond | Hammond | Hammond | Cholla | Cholla | Navajo Generating Station | Pleasant Prairie | AES Puerto Rico Cogeneration Facility | San Juan | Pleasant Prairie | Dallman | AES Puerto Rico Cogeneration Facility | Walter Scott Jr. Energy Center | Hamilton | San Juan | San Juan | H L Spurlock Station | Bowen | Oak Grove | San Juan | Hayden | Cardinal | Hopewell | Hopewell | Neil Simpson II | Wygen 1 | Healy | Southampton Power Station | Southampton Power Station | Bowen | Whelan Energy Center Unit 1 (WEC1) | AES Petersburg | Yates | Conesville | AES Petersburg | Ghent | John E. Amos | Cardinal | Cherokee | Louisa | Welsh | Valmont | Mountaineer | Arapahoe | Hayden | Asheville Steam Electric Plant | Wansley | R D Green | Cherokee | Cherokee | Cross | Bowen | HMP&L Station Two Henderson | Gibson | Labadie | Crystal River Power Plant | Nebraska City | Mt. Storm | Marshall | Marshall | Conemaugh | Asheville Steam Electric Plant | Montrose | Montrose | Montrose | PPL Montour | HMP&L Station Two Henderson | Cherokee | Springerville | Wansley | John E. Amos | Cumberland | Marshall | Conemaugh | Cumberland | Clover | PPL Montour | AES Cayuga, LLC | Red Hills Generating Facility | Red Hills Generating Facility | Clover | Quindaro | Wygen 2 | PPL Brunner Island | PPL Brunner Island | BL England | Homer City Station | Nearman Creek | Laramie River Station | Reid Gardner | AES Cayuga, LLC | Lamar Plant | Newton | Duck Creek | Boswell Energy Center
ORIS/Facility/Unit | 10043 | 3130 | 3130 | 52071 | 3179 | 52071 | 108 | 54755 | 54081 | 54081 | 54081 | 54081 | 50976 | 6761 | 1082 | 130 | 10566 | 4941 | 55749 | 10566 | 2712 | 6076 | 56224 | 4941 | 130 | 2079 | 54035 | 6041 | 2727 | 7097 | 56068 | 4078 | 54081 | 54081 | 708 | 708 | 708 | 708 | 113 | 113 | 4941 | 6170 | 68029 | 2451 | 6170 | 963 | 68029 | 1082 | 2917 | 2451 | 2451 | 6041 | 703 | 6180 | 2451 | 525 | 2828 | 10771 | 10771 | 7504 | 55479 | 6288 | 10774 | 10774 | 703 | 60 | 994 | 728 | 2840 | 994 | 1356 | 3935 | 2828 | 469 | 6664 | 6139 | 477 | 6264 | 465 | 525 | 2706 | 6052 | 6639 | 469 | 469 | 130 | 703 | 1382 | 6113 | 2103 | 628 | 6096 | 3954 | 2727 | 2727 | 3118 | 2706 | 2080 | 2080 | 2080 | 3149 | 1382 | 469 | 8223 | 6052 | 3935 | 3399 | 2727 | 3118 | 3399 | 7213 | 3149 | 2535 | 55076 | 55076 | 7213 | 1295 | 56319 | 3140 | 3140 | 2378 | 3122 | 6064 | 6204 | 2324 | 2535 | 508 | 6017 | 6016 | 1893
Test Averages | B01 | 1 | 2 | 5A | 1 | 5B | SGU1 | BLR2 | 3A | 3B | 2A | 2B | AABO1 | 101 | 4 | 4 | Boil 1 | 1 | PC1 | Boil 2 | 2 | 3 | BLR100 | 2 | 3 | 5A | BLR1 | 3 | Unit 4 | BLR1 | 1 | 4 | 4A | 4B | 2 | 3 | 1 | 4 | 3 | 4 | 3 | 2 | BLR2 | Unit 3 | 1 | 34 | BLR1 | 3 | 9 | Unit 1 | Unit 4 | 4 | 4 | 1 | Unit 2 | 2 | 1 | 10771-01 | 10771-02 | 2 | 3 | 1 | 1 | 2 | 2 | 1 | 2 | Y1BR | 4 | 1 | 1 | 2 | 2 | 2 | 101 | 1 | 5 | 1 | 3 | 1 | 2 | 2 | G2 | 1 | 4 | 1 | 3 | H1 | 4 | 2 | 5 | NC2 | 3 | Unit 1 | Unit 2 | 1 | 1 | 2 | 1 | 3 | 1 | H2 | 3 | 3 | 1 | 3 | 1 | Unit 3 | 2 | 2 | 2 | 2 | 1 | AA-002 | AA-001 | 1 | 1 | 1 | 2 | 1 | 2 | 3 | N1 | 3 | 3 | 2 | 4 | 2 | 1 | 3
1 | 1.2873e-05 | 1.9267e-05 | 1.9267e-05 | 2.1186e-05 | 2.47e-05 | 2.5524e-05 | 2.6e-05 | 3.2175e-05 | 3.2235e-05 | 3.2235e-05 | 3.3866e-05 | 3.3866e-05 | 3.5766e-05 | 3.6081e-05 | 3.8e-05 | 4.0967e-05 | 4.24e-05 | 5e-05 | 5e-05 | 5.6009e-05 | 5.65e-05 | 6.2094e-05 | 6.5139e-05 | 6.6667e-05 | 6.894e-05 | 7.2108e-05 | 7.3157e-05 | 7.3333e-05 | 7.5417e-05 | 7.6237e-05 | 7.6401e-05 | 7.6667e-05 | 7.6841e-05 | 7.6841e-05 | 7.8767e-05 | 7.8767e-05 | 7.8767e-05 | 7.8767e-05 | 8.0274e-05 | 8.5239e-05 | 9.3828e-05 | 9.4427e-05 | 9.5966e-05 | 9.5979e-05 | 9.6556e-05 | 9.7e-05 | 0.00010185 | 0.00011 | 0.00011019 | 0.00011135 | 0.00011782 | 0.00011844 | 0.00011939 | 0.00012026 | 0.00012406 | 0.00014256 | 0.00014296 | 0.00014673 | 0.00014673 | 0.0001475 | 0.0001535 | 0.00015405 | 0.00015527 | 0.00015527 | 0.00015567 | 0.0001624 | 0.00016245 | 0.00016306 | 0.00016321 | 0.00017578 | 0.00017961 | 0.00018274 | 0.00018536 | 0.00018637 | 0.00019104 | 0.00019445 | 0.00021111 | 0.00021405 | 0.00021753 | 0.00021783 | 0.00022 | 0.00022052 | 0.00022267 | 0.00022537 | 0.00023684 | 0.00024375 | 0.00024955 | 0.00025197 | 0.00026058 | 0.00027303 | 0.00027384 | 0.0002764 | 0.00028488 | 0.0002859 | 0.0002859 | 0.00028801 | 0.00029533 | 0.0003 | 0.0003 | 0.0003 | 0.0003015 | 0.00030516 | 0.0003054 | 0.00030598 | 0.00031074 | 0.00031262 | 0.00031666 | 0.00032635 | 0.00033266 | 0.00033471 | 0.00033766 | 0.00035654 | 0.00035901 | 0.00036675 | 0.00036675 | 0.00037307 | 0.00038 | 0.00039233 | 0.00039814 | 0.00039814 | 0.00040495 | 0.00040608 | 0.00041 | 0.00041077 | 0.00045233 | 0.00046614 | 0.00047688 | 0.00048706 | 0.00050141 | 0.00051267
2 | 0.0004124 | 0.00029484 | 0.00029484 | 9.2435e-05 | 0.0001313 | 3.0185e-05 |  | 0.000492 | [5 empty] | 0.000351 | 7.3724e-05 | 0.00022897 |  | 6.4809e-05 | 0.0001455 |  |  |  | 0.001052 | 6.965e-05 | 0.000276 | 0.00035 | 0.000563 | 7.5133e-05 | 0.00028343 | [11 empty] | 9.6667e-05 |  |  |  |  | 0.00086 | [5 empty] | 0.00113 |  | 0.00022667 | [5 empty] | 0.00014767 | 0.00015658 | [27 empty] | 0.00054699 | [6 empty] | 0.00033 | 0.0061356 | 0.0036 | 0.001 | 0.0036 | [8 empty] | 0.00046667 |  |  |  |  | 0.00038667 | 0.00038667 |  |  | 0.0004 |  |  | 0.0010116 | [7 empty] | 0.00114
3 | 0.00018748 | [12 empty] | 0.00033354 | 5.9e-05 | [7 empty] | 0.0004 |  |  | 0.00027 |  |  | 9.2967e-05 | [16 empty] | 0.00010033 | [5 empty] | 0.0002 | [68 empty] | 0.001
4 | 0.0001184 | [12 empty] | 0.00032 | [14 empty] | 7.93e-05 | [22 empty] | 0.00013024 | [68 empty] | 0.00053109
5 | 7.8689e-05 | [12 empty] | 0.00016
6 | 7.8076e-05 | [12 empty] | 6e-05
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 6 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 6 | 3 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 3 | 2 | 2 | 3 | 2 | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1
Outlier Emission Averages Removed:
Total number of values used to calculate mean on row 65 |  | 130 |  | = n for existing sources in Term 1 on row 79
n =Total # test runs = |  | 185 |  | = n for new sources in Term 1 | ; = number of data points in s^2 calculation; also, this number minus 1 is the value used to calculate the t-statistic | [10 empty] | UPL Pooled Variance=
|  | 184 |  | (this value is used to determine the t-statistic on row 95)
This step is for QC only:
means | 1.2873e-05 | 1.9267e-05 | 1.9267e-05 | 2.1186e-05 | 2.47e-05 | 2.5524e-05 | 2.6e-05 | 3.2175e-05 | 3.2235e-05 | 3.2235e-05 | 3.3866e-05 | 3.3866e-05 | 3.5766e-05 | 3.6081e-05 | 3.8e-05 | 4.0967e-05 | 4.24e-05 | 5e-05 | 5e-05 | 5.6009e-05 | 5.65e-05 | 6.2094e-05 | 6.5139e-05 | 6.6667e-05 | 6.894e-05 | 7.2108e-05 | 7.3157e-05 | 7.3333e-05 | 7.5417e-05 | 7.6237e-05 | 7.6401e-05 | 7.6667e-05 | 7.6841e-05 | 7.6841e-05 | 7.8767e-05 | 7.8767e-05 | 7.8767e-05 | 7.8767e-05 | 8.0274e-05 | 8.5239e-05 | 9.3828e-05 | 9.4427e-05 | 9.5966e-05 | 9.5979e-05 | 9.6556e-05 | 9.7e-05 | 0.00010185 | 0.00011 | 0.00011019 | 0.00011135 | 0.00011782 | 0.00011844 | 0.00011939 | 0.00012026 | 0.00012406 | 0.00014256 | 0.00014296 | 0.00014673 | 0.00014673 | 0.0001475 | 0.0001535 | 0.00015405 | 0.00015527 | 0.00015527 | 0.00015567 | 0.0001624 | 0.00016245 | 0.00016306 | 0.00016321 | 0.00017578 | 0.00017961 | 0.00018274 | 0.00018536 | 0.00018637 | 0.00019104 | 0.00019445 | 0.00021111 | 0.00021405 | 0.00021753 | 0.00021783 | 0.00022 | 0.00022052 | 0.00022267 | 0.00022537 | 0.00023684 | 0.00024375 | 0.00024955 | 0.00025197 | 0.00026058 | 0.00027303 | 0.00027384 | 0.0002764 | 0.00028488 | 0.0002859 | 0.0002859 | 0.00028801 | 0.00029533 | 0.0003 | 0.0003 | 0.0003 | 0.0003015 | 0.00030516 | 0.0003054 | 0.00030598 | 0.00031074 | 0.00031262 | 0.00031666 | 0.00032635 | 0.00033266 | 0.00033471 | 0.00033766 | 0.00035654 | 0.00035901 | 0.00036675 | 0.00036675 | 0.00037307 | 0.00038 | 0.00039233 | 0.00039814 | 0.00039814 | 0.00040495 | 0.00040608 | 0.00041 | 0.00041077 | 0.00045233 | 0.00046614 | 0.00047688 | 0.00048706 | 0.00050141 | 0.00051267
0.00019044
UPL Mean = | [6 empty] | Distribution of Normal Tests | Distribution of Log Tests
[6 empty] | Skewness = | 0.57967 | #DIV/0!
[6 empty] | SE Skewness | 0.21483 | #DIV/0!
Pooled Variance = |  | 3.5111e-07 |  |  |  | Skewness Test | non-normal | #DIV/0!
[6 empty] | Kurtosis = | -0.69914 | #DIV/0!
[6 empty] | SE Kurtosis | 0.42967 | #DIV/0!
[6 empty] | Kurtosis Test | normal | #DIV/0!
[6 empty] | Number of test runs = | 130 | 0 | Result: | normal
m= number future runs = |  | 1
Term1 |  | 1.0077
Term2 |  | 3.5381e-07
Squared root Term2 |  | 0.00059482
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 2.3468 |  | (the t-statistic should be calculated with the one less data point than the data set used for calculation of s^2.)
UPL POOLED VARIANCE = |  | 0.0015864 | lb/MMBtu
HCl | 3xRDL, 4dscm sample volume | 0.0004 | lb/MMBtu
| Floor Value | 0.0015864 | lb/MMBtu
Tukey's Exploratory Data Analysis Model
7.6841e-05 | 25th Percentile
0.00029883 | 75th Percentile
0.00022199 | IQR
Gross Outlier Test
Far Outlier Test (low)
Far Outlier Test (high)
Near Outlier Test (low)
Near Outlier Test (high)
Note on A113: Evaluates multiple test averages for a source and flags if max test average is >100x larger than Min test avg.
Note on A114: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A115: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A116: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.
Note on A117: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.

## HCl_New_MMBtu
Emissions (lb/MMBtu)
Logan Generating Plant
ORIS/Facility/Unit | 10043
Runs | B01
1 | 1.4098e-05 | BDL
2 | 1.4563e-05 | BDL
3 | 9.9578e-06 | BDL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3
2
This step is for QC only:
means | 1.2873e-05
1.2873e-05
UPL Mean =
Pooled Variance = |  | 6.4272e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 4.2848e-12
Squared root Term2 |  | 2.07e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 2.7289e-05 | lb/MMBtu
HCl | 3xRDL, 4dscm sample volume | 0.0004 | lb/MMBtu
| Floor Value | 0.0004 | lb/MMBtu

## HCl_Avg_MW
Emissions (lb/MW)
| Logan Generating Plant | Seward | Seward | Sandow Station | HOLCOMB | Hatfield's Ferry Power Station | Sandow Station | Rawhide | INDIANTOWN COGENERATION L.P. | Walter Scott Jr. Energy Center | Roanoke Valley II | Chambers Cogeneration LP | Spruance Genco, LLC | Spruance Genco, LLC | Spruance Genco, LLC | Spruance Genco, LLC | Cross | Navajo Generating Station | Chambers Cogeneration LP | Hardin Generator Project | Roxboro Steam Electric Plant | TS Power Plant | Colstrip | H L Spurlock Station | Navajo Generating Station | Marshall | Cross | Roanoke Valley I | Weston | Elm Road Generating Station | Cholla | Hammond | Hammond | Hammond | Hawthorn | Dallman | Hammond | J K Spruce | Cholla | Navajo Generating Station | AES Puerto Rico Cogeneration Facility | Pleasant Prairie | Pleasant Prairie | AES Puerto Rico Cogeneration Facility | Spruance Genco, LLC | Spruance Genco, LLC | San Juan | H L Spurlock Station | Walter Scott Jr. Energy Center | San Juan | Bowen | San Juan | Cardinal | San Juan | Oak Grove | Hayden | Bowen | AES Petersburg | AES Petersburg | Conesville | John E. Amos | Hamilton | Cardinal | Whelan Energy Center Unit 1 (WEC1) | Yates | Wygen 1 | Welsh | Neil Simpson II | Hopewell | Hopewell | Mountaineer | Lamar Plant | Valmont | Southampton Power Station | Southampton Power Station | Louisa | Wansley | Asheville Steam Electric Plant | Hayden | Healy | Ghent | Cherokee | Bowen | Cherokee | Gibson | R D Green | Cross | Marshall | Marshall | Crystal River Power Plant | Cherokee | Labadie | HMP&L Station Two Henderson | Asheville Steam Electric Plant | PPL Montour | Conemaugh | Nebraska City | Marshall | Wansley | Springerville | John E. Amos | Mt. Storm | Conemaugh | AES Cayuga, LLC | PPL Montour | HMP&L Station Two Henderson | Montrose | Montrose | Arapahoe | Cumberland | Cherokee | Red Hills Generating Facility | Red Hills Generating Facility | Montrose | Cumberland | Homer City Station | PPL Brunner Island | Quindaro | BL England | Nearman Creek | Clover | AES Cayuga, LLC | PPL Brunner Island | Clover | Newton | Laramie River Station | Harrison Power Station | Reid Gardner | Eddystone Generating Station | East Bend Station
ORIS/Facility/Unit | 10043 | 3130 | 3130 | 52071 | 108 | 3179 | 52071 | 6761 | 50976 | 1082 | 54755 | 10566 | 54081 | 54081 | 54081 | 54081 | 130 | 4941 | 10566 | 55749 | 2712 | 56224 | 6076 | 6041 | 4941 | 2727 | 130 | 54035 | 4078 | 56068 | 113 | 708 | 708 | 708 | 2079 | 963 | 708 | 7097 | 113 | 4941 | 68029 | 6170 | 6170 | 68029 | 54081 | 54081 | 2451 | 6041 | 1082 | 2451 | 703 | 2451 | 2828 | 2451 | 6180 | 525 | 703 | 994 | 994 | 2840 | 3935 | 2917 | 2828 | 60 | 728 | 55479 | 6139 | 7504 | 10771 | 10771 | 6264 | 508 | 477 | 10774 | 10774 | 6664 | 6052 | 2706 | 525 | 6288 | 1356 | 469 | 703 | 469 | 6113 | 6639 | 130 | 2727 | 2727 | 628 | 469 | 2103 | 1382 | 2706 | 3149 | 3118 | 6096 | 2727 | 6052 | 8223 | 3935 | 3954 | 3118 | 2535 | 3149 | 1382 | 2080 | 2080 | 465 | 3399 | 469 | 55076 | 55076 | 2080 | 3399 | 3122 | 3140 | 1295 | 2378 | 6064 | 7213 | 2535 | 3140 | 7213 | 6017 | 6204 | 3944 | 2324 | 3161 | 6018
Test Averages | B01 | 1 | 2 | 5A | SGU1 | 1 | 5B | 101 | AABO1 | 4 | BLR2 | Boil 1 | 3A | 3B | 2A | 2B | 4 | 1 | Boil 2 | PC1 | 2 | BLR100 | 3 | 3 | 2 | Unit 4 | 3 | BLR1 | 4 | 1 | 3 | 2 | 3 | 1 | 5A | 34 | 4 | BLR1 | 4 | 3 | BLR2 | 2 | 1 | BLR1 | 4A | 4B | Unit 3 | 4 | 3 | Unit 1 | 4 | Unit 4 | 1 | Unit 2 | 1 | 2 | 2 | 2 | 1 | 4 | 2 | 9 | 2 | 1 | Y1BR | 3 | 1 | 2 | 10771-01 | 10771-02 | 1 | 4 | 5 | 1 | 2 | 101 | 2 | 2 | 1 | 1 | 1 | 4 | 3 | 2 | 4 | G2 | 1 | Unit 1 | Unit 2 | 5 | 1 | 2 | H1 | 1 | 1 | 1 | NC2 | Unit 3 | 1 | 3 | 3 | 3 | 2 | 1 | 2 | H2 | 2 | 1 | 3 | 1 | 3 | AA-002 | AA-001 | 3 | 2 | 3 | 2 | 1 | 2 | N1 | 2 | 2 | 1 | 1 | 2 | 3 | 1 | 3 | 2 | 2
1 | 0.0001127 | 0.00020419 | 0.00020419 | 0.0002221 | 0.00022768 | 0.00023863 | 0.00026758 | 0.00033124 | 0.00033904 | 0.00034312 | 0.00036036 | 0.00041269 | 0.00042119 | 0.00042119 | 0.0004425 | 0.0004425 | 0.00044559 | 0.00045874 | 0.00054515 | 0.0005479 | 0.00055399 | 0.00056849 | 0.00058415 | 0.00061111 | 0.00061166 | 0.00064964 | 0.00066822 | 0.00068333 | 0.00069034 | 0.00073523 | 0.0007709 | 0.00077947 | 0.00078177 | 0.00079366 | 0.00080121 | 0.00081393 | 0.00082683 | 0.00083611 | 0.000856 | 0.00086086 | 0.00092632 | 0.00094706 | 0.00095067 | 0.00098314 | 0.001004 | 0.001004 | 0.0010159 | 0.0011054 | 0.0011072 | 0.0011156 | 0.0011373 | 0.0012235 | 0.0012258 | 0.0012366 | 0.0013203 | 0.0013566 | 0.0015018 | 0.0015128 | 0.0015165 | 0.0015439 | 0.0015715 | 0.0015875 | 0.0015893 | 0.0016417 | 0.0016683 | 0.0017762 | 0.0017967 | 0.0018437 | 0.001845 | 0.001845 | 0.0019394 | 0.0019509 | 0.0019872 | 0.0020299 | 0.0020299 | 0.0020466 | 0.0020504 | 0.0020512 | 0.0021169 | 0.0021382 | 0.0021712 | 0.0021767 | 0.0021892 | 0.0022756 | 0.0024698 | 0.0025404 | 0.0025981 | 0.0026147 | 0.0026183 | 0.0026503 | 0.0026813 | 0.0027097 | 0.002729 | 0.0027308 | 0.0027385 | 0.0027647 | 0.0028046 | 0.0028454 | 0.0028526 | 0.0028558 | 0.0028703 | 0.0030142 | 0.0031933 | 0.0032004 | 0.0032588 | 0.00329 | 0.0033989 | 0.0034149 | 0.0034207 | 0.0034419 | 0.0034742 | 0.0034949 | 0.0035223 | 0.0035904 | 0.003638 | 0.0036876 | 0.0038395 | 0.0038592 | 0.0038728 | 0.0038754 | 0.0039219 | 0.0040232 | 0.0040357 | 0.0042613 | 0.0043207 | 0.0044444 | 0.0050165 | 0.0050409 | 0.0050421 | 0.0051268
2 | 0.0036105 | 0.0031248 | 0.0031248 | 0.00096904 |  | 0.0012685 | 0.00031644 | 0.0032223 |  | 0.00066568 | 0.0055104 | [5 empty] | 0.0024905 | 0.00059462 |  | 0.0015944 |  | 0.0091811 |  | 0.0006261 | 0.00063903 | 0.0024415 | 0.0026752 | 0.0052588 | [6 empty] | 0.0038889 | 0.0072163 |  |  |  | 0.0008869 | [7 empty] | 0.010547 | [6 empty] | 0.0024886 | [10 empty] | 0.0018119 |  | 0.0018458 | [16 empty] | 0.0051844 | [8 empty] | 0.056732 |  | 0.0031678 | [6 empty] | 0.0044797 |  |  |  | 0.040787 | 0.011383 |  |  |  | 0.0036846 | 0.0037135 | 0.043085 |  |  |  |  | 0.0096746
3 | 0.0016413 | [6 empty] | 0.003062 |  | 0.00053274 | [11 empty] | 0.0034909 |  |  |  | 0.00080081 | [8 empty] | 0.003 | 0.0008419 | [11 empty] | 0.0018667 | [70 empty] | 0.0095637
4 | 0.0010366 | [6 empty] | 0.0029377 | [17 empty] | 0.00068309 | [21 empty] | 0.0012156 | [70 empty] | 0.0050792
5 | 0.0006889 | [6 empty] | 0.0014689
6 | 0.00068353 | [6 empty] | 0.00055082
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 6 | 2 | 2 | 2 | 1 | 2 | 2 | 6 | 1 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 2 | 2 | 4 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Outlier Emission Averages Removed:
Total number of values used to calculate mean on row 65 |  | 130 |  | = n for existing sources in Term 1 on row 79
n =Total # test runs = |  | 183 |  | = n for new sources in Term 1 | ; = number of data points in s^2 calculation; also, this number minus 1 is the value used to calculate the t-statistic | [10 empty] | UPL Pooled Variance=
|  | 182 |  | (this value is used to determine the t-statistic on row 95)
This step is for QC only:
means | 0.0001127 | 0.00020419 | 0.00020419 | 0.0002221 | 0.00022768 | 0.00023863 | 0.00026758 | 0.00033124 | 0.00033904 | 0.00034312 | 0.00036036 | 0.00041269 | 0.00042119 | 0.00042119 | 0.0004425 | 0.0004425 | 0.00044559 | 0.00045874 | 0.00054515 | 0.0005479 | 0.00055399 | 0.00056849 | 0.00058415 | 0.00061111 | 0.00061166 | 0.00064964 | 0.00066822 | 0.00068333 | 0.00069034 | 0.00073523 | 0.0007709 | 0.00077947 | 0.00078177 | 0.00079366 | 0.00080121 | 0.00081393 | 0.00082683 | 0.00083611 | 0.000856 | 0.00086086 | 0.00092632 | 0.00094706 | 0.00095067 | 0.00098314 | 0.001004 | 0.001004 | 0.0010159 | 0.0011054 | 0.0011072 | 0.0011156 | 0.0011373 | 0.0012235 | 0.0012258 | 0.0012366 | 0.0013203 | 0.0013566 | 0.0015018 | 0.0015128 | 0.0015165 | 0.0015439 | 0.0015715 | 0.0015875 | 0.0015893 | 0.0016417 | 0.0016683 | 0.0017762 | 0.0017967 | 0.0018437 | 0.001845 | 0.001845 | 0.0019394 | 0.0019509 | 0.0019872 | 0.0020299 | 0.0020299 | 0.0020466 | 0.0020504 | 0.0020512 | 0.0021169 | 0.0021382 | 0.0021712 | 0.0021767 | 0.0021892 | 0.0022756 | 0.0024698 | 0.0025404 | 0.0025981 | 0.0026147 | 0.0026183 | 0.0026503 | 0.0026813 | 0.0027097 | 0.002729 | 0.0027308 | 0.0027385 | 0.0027647 | 0.0028046 | 0.0028454 | 0.0028526 | 0.0028558 | 0.0028703 | 0.0030142 | 0.0031933 | 0.0032004 | 0.0032588 | 0.00329 | 0.0033989 | 0.0034149 | 0.0034207 | 0.0034419 | 0.0034742 | 0.0034949 | 0.0035223 | 0.0035904 | 0.003638 | 0.0036876 | 0.0038395 | 0.0038592 | 0.0038728 | 0.0038754 | 0.0039219 | 0.0040232 | 0.0040357 | 0.0042613 | 0.0043207 | 0.0044444 | 0.0050165 | 0.0050409 | 0.0050421 | 0.0051268
0.0019178
UPL Mean = | [6 empty] | Distribution of Normal Tests | Distribution of Log Tests
[6 empty] | Skewness = | 0.56534 | #DIV/0!
[6 empty] | SE Skewness | 0.21483 | #DIV/0!
Pooled Variance = |  | 3.6744e-05 |  |  |  | Skewness Test | non-normal | #DIV/0!
[6 empty] | Kurtosis = | -0.65309 | #DIV/0!
[6 empty] | SE Kurtosis | 0.42967 | #DIV/0!
[6 empty] | Kurtosis Test | normal | #DIV/0!
[6 empty] | Number of test runs = | 130 | 0 | Result: | normal
m= number future runs = |  | 1
Term1 |  | 1.0077
Term2 |  | 3.7027e-05
Squared root Term2 |  | 0.006085
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 2.347 |  | (the t-statistic should be calculated with the one less data point than the data set used for calculation of s^2.)
UPL POOLED VARIANCE = |  | 0.016199 | lb/MW
HCl | 3xRDL, 4dscm sample volume | 0.0004 | lb/MW
| Floor Value | 0.016199 | lb/MW
Tukey's Exploratory Data Analysis Model
0.00078474 | 25th Percentile
0.0028352 | 75th Percentile
0.0020504 | IQR
Gross Outlier Test
Far Outlier Test (low)
Far Outlier Test (high)
Near Outlier Test (low)
Near Outlier Test (high)
IF(COUNT(Q5:Q39)>1,IF(MAX(Q5:Q39)>100*MIN(Q5:Q39),"Gross Outlier",""),"")
13.4171
[16 empty] | 0.0004425 | 0.04425
1.4594e-08
30321.1397
Note on A113: Evaluates multiple test averages for a source and flags if max test average is >100x larger than Min test avg.
Note on A114: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A115: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A116: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.
Note on A117: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.

## HCl_New_MW
Emissions (lb/MW)
Logan Generating Plant
ORIS/Facility/Unit | 10043
Runs | B01
1 | 0.00012342 | BDL
2 | 0.0001275 | BDL
3 | 8.7177e-05 | BDL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3
2
This step is for QC only:
means | 0.0001127
0.0001127
UPL Mean =
Pooled Variance = |  | 4.9261e-10
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.284e-10
Squared root Term2 |  | 1.8122e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.00023891 | lb/MW
HCl | 3xRDL, 4dscm sample volume | 0.0004 | lb/MW
| Floor Value | 0.0004 | lb/MW

## AcidGas_coal_
primary_fuel | ORIS code | Plant Name | physical_state | Unit Number | boiler_id | Unit Type | boiler_type | MWe_capacity | max_heat_input | Boiler_heat_rate | Fuel types | Fuel_Cl_lb/MMBtu | Fuel_F_lb/MMBtu | Chlorine - ERT | Chlorine MW - ERT | Chlorine - ETTS | Chlorine MW - ETTS | Chlorine - Part II | Chlorine MW - Part II | Chlorine - min | Chlorine MW - min | HCN - ERT | HCN MW - ERT | HCN - ETTS | HCN MW - ETTS | HCN - Part II | HCN MW - Part II | HCN - min | HCN MW - min | Hydrogen Chloride - ERT | Hydrogen Chloride MW - ERT | Hydrogen Chloride - ETTS | Hydrogen Chloride MW - ETTS | Hydrogen Chloride - Part II | Hydrogen Chloride MW - Part II | Hydrogen Chloride - min | Hydrogen Chloride MW - min | Hydrogen Fluoride - ERT | Hydrogen Fluoride MW - ERT | Hydrogen Fluoride - ETTS | Hydrogen Fluoride MW - ETTS | Hydrogen Fluoride - Part II | Hydrogen Fluoride MW - Part II | Hydrogen Fluoride - min | Hydrogen Fluoride MW - min | Sulfur Dioxide - CEMS | Sulfur Dioxide MW - CEMS | Sulfur Dioxide - ERT | Sulfur Dioxide MW - ERT | Sulfur Dioxide - ETTS | Sulfur Dioxide MW - ETTS | Sulfur Dioxide - Part II | Sulfur Dioxide MW - Part II | Sulfur Dioxide - min | Sulfur Dioxide MW - min | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
[8 empty] | MW | MMBtu/hr | Mmbtu/MWh |  | lb/MMBtu | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW
coal | 3130 | Seward | PA | SEW-1 | 1 | Fluidized bed firing | Fluidized bed firing | 292.5 | 3100 | 10.5983 | coal refuse (culm or gob) | 0.03353 | 0.027763 | [10 empty] | 0.00012193 | 0.0012923 |  |  | 0.00012193 | 0.0012923 | 0.00029484 | 0.0031248 |  |  | 1.9267e-05 | 0.00020419 | 1.9267e-05 | 0.00020419 | 0.00020526 | 0.0021754 |  |  | 5.6867e-06 | 6.0269e-05 | 5.6867e-06 | 6.0269e-05 |  |  | 0.67075 | 7.1088 |  |  |  |  | 0.67075 | 7.1088 | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Fabric Filter, pulse | 2004-03-01
coal | 3130 | Seward | PA | SEW-1 | 2 | Fluidized bed firing | Fluidized bed firing | 292.5 | 3100 | 10.5983 | coal refuse (culm or gob) | 0.03353 | 0.027763 | [10 empty] | 0.00012193 | 0.0012923 |  |  | 0.00012193 | 0.0012923 | 0.00029484 | 0.0031248 |  |  | 1.9267e-05 | 0.00020419 | 1.9267e-05 | 0.00020419 | 0.00020526 | 0.0021754 |  |  | 5.6867e-06 | 6.0269e-05 | 5.6867e-06 | 6.0269e-05 |  |  | 0.67075 | 7.1088 |  |  |  |  | 0.67075 | 7.1088 | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Fabric Filter, pulse | 2004-03-01
coal | 10043 | Logan Generating Plant | NJ | Unit1 | B01 | Conventional Boiler | Wall firing - opposed firing | 241.7 | 2116 | 8.7547 | bituminous | 0.0836 | 0.004086 | [10 empty] | 2.4667e-06 | 2.1595e-05 |  |  | 2.4667e-06 | 2.1595e-05 | 1.2873e-05 | 0.0001127 |  |  | 7.8076e-05 | 0.00068353 | 1.2873e-05 | 0.0001127 | 8.3606e-06 | 7.3194e-05 |  |  | 6.737e-06 | 5.898e-05 | 6.737e-06 | 5.898e-05 |  |  | 0.090996 | 0.79664 |  |  | 0.10625 | 0.93018 | 0.090996 | 0.79664 | NOx control | Selective Catalytic Reduction | 1994-09-01 | SO2 control | Dry FGD - Spray Dryer | 1994-09-01 | PM control | Fabric Filter, reverse air | 1994-09-01
coal | 10566 | Chambers Cogeneration LP | NJ | Boil 1 | Boil 1 | Conventional Boiler | Wall firing - front firing | 142.5 | 1387 | 9.7333 | bituminous | 0.071311 | 0.0054197 | [10 empty] | 4.3433e-07 | 4.2275e-06 |  |  | 4.3433e-07 | 4.2275e-06 | 4.24e-05 | 0.00041269 |  |  |  |  | 4.24e-05 | 0.00041269 | 7.3682e-06 | 7.1717e-05 |  |  | 1.836e-05 | 0.00017871 | 7.3682e-06 | 7.1717e-05 |  |  | 0.15911 | 1.5487 |  |  |  |  | 0.15911 | 1.5487 | NOx control | Selective Catalytic Reduction | 1994-03-01 | SO2 control | Dry FGD - Spray Dryer | 1994-03-01 | PM control | Fabric Filter, reverse air | 1994-03-01
coal | 55076 | Red Hills Generating Facility | MS | 002 | AA-002 | Fluidized bed firing | Fluidized bed firing | 250 | 2382.3 | 9.5292 | lignite | 0.033823 | 0.0050437 | [10 empty] | 1.3143e-05 | 0.00012524 |  |  | 1.3143e-05 | 0.00012524 |  |  | 0.00036675 | 0.0034949 | 0.00038667 | 0.0036846 | 0.00036675 | 0.0034949 |  |  | 8.7975e-06 | 8.3833e-05 | 0.00015 | 0.0014294 | 8.7975e-06 | 8.3833e-05 |  |  | 0.12496 | 1.1908 |  |  |  |  | 0.12496 | 1.1908 | PM control | Fabric Filter, unspecified | 2002-05-01
coal | 55076 | Red Hills Generating Facility | MS | 001 | AA-001 | Fluidized bed firing | Fluidized bed firing | 250 | 2401 | 9.604 | lignite | 0.033823 | 0.0050437 | [10 empty] | 1.3143e-05 | 0.00012622 |  |  | 1.3143e-05 | 0.00012622 |  |  | 0.00036675 | 0.0035223 | 0.00038667 | 0.0037135 | 0.00036675 | 0.0035223 |  |  | 8.7975e-06 | 8.4491e-05 | 0.00015 | 0.0014406 | 8.7975e-06 | 8.4491e-05 |  |  | 0.12496 | 1.2002 |  |  |  |  | 0.12496 | 1.2002 | PM control | Fabric Filter, unspecified | 2002-05-01
coal | 10566 | Chambers Cogeneration LP | NJ | Boil 2 | Boil 2 | Conventional Boiler | Wall firing - front firing | 142.5 | 1387 | 9.7333 | bituminous | 0.07865 | 0.0056485 | [10 empty] | 6.7e-07 | 6.5213e-06 |  |  | 6.7e-07 | 6.5213e-06 | 5.6009e-05 | 0.00054515 |  |  |  |  | 5.6009e-05 | 0.00054515 | 9.2489e-06 | 9.0023e-05 |  |  |  |  | 9.2489e-06 | 9.0023e-05 |  |  | 0.16816 | 1.6367 |  |  |  |  | 0.16816 | 1.6367 | NOx control | Selective Catalytic Reduction | 1994-03-01 | SO2 control | Dry FGD - Spray Dryer | 1994-03-01 | PM control | Fabric Filter, reverse air | 1994-03-01
coal | 52071 | Sandow Station | TX | 5B | 5B | Fluidized bed firing | Fluidized bed firing | 282.35 | 2960 | 10.4834 | lignite | [12 empty] | 1.62e-05 | 0.00016983 |  |  | 1.62e-05 | 0.00016983 | 3.0185e-05 | 0.00031644 |  |  | 2.5524e-05 | 0.00026758 | 2.5524e-05 | 0.00026758 | 4.4525e-05 | 0.00046677 |  |  | 9.5233e-06 | 9.9837e-05 | 9.5233e-06 | 9.9837e-05 |  |  | 0.047983 | 0.50303 |  |  | 0.032 | 0.33547 | 0.032 | 0.33547 | NOx control | Selective Noncatalytic Reduction | 2009-07-01 | Other control | Activated carbon injection | 2009-08-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-07-01 | PM control | Fabric Filter, pulse | 2009-07-01
coal | 6016 | Duck Creek | IL | 001 | 1 | Conventional Boiler | Wall firing - unspecified | 400 | 4500 | 11.25 | subbituminous | 0.021977 | 0.0047007 | [10 empty] | 7.6333e-05 | 0.00085875 |  |  | 7.6333e-05 | 0.00085875 | 0.00050141 | 0.0056408 |  |  | 0.00114 | 0.012825 | 0.00050141 | 0.0056408 | 0.00045197 | 0.0050846 |  |  | 9.74e-06 | 0.00010957 | 9.74e-06 | 0.00010957 | [6 empty] | 0.0133 | 0.14963 | 0.0133 | 0.14963 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2009-03-01 | SO2 control | Wet FGD - Venturi Type | 2009-03-01
coal | 6204 | Laramie River Station | WY | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 610 | 6600 | 10.8197 | coal - subbituminous | [22 empty] | 0.00041077 | 0.0044444 | 0.00041077 | 0.0044444 |  |  |  |  | 1.1327e-05 | 0.00012255 | 1.1327e-05 | 0.00012255 | [10 empty] | SO2 control | Dry FGD - Spray Dryer | 1982-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-11-01
coal | 6041 | H L Spurlock Station | KY | Unit 04 | 4 | Fluidized bed firing | Fluidized bed firing | 300 | 2800 | 9.3333 | bituminous |  | 0.0091676 | 0.00029109 | 0.0027169 |  |  |  |  | 0.00029109 | 0.0027169 |  |  | 0.0027 | 0.0252 |  |  | 0.0027 | 0.0252 | 0.00013024 | 0.0012156 | 0.0002 | 0.0018667 | 0.00011844 | 0.0011054 | 0.00011844 | 0.0011054 | 4.8516e-05 | 0.00045281 | 0.0001 | 0.00093333 | 1.3333e-05 | 0.00012444 | 1.3333e-05 | 0.00012444 | 0.097767 | 0.91249 |  |  |  |  | 0.099333 | 0.92711 | 0.097767 | 0.91249 | NOx control | Selective Noncatalytic Reduction | 2009-04-01 | SO2 control | Dry FGD - Unspecified | 2009-04-01 | PM control | Fabric Filter, pulse | 2009-04-01
coal | 56224 | TS Power Plant | NV | TSPower | BLR100 | Conventional Boiler | Wall firing - opposed firing | 242 | 2112 | 8.7273 | subbituminous | 0.00060793 | 0.0034306 | [10 empty] | 0.00013433 | 0.0011724 |  |  | 0.00013433 | 0.0011724 | 6.5139e-05 | 0.00056849 |  |  | 0.0004 | 0.0034909 | 6.5139e-05 | 0.00056849 | 6.5139e-05 | 0.00056849 |  |  | 1.5011e-05 | 0.000131 | 1.5011e-05 | 0.000131 | 0.0427 | 0.37265 |  |  |  |  | 0.041667 | 0.36364 | 0.041667 | 0.36364 | NOx control | Selective Catalytic Reduction | 2008-03-01 | Other control | Activated carbon injection | 2008-03-01 | SO2 control | Dry FGD - Spray Dryer | 2008-03-01 | PM control | Fabric Filter, pulse | 2008-01-01
coal | 1082 | Walter Scott Jr. Energy Center | IA | 4 | 4 | Conventional Boiler | Wall firing - unspecified | 850 | 7675 | 9.0294 | subbituminous | 0.00083195 | 0.0027621 | [10 empty] | 1.5134e-06 | 1.3665e-05 |  |  | 1.5134e-06 | 1.3665e-05 | 7.3724e-05 | 0.00066568 |  |  | 3.8e-05 | 0.00034312 | 3.8e-05 | 0.00034312 | 1.5307e-05 | 0.00013821 |  |  | 2.9e-05 | 0.00026185 | 1.5307e-05 | 0.00013821 | 0.078 | 0.70429 |  |  |  |  | 0.041 | 0.37021 | 0.041 | 0.37021 | NOx control | Selective Catalytic Reduction | 2007-02-01 | Other control | Activated carbon injection | 2007-02-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-02-01 | PM control | Fabric Filter, pulse | 2007-02-01
coal | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_2c | 2 | Conventional Boiler | Tangential firing | 703 | 6893 | 9.8051 | bituminous | [6 empty] | 6.0033e-05 | 0.00058863 | 6.0033e-05 | 0.00058863 | [12 empty] | 5.65e-05 | 0.00055399 | 5.65e-05 | 0.00055399 |  |  |  |  | 2.117e-05 | 0.00020757 | 2.117e-05 | 0.00020757 | [6 empty] | 0.042 | 0.41182 | 0.042 | 0.41182 | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-05-01 | SO2 control | Wet FGD - Spray/Tray Type | 2007-04-20
coal | 708 | Hammond | GA | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 115 | 1138.032 | 9.8959 | bituminous | 0.022666 | 0.0097291 | [10 empty] | 8.9383e-06 | 8.8453e-05 |  |  | 8.9383e-06 | 8.8453e-05 | 7.8767e-05 | 0.00077947 |  |  |  |  | 7.8767e-05 | 0.00077947 | 2.1654e-05 | 0.00021429 |  |  |  |  | 2.1654e-05 | 0.00021429 | 0.029367 | 0.29061 | [6 empty] | 0.029367 | 0.29061 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-04-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
coal | 708 | Hammond | GA | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 115 | 1141.392 | 9.9251 | bituminous | 0.022666 | 0.0097291 | [10 empty] | 8.9383e-06 | 8.8714e-05 |  |  | 8.9383e-06 | 8.8714e-05 | 7.8767e-05 | 0.00078177 |  |  |  |  | 7.8767e-05 | 0.00078177 | 2.1654e-05 | 0.00021492 |  |  |  |  | 2.1654e-05 | 0.00021492 | 0.029367 | 0.29147 | [6 empty] | 0.029367 | 0.29147 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
coal | 708 | Hammond | GA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 115 | 1158.752 | 10.0761 | bituminous | 0.022666 | 0.0097291 | [10 empty] | 8.9383e-06 | 9.0064e-05 |  |  | 8.9383e-06 | 9.0064e-05 | 7.8767e-05 | 0.00079366 |  |  |  |  | 7.8767e-05 | 0.00079366 | 2.1654e-05 | 0.00021819 |  |  |  |  | 2.1654e-05 | 0.00021819 | 0.029367 | 0.2959 | [6 empty] | 0.029367 | 0.2959 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-02-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
coal | 708 | Hammond | GA | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 520 | 5458.53 | 10.4972 | bituminous | 0.022666 | 0.0097291 | [10 empty] | 8.9383e-06 | 9.3827e-05 |  |  | 8.9383e-06 | 9.3827e-05 | 7.8767e-05 | 0.00082683 |  |  |  |  | 7.8767e-05 | 0.00082683 | 2.1654e-05 | 0.00022731 |  |  |  |  | 2.1654e-05 | 0.00022731 | 0.029367 | 0.30827 | [6 empty] | 0.029367 | 0.30827 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
coal | 52071 | Sandow Station | TX | 5A | 5A | Fluidized bed firing | Fluidized bed firing | 282.35 | 2960 | 10.4834 | lignite | [12 empty] | 2.6597e-05 | 0.00027882 |  |  | 2.6597e-05 | 0.00027882 | 9.2435e-05 | 0.00096904 |  |  | 2.1186e-05 | 0.0002221 | 2.1186e-05 | 0.0002221 | 9.4701e-05 | 0.00099279 |  |  | 2.241e-05 | 0.00023493 | 2.241e-05 | 0.00023493 |  |  | 0.011155 | 0.11695 |  |  | 0.025667 | 0.26908 | 0.011155 | 0.11695 | NOx control | Selective Noncatalytic Reduction | 2009-08-01 | Other control | Activated carbon injection | 2009-08-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-08-01 | PM control | Fabric Filter, pulse | 2009-08-01
coal | 3179 | Hatfield's Ferry Power Station | PA | 001 | 1 | Conventional Boiler | Wall firing - opposed firing | 590 | 5700 | 9.661 | bituminous | 0.033236 | 0.004807 | [10 empty] | 0.0019433 | 0.018775 |  |  | 0.0019433 | 0.018775 | 0.0001313 | 0.0012685 |  |  | 2.47e-05 | 0.00023863 | 2.47e-05 | 0.00023863 | 7.7176e-05 | 0.0007456 |  |  | 2.47e-05 | 0.00023863 | 2.47e-05 | 0.00023863 |  |  | 0.031525 | 0.30456 |  |  |  |  | 0.031525 | 0.30456 | PM control | Electrostatic precipitator, cold side, unspecified | 1969-01-01 | SO2 control | Wet FGD - Spray Type | 2009-06-01
coal | 108 | HOLCOMB | KS | SGU1 | SGU1 | Conventional Boiler | Wall firing - opposed firing | 387 | 3389 | 8.7571 | [15 empty] | 1e-06 | 8.7571e-06 | 1e-06 | 8.7571e-06 |  |  |  |  | 2.6e-05 | 0.00022768 | 2.6e-05 | 0.00022768 |  |  |  |  | 2.8e-05 | 0.0002452 | 2.8e-05 | 0.0002452 | [10 empty] | SO2 control | Dry FGD - Spray Dryer | 1983-08-01 | PM control | Fabric Filter, reverse air | 1983-08-01
coal | 55749 | Hardin Generator Project | MT | PC1 | PC1 | Conventional Boiler | Wall firing - unspecified | 119 | 1304 | 10.958 | bituminous | [12 empty] | 1.0433e-05 | 0.00011433 |  |  | 1.0433e-05 | 0.00011433 | 0.0001455 | 0.0015944 |  |  | 5e-05 | 0.0005479 | 5e-05 | 0.0005479 | 2.8873e-05 | 0.00031639 |  |  | 5e-05 | 0.0005479 | 2.8873e-05 | 0.00031639 | 0.095333 | 1.0447 |  |  |  |  | 0.104 | 1.1396 | 0.095333 | 1.0447 | NOx control | Selective Catalytic Reduction | 2006-04-01 | Other control | Activated carbon injection |  | SO2 control | Dry FGD - Spray Dryer | 2006-04-01 | PM control | Fabric Filter, pulse | 2006-04-01
coal | 703 | Bowen | GA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 755 | 7284.11 | 9.6478 | bituminous | 0.069634 | 0.0044876 | [10 empty] | 1.0733e-05 | 0.00010355 |  |  | 1.0733e-05 | 0.00010355 | 0.00015567 | 0.0015018 |  |  |  |  | 0.00015567 | 0.0015018 | 2.9983e-05 | 0.00028928 |  |  |  |  | 2.9983e-05 | 0.00028928 | [10 empty] | NOx control | Selective Catalytic Reduction | 2001-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1981-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-09-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
coal | 6761 | Rawhide | CO | Rawhide101 | 101 | Conventional Boiler | Tangential firing | 305 | 2800 | 9.1803 | subbituminous | [12 empty] | 1.7967e-05 | 0.00016494 |  |  | 1.7967e-05 | 0.00016494 | 0.00033354 | 0.003062 |  |  | 3.6081e-05 | 0.00033124 | 3.6081e-05 | 0.00033124 | 4.6491e-05 | 0.0004268 |  |  | 3e-05 | 0.00027541 | 3e-05 | 0.00027541 | 0.078533 | 0.72096 | [6 empty] | 0.078533 | 0.72096 | SO2 control | Dry FGD - Spray Dryer | 1984-04-01 | PM control | Fabric Filter, reverse air | 1984-04-01
coal | 4078 | Weston | WI | W4 | 4 | Conventional Boiler | Wall firing - opposed firing | 574.5 | 5173.07 | 9.0045 | subbituminous | [12 empty] | 0.00017233 | 0.0015518 |  |  | 0.00017233 | 0.0015518 |  |  |  |  | 7.6667e-05 | 0.00069034 | 7.6667e-05 | 0.00069034 |  |  |  |  | 3.1e-05 | 0.00027914 | 3.1e-05 | 0.00027914 | 0.061233 | 0.55137 |  |  |  |  | 0.05 | 0.45022 | 0.05 | 0.45022 | NOx control | Selective Catalytic Reduction | 2008-07-01 | Other control | Activated carbon injection | 2008-07-01 | SO2 control | Dry FGD - Spray Dryer | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-07-01
coal | 130 | Cross | SC | C4 | 4 | Conventional Boiler | Tangential firing | 625 | 6798 | 10.8768 | bituminous | 0.12985 | 6.8615 | [10 empty] | 1.72e-05 | 0.00018708 |  |  | 1.72e-05 | 0.00018708 | 0.00022897 | 0.0024905 |  |  | 4.0967e-05 | 0.00044559 | 4.0967e-05 | 0.00044559 | 0.00010289 | 0.0011191 |  |  | 3.26e-05 | 0.00035458 | 3.26e-05 | 0.00035458 | 0.1386 | 1.5075 | [6 empty] | 0.1386 | 1.5075 | NOx control | Selective Catalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2008-05-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
coal | 54081 | Spruance Genco, LLC | VA | GEN3 | 3A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.091094 | 0.0040189 | [10 empty] | 1.6191e-05 | 0.00021155 |  |  | 1.6191e-05 | 0.00021155 | 3.2235e-05 | 0.00042119 |  |  |  |  | 3.2235e-05 | 0.00042119 | 3.532e-05 | 0.0004615 |  |  |  |  | 3.532e-05 | 0.0004615 | 0.0227 | 0.2966 | 0.13054 | 1.7057 |  |  | 0.025247 | 0.32988 | 0.0227 | 0.2966 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 54081 | Spruance Genco, LLC | VA | GEN3 | 3B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.091094 | 0.0040189 | [10 empty] | 1.6191e-05 | 0.00021155 |  |  | 1.6191e-05 | 0.00021155 | 3.2235e-05 | 0.00042119 |  |  |  |  | 3.2235e-05 | 0.00042119 | 3.532e-05 | 0.0004615 |  |  |  |  | 3.532e-05 | 0.0004615 | 0.0227 | 0.2966 | 0.13054 | 1.7057 |  |  | 0.025247 | 0.32988 | 0.0227 | 0.2966 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 130 | Cross | SC | C3 | 3 | Conventional Boiler | Tangential firing | 625 | 6058 | 9.6928 | bituminous | 0.0817 | 0.0054164 | [10 empty] | 1.1373e-05 | 0.00011024 |  |  | 1.1373e-05 | 0.00011024 | 6.894e-05 | 0.00066822 |  |  | 0.000276 | 0.0026752 | 6.894e-05 | 0.00066822 | 6.7011e-05 | 0.00064953 |  |  | 4.1533e-05 | 0.00040257 | 4.1533e-05 | 0.00040257 | 0.0743 | 0.72018 | [6 empty] | 0.0743 | 0.72018 | NOx control | Selective Catalytic Reduction | 2006-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2006-08-01 | SO2 control | Wet FGD - Spray Type | 2006-08-01
coal | 703 | Bowen | GA | Unit 3 | 3 | Conventional Boiler | Tangential firing | 933 | 8184.748 | 8.7725 | bituminous | 0.086573 | 0.0050255 | [10 empty] | 1.13e-05 | 9.9129e-05 |  |  | 1.13e-05 | 9.9129e-05 | 0.00024955 | 0.0021892 |  |  |  |  | 0.00024955 | 0.0021892 | 4.4955e-05 | 0.00039437 |  |  |  |  | 4.4955e-05 | 0.00039437 | 0.071933 | 0.63104 | [6 empty] | 0.071933 | 0.63104 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
coal | 4941 | Navajo Generating Station | AZ | 001 | 1 | Conventional Boiler | Tangential firing | 812 | 7450 | 9.1749 | bituminous | 0.00083008 | 0.0073047 | 0.00029463 | 0.0027032 |  |  |  |  | 0.00029463 | 0.0027032 |  |  | 0.0008 | 0.0073399 |  |  | 0.0008 | 0.0073399 | 6.4809e-05 | 0.00059462 | 5e-05 | 0.00045874 |  |  | 5e-05 | 0.00045874 | 4.9105e-05 | 0.00045053 | 5e-05 | 0.00045874 |  |  | 4.9105e-05 | 0.00045053 | [10 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1974-05-01 | SO2 control | Wet FGD - Spray Type | 1999-04-01
coal | 7097 | J K Spruce | TX | 1 | BLR1 | Conventional Boiler | Tangential firing | 580 | 6361 | 10.9672 | bituminous | 0.0029487 | 0.0031795 | [10 empty] | 0.00031667 | 0.003473 |  |  | 0.00031667 | 0.003473 | 7.6237e-05 | 0.00083611 |  |  |  |  | 7.6237e-05 | 0.00083611 | 4.9757e-05 | 0.0005457 |  |  | 0.00015333 | 0.0016816 | 4.9757e-05 | 0.0005457 | [10 empty] | PM control | Fabric Filter, reverse air | 1992-07-01 | SO2 control | Wet FGD - Spray Type | 1992-12-01
coal | 4941 | Navajo Generating Station | AZ | 002 | 2 | Conventional Boiler | Tangential firing | 812 | 7450 | 9.1749 | bituminous | 0.00091496 | 0.0073633 | 0.00031432 | 0.0028838 |  |  |  |  | 0.00031432 | 0.0028838 |  |  | 0.0008 | 0.0073399 |  |  | 0.0008 | 0.0073399 | 6.965e-05 | 0.00063903 | 6.6667e-05 | 0.00061166 |  |  | 6.6667e-05 | 0.00061166 | 5.2386e-05 | 0.00048064 | 5e-05 | 0.00045874 |  |  | 5e-05 | 0.00045874 | [10 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1975-04-01 | SO2 control | Wet FGD - Spray Type | 1998-04-01
coal | 2706 | Asheville Steam Electric Plant | NC | Ash_Cfg_1d | 1 | Conventional Boiler | Wall firing - front firing | 207 | 1914 | 9.2464 | bituminous | 19.8666 | [5 empty] | 1.2367e-05 | 0.00011435 | 1.2367e-05 | 0.00011435 |  |  | 0.000321 | 0.0029681 |  |  | 0.000321 | 0.0029681 | 0.0061356 | 0.056732 |  |  | 0.00029533 | 0.0027308 | 0.00029533 | 0.0027308 | 6.2577e-05 | 0.00057862 |  |  | 5.01e-05 | 0.00046324 | 5.01e-05 | 0.00046324 |  |  | 0.051661 | 0.47768 |  |  | 0.038 | 0.35136 | 0.038 | 0.35136 | NOx control | Selective Catalytic Reduction | 2007-06-14 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2005-11-17 | SO2 control | Wet FGD - Spray/Tray Type | 2005-11-17
coal | 10672 | Cedar Bay Generating Company L.P. | FL | CBC1 | CBC | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | 11.5543 | bituminous | 0.054795 | [11 empty] | 8.6667e-06 | 0.00010014 |  |  | 8.6667e-06 | 0.00010014 | 0.049706 | 0.57432 | 0.049985 | 0.57754 |  |  | 0.049706 | 0.57432 | 5.0206e-05 | 0.0005801 | 5.0333e-05 | 0.00058157 | 7e-05 | 0.0008088 | 5.0206e-05 | 0.0005801 | 0.13557 | 1.5664 | [6 empty] | 0.13557 | 1.5664 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
coal | 50976 | INDIANTOWN COGENERATION L.P. | FL | 001 | AABO1 | Conventional Boiler | Wall firing - opposed firing | 361 | 3422 | 9.4792 | bituminous | 0.12078 | [11 empty] | 6.7e-07 | 6.3511e-06 |  |  | 6.7e-07 | 6.3511e-06 | 3.5766e-05 | 0.00033904 |  |  |  |  | 3.5766e-05 | 0.00033904 | 9.4655e-05 | 0.00089726 |  |  | 5.0377e-05 | 0.00047753 | 5.0377e-05 | 0.00047753 |  |  | 0.14692 | 1.3927 |  |  | 0.12667 | 1.2007 | 0.12667 | 1.2007 | NOx control | Selective Catalytic Reduction | 1995-12-01 | SO2 control | Dry FGD - Spray Dryer | 1995-12-01 | PM control | Fabric Filter, pulse | 1995-12-01
coal | 10672 | Cedar Bay Generating Company L.P. | FL | CBA1 | CBA | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | 11.5543 | bituminous | 0.058349 | [11 empty] | 9.1e-05 | 0.0010514 |  |  | 9.1e-05 | 0.0010514 | 0.042543 | 0.49155 | 0.040228 | 0.46481 |  |  | 0.040228 | 0.46481 | 5.4742e-05 | 0.0006325 | 5.2e-05 | 0.00060083 | 6e-05 | 0.00069326 | 5.2e-05 | 0.00060083 | [10 empty] | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
coal | 10743 | Morgantown Energy Facility | WV | Unit 1&2 | CFB1 | Fluidized bed firing | Fluidized bed firing | 29 | 457 | 15.7586 | bituminous | 0.012126 | 0.016006 | [10 empty] | 0.00153 | 0.024005 |  |  | 0.00153 | 0.024005 | 0.01455 | 0.22828 | 0.0073 | 0.11453 |  |  | 0.0073 | 0.11453 | 0.00010482 | 0.0016447 | 5.2633e-05 | 0.0008258 |  |  | 5.2633e-05 | 0.0008258 |  |  | 0.58928 | 9.2457 |  |  |  |  | 0.58928 | 9.2457 | PM control | Fabric Filter, pulse | 1992-01-01 | PM control | Fabric Filter, pulse | 1992-01-01
coal | 10743 | Morgantown Energy Facility | WV | Unit 1&2 | CFB2 | Fluidized bed firing | Fluidized bed firing | 29 | 453 | 15.6207 | bituminous | 0.012126 | 0.016006 | [10 empty] | 0.00153 | 0.024005 |  |  | 0.00153 | 0.024005 | 0.01455 | 0.22828 | 0.0073 | 0.11453 |  |  | 0.0073 | 0.11453 | 0.00010482 | 0.0016447 | 5.2633e-05 | 0.0008258 |  |  | 5.2633e-05 | 0.0008258 |  |  | 0.58928 | 9.2457 |  |  |  |  | 0.58928 | 9.2457 | PM control | Fabric Filter, pulse | 1992-01-01 | PM control | Fabric Filter, pulse | 1992-01-01
coal | 10672 | Cedar Bay Generating Company L.P. | FL | CBB1 | CBB | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | 11.5543 | bituminous | 0.046999 | [11 empty] | 9e-06 | 0.00010399 |  |  | 9e-06 | 0.00010399 | 0.049879 | 0.57632 | 0.049247 | 0.56901 |  |  | 0.049247 | 0.56901 | 5.5154e-05 | 0.00063727 | 5.4333e-05 | 0.00062779 | 5.9333e-05 | 0.00068556 | 5.4333e-05 | 0.00062779 | [10 empty] | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
coal | 6113 | Gibson | IN | 4 | 4 | Conventional Boiler | Wall firing - opposed firing | 661 | 6265 | 9.4781 | bituminous | 0.028909 | 0.0067699 | [10 empty] | 4.4367e-05 | 0.00042051 |  |  | 4.4367e-05 | 0.00042051 | 0.00026058 | 0.0024698 |  |  | 0.00054699 | 0.0051844 | 0.00026058 | 0.0024698 | 0.00015811 | 0.0014986 |  |  | 5.6145e-05 | 0.00053215 | 5.6145e-05 | 0.00053215 |  |  | 0.16691 | 1.582 |  |  | 0.381 | 3.6111 | 0.16691 | 1.582 | NOx control | Selective Catalytic Reduction | 2003-04-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01 | SO2 control | Wet FGD - Tray Type | 1994-12-01
coal | 10678 | AES Warrior Run Cogeneration Facility | MD | BLR1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 202 | 2047 | 10.1337 | bituminous | 0.021176 | 0.006577 | [10 empty] | 0.0041059 | 0.041608 |  |  | 0.0041059 | 0.041608 | 0.015626 | 0.15835 |  |  |  |  | 0.015626 | 0.15835 | 5.623e-05 | 0.00056982 |  |  |  |  | 5.623e-05 | 0.00056982 | 0.15393 | 1.5599 | [6 empty] | 0.15393 | 1.5599 | NOx control | Selective Noncatalytic Reduction | 2000-02-01 | PM control | Fabric Filter, pulse | 2000-02-01
coal | 6041 | H L Spurlock Station | KY | Unit 03 | 3 | Fluidized bed firing | Fluidized bed firing | 300 | 2500 | 8.3333 | bituminous |  |  | 0.00027554 | 0.0022961 |  |  |  |  | 0.00027554 | 0.0022961 |  |  | 0.0011667 | 0.0097222 |  |  | 0.0011667 | 0.0097222 | 7.5133e-05 | 0.0006261 | 7.3333e-05 | 0.00061111 |  |  | 7.3333e-05 | 0.00061111 | 5.7403e-05 | 0.00047836 | 5.6667e-05 | 0.00047222 |  |  | 5.6667e-05 | 0.00047222 | 0.2807 | 2.3392 | [6 empty] | 0.2807 | 2.3392 | NOx control | Selective Noncatalytic Reduction | 2005-03-01 | SO2 control | Dry FGD - Unspecified | 2005-03-01 | PM control | Fabric Filter, pulse | 2005-03-01
coal | 56068 | Elm Road Generating Station | WI | ERGS-B1 | 1 | Conventional Boiler | Wall firing - unspecified | 677 | 6515 | 9.6233 | bituminous | 0.092235 | 0.0036898 | [10 empty] | 0.00016667 | 0.0016039 |  |  | 0.00016667 | 0.0016039 | 7.6401e-05 | 0.00073523 |  |  |  |  | 7.6401e-05 | 0.00073523 | 5.7206e-05 | 0.00055051 |  |  |  |  | 5.7206e-05 | 0.00055051 |  |  |  |  | 0.009 | 0.08661 |  |  | 0.009 | 0.08661 | NOx control | Selective Catalytic Reduction | 2009-10-01 | PM control | Fabric Filter, pulse | 2009-10-01 | SO2 control | Wet FGD - Spray Type | 2009-10-01 | Other control | Wet electrostatic precipitator | 2009-10-01
coal | 703 | Bowen | GA | Unit 4 | 4 | Conventional Boiler | Tangential firing | 933 | 8887.743 | 9.526 | bituminous | 0.11636 | 0.004704 | [10 empty] | 1.0833e-05 | 0.0001032 |  |  | 1.0833e-05 | 0.0001032 | 0.00011939 | 0.0011373 |  |  |  |  | 0.00011939 | 0.0011373 | 5.7474e-05 | 0.0005475 |  |  |  |  | 5.7474e-05 | 0.0005475 | 0.053933 | 0.51377 | [6 empty] | 0.053933 | 0.51377 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1975-11-01 | SO2 control | Wet FGD - Spray Type | 2008-12-01
coal | 4941 | Navajo Generating Station | AZ | 003 | 3 | Conventional Boiler | Tangential firing | 812 | 7450 | 9.1749 | bituminous | 0.00083112 | 0.0056516 | 0.00034737 | 0.0031871 |  |  |  |  | 0.00034737 | 0.0031871 |  |  | 0.00083333 | 0.0076457 |  |  | 0.00083333 | 0.0076457 | 9.3828e-05 | 0.00086086 | 9.6667e-05 | 0.0008869 |  |  | 9.3828e-05 | 0.00086086 | 5.7895e-05 | 0.00053118 | 6e-05 | 0.00055049 |  |  | 5.7895e-05 | 0.00053118 | [10 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1976-05-01 | SO2 control | Wet FGD - Spray Type | 1997-04-01
coal | 2378 | BL England | NJ | 2 Coal w or w/o TDF | 2 | Conventional Boiler | Cyclone firing | 167.3 | 1600 | 9.5637 | bituminous | 0.067182 |  | 0.00035703 | 0.0034146 |  |  |  |  | 0.00035703 | 0.0034146 |  |  | 0.00095 | 0.0090855 |  |  | 0.00095 | 0.0090855 | 0.0010116 | 0.0096746 | 0.001 | 0.0095637 | 0.00040495 | 0.0038728 | 0.00040495 | 0.0038728 | 5.9506e-05 | 0.00056909 | 0.0001 | 0.00095637 | 0.00018472 | 0.0017666 | 5.9506e-05 | 0.00056909 | [6 empty] | 0.30993 | 2.9641 | 0.30993 | 2.9641 | NOx control | Selective Noncatalytic Reduction | 1998-06-01 | Other control | Activated carbon injection | 2007-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
coal | 6170 | Pleasant Prairie | WI | PPPPB1 | 1 | Conventional Boiler | Wall firing - opposed firing | 655 | 6449 | 9.8458 | subbituminous | 0.0040029 | 0.0074702 | [10 empty] | 0.00019533 | 0.0019232 |  |  | 0.00019533 | 0.0019232 | 9.6556e-05 | 0.00095067 |  |  |  |  | 9.6556e-05 | 0.00095067 | 5.9544e-05 | 0.00058626 |  |  |  |  | 5.9544e-05 | 0.00058626 | [10 empty] | NOx control | Selective Catalytic Reduction | 2006-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-06-01 | SO2 control | Wet FGD - Spray Type | 2006-11-01
coal | 54755 | Roanoke Valley II | NC | Boiler 2 | BLR2 | Conventional Boiler | Wall firing - front firing | 50 | 560 | 11.2 | bituminous | 0.078934 | 0.0054352 | [10 empty] | 0.00085933 | 0.0096245 |  |  | 0.00085933 | 0.0096245 | 3.2175e-05 | 0.00036036 |  |  | 0.000492 | 0.0055104 | 3.2175e-05 | 0.00036036 | 6.0043e-05 | 0.00067248 |  |  |  |  | 6.0043e-05 | 0.00067248 | [10 empty] | NOx control | Selective Noncatalytic Reduction | 1995-06-01 | SO2 control | Dry FGD - Spray Dryer | 1995-06-01 | PM control | Fabric Filter, pulse | 1995-06-01
coal | 10673 | AES Hawaii | HI | 001 | BLR A | Fluidized bed firing | Fluidized bed firing | 101.5 | 1021.4 | 10.0631 | bituminous | 0.005514 | 0.0051881 | [10 empty] | 0.0019472 | 0.019595 |  |  | 0.0019472 | 0.019595 | 0.0028947 | 0.02913 |  |  |  |  | 0.0028947 | 0.02913 | 6.2111e-05 | 0.00062503 |  |  |  |  | 6.2111e-05 | 0.00062503 | 0.22333 | 2.2474 | [6 empty] | 0.22333 | 2.2474 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
coal | 525 | Hayden | CO | Unit 2 | 2 | Conventional Boiler | Tangential firing | 285 | 2712 | 9.5158 | bituminous | 0.0023437 | 0.010113 | [10 empty] | 1.7067e-06 | 1.624e-05 |  |  | 1.7067e-06 | 1.624e-05 | 0.00014256 | 0.0013566 |  |  |  |  | 0.00014256 | 0.0013566 | 6.2331e-05 | 0.00059313 |  |  |  |  | 6.2331e-05 | 0.00059313 | 0.13686 | 1.3024 |  |  | 0.12141 | 1.1553 |  |  | 0.12141 | 1.1553 | SO2 control | Dry FGD - Spray Dryer | 1999-06-01 | PM control | Fabric Filter, reverse air | 1999-06-01
coal | 54304 | Birchwood Power Facility | VA | 1A | 1A | Conventional Boiler | Tangential firing | 222 | 2300 | 10.3604 | bituminous | 0.030083 | 0.0016573 | [10 empty] | 1e-05 | 0.0001036 |  |  | 1e-05 | 0.0001036 |  |  | 0.00086667 | 0.008979 |  |  | 0.00086667 | 0.008979 |  |  | 6.3333e-05 | 0.00065616 |  |  | 6.3333e-05 | 0.00065616 | [10 empty] | NOx control | Selective Catalytic Reduction | 1996-10-01 | SO2 control | Dry FGD - Spray Dryer | 1996-10-01 | PM control | Fabric Filter, reverse air | 1996-10-01
coal | 8223 | Springerville | AZ | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 450 | 4200 | 9.3333 | subbituminous | 0.00099462 | 0.0052202 | [10 empty] | 0.0011277 | 0.010525 |  |  | 0.0011277 | 0.010525 |  |  | 0.00030598 | 0.0028558 |  |  | 0.00030598 | 0.0028558 |  |  | 0.00020733 | 0.0019351 | 6.4e-05 | 0.00059733 | 6.4e-05 | 0.00059733 | 0.074367 | 0.69409 |  |  |  |  | 0.099 | 0.924 | 0.074367 | 0.69409 | NOx control | Selective Catalytic Reduction | 2006-08-01 | SO2 control | Dry FGD - Spray Dryer | 2006-08-01 | PM control | Fabric Filter, pulse | 2006-08-01
coal | 2840 | Conesville | OH | CV-4 | 4 | Conventional Boiler | Tangential firing | 841.5 | 7960 | 9.4593 | bituminous | 0.041288 | 0.0042859 | [10 empty] | 0.00023333 | 0.0022072 |  |  | 0.00023333 | 0.0022072 | 0.00016321 | 0.0015439 |  |  |  |  | 0.00016321 | 0.0015439 | 6.5255e-05 | 0.00061726 |  |  |  |  | 6.5255e-05 | 0.00061726 | 0.157 | 1.4851 | [6 empty] | 0.157 | 1.4851 | NOx control | Selective Catalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-06-01 | Other control | Dry sorbent injection | 2009-06-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2009-06-01
coal | 54035 | Roanoke Valley I | NC | Boiler 1 | BLR1 | Conventional Boiler | Wall firing - front firing | 182 | 1700 | 9.3407 | bituminous | 0.065768 | 0.0075852 | [10 empty] | 0.000288 | 0.0026901 |  |  | 0.000288 | 0.0026901 | 7.3157e-05 | 0.00068333 |  |  | 0.000563 | 0.0052588 | 7.3157e-05 | 0.00068333 | 6.5791e-05 | 0.00061453 |  |  |  |  | 6.5791e-05 | 0.00061453 | [10 empty] | SO2 control | Dry FGD - Spray Dryer | 1994-05-01 | PM control | Fabric Filter, reverse air | 1994-05-01
coal | 3944 | Harrison Power Station | WV | Boiler1 | 1 | Conventional Boiler | Wall firing - unspecified | 693 | 5779 | 8.3391 | bituminous | 0.038976 | 0.0085591 |  |  |  |  | 0.2 | 1.6678 | 0.2 | 1.6678 |  |  | 2.4919e-05 | 0.0002078 |  |  | 2.4919e-05 | 0.0002078 | 0.00060157 | 0.0050165 |  |  | 0.9 | 7.5052 | 0.00060157 | 0.0050165 | 6.5821e-05 | 0.00054888 |  |  |  |  | 6.5821e-05 | 0.00054888 |  |  | 0.17829 | 1.4868 |  |  |  |  | 0.17829 | 1.4868 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1974-12-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
coal | 6052 | Wansley | GA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 920 | 8554.28 | 9.2981 | bituminous | 0.11287 | 0.0063207 | [10 empty] | 0.00031467 | 0.0029258 |  |  | 0.00031467 | 0.0029258 | 0.00022052 | 0.0020504 |  |  |  |  | 0.00022052 | 0.0020504 | 6.6759e-05 | 0.00062073 |  |  |  |  | 6.6759e-05 | 0.00062073 | [10 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-04-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
coal | 963 | Dallman | IL | 34 | 34 | Conventional Boiler | Wall firing - opposed firing | 229.4 | 1924.9 | 8.391 | bituminous | 0.15592 | 0.0034105 | [10 empty] | 0.00024467 | 0.002053 |  |  | 0.00024467 | 0.002053 |  |  | 0.00010033 | 0.0008419 | 9.7e-05 | 0.00081393 | 9.7e-05 | 0.00081393 |  |  | 6.7e-05 | 0.0005622 | 6.9e-05 | 0.00057898 | 6.7e-05 | 0.0005622 | 0.118 | 0.99014 | [6 empty] | 0.118 | 0.99014 | NOx control | Selective Catalytic Reduction | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01 | SO2 control | Wet FGD - Packed Type | 2009-05-01 | Other control | Wet electrostatic precipitator | 2009-05-01
coal | 477 | Valmont | CO | Unit 5 | 5 | Conventional Boiler | Tangential firing | 196 | 1845 | 9.4133 | bituminous | 0.0041123 | 0.0081141 | [10 empty] | 1.9767e-06 | 1.8607e-05 |  |  | 1.9767e-06 | 1.8607e-05 | 0.00021111 | 0.0019872 |  |  |  |  | 0.00021111 | 0.0019872 | 7.246e-05 | 0.00068209 |  |  |  |  | 7.246e-05 | 0.00068209 | 0.11412 | 1.0742 |  |  | 0.11116 | 1.0464 |  |  | 0.11116 | 1.0464 | SO2 control | Dry FGD - Spray Dryer | 2002-04-01 | PM control | Fabric Filter, reverse air | 1984-04-01
coal | 525 | Hayden | CO | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 202 | 1963 | 9.7178 | bituminous | 0.0018327 | 0.010893 | [10 empty] | 6.13e-06 | 5.957e-05 |  |  | 6.13e-06 | 5.957e-05 | 0.00021783 | 0.0021169 |  |  |  |  | 0.00021783 | 0.0021169 | 7.315e-05 | 0.00071086 |  |  |  |  | 7.315e-05 | 0.00071086 | 0.11897 | 1.1561 |  |  | 0.12021 | 1.1682 |  |  | 0.11897 | 1.1561 | SO2 control | Dry FGD - Spray Dryer | 1998-12-01 | PM control | Fabric Filter, reverse air | 1998-12-01
coal | 3181 | Mitchell Power Station | PA | 033 | 33 | Conventional Boiler | Tangential firing | 289 | 2563 | 8.8685 | coal - bituminous | [6 empty] | 0.00010486 | 0.00092995 | 0.00010486 | 0.00092995 | [12 empty] | 0.00097203 | 0.0086205 | 0.00097203 | 0.0086205 |  |  |  |  | 7.3553e-05 | 0.00065231 | 7.3553e-05 | 0.00065231 | [10 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1971-01-01 | SO2 control | Wet FGD - Spray Type | 1983-01-01
coal | 2079 | Hawthorn | MO | 5A | 5A | Conventional Boiler | Wall firing - opposed firing | 594 | 6600 | 11.1111 | subbituminous, bituminous | 0.00086835 | 0.0061392 | [10 empty] | 4.6267e-05 | 0.00051407 |  |  | 4.6267e-05 | 0.00051407 | 7.2108e-05 | 0.00080121 |  |  | 0.00027 | 0.003 | 7.2108e-05 | 0.00080121 | 7.3847e-05 | 0.00082053 |  |  |  |  | 7.3847e-05 | 0.00082053 |  |  | 0.12535 | 1.3928 |  |  |  |  | 0.12535 | 1.3928 | NOx control | Selective Catalytic Reduction | 2001-05-01 | SO2 control | Dry FGD - Spray Dryer | 2001-05-01 | PM control | Fabric Filter, pulse | 2001-05-01
coal | 6170 | Pleasant Prairie | WI | PPPPB2 | 2 | Conventional Boiler | Wall firing - opposed firing | 643 | 6449 | 10.0295 | subbituminous | 0.0029916 | 0.0072305 | [10 empty] | 0.00021 | 0.0021062 |  |  | 0.00021 | 0.0021062 | 9.4427e-05 | 0.00094706 |  |  |  |  | 9.4427e-05 | 0.00094706 | 7.6263e-05 | 0.00076488 |  |  |  |  | 7.6263e-05 | 0.00076488 | [10 empty] | NOx control | Selective Catalytic Reduction | 2003-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1985-05-01 | SO2 control | Wet FGD - Spray Type | 2007-03-01
coal | 3935 | John E. Amos | WV | AM-3 | 3 | Conventional Boiler | Wall firing - opposed firing | 1300 | 11936 | 9.1815 | bituminous | 0.064565 | 0.0058855 | [10 empty] | 0.000234 | 0.0021485 |  |  | 0.000234 | 0.0021485 | 0.00031262 | 0.0028703 |  |  |  |  | 0.00031262 | 0.0028703 | 7.7926e-05 | 0.00071548 |  |  |  |  | 7.7926e-05 | 0.00071548 | 0.052143 | 0.47875 | [6 empty] | 0.052143 | 0.47875 | NOx control | Selective Catalytic Reduction | 2001-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-10-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
coal | 10673 | AES Hawaii | HI | 002 | BLR B | Fluidized bed firing | Fluidized bed firing | 101.5 | 944.2 | 9.3025 | bituminous | 0.0046502 | 0.004278 | [10 empty] | 0.0021592 | 0.020086 |  |  | 0.0021592 | 0.020086 | 0.0018275 | 0.017 |  |  |  |  | 0.0018275 | 0.017 | 7.8954e-05 | 0.00073447 |  |  |  |  | 7.8954e-05 | 0.00073447 | 0.22503 | 2.0934 | [6 empty] | 0.22503 | 2.0934 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
coal | 2828 | Cardinal | OH | CD-U2 | 2 | Conventional Boiler | Wall firing - opposed firing | 615.2 | 5275 | 8.5744 | bituminous | 0.073673 | 0.0071919 | [10 empty] | 0.00023667 | 0.0020293 |  |  | 0.00023667 | 0.0020293 | 0.00018536 | 0.0015893 |  |  |  |  | 0.00018536 | 0.0015893 | 8.1572e-05 | 0.00069944 |  |  |  |  | 8.1572e-05 | 0.00069944 | 0.1369 | 1.1738 | [6 empty] | 0.1369 | 1.1738 | NOx control | Selective Catalytic Reduction | 2003-01-01 | Other control | Dry sorbent injection | 2007-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2007-12-01
coal | 113 | Cholla | AZ | 003 | 3 | Conventional Boiler | Tangential firing | 305 | 2929 | 9.6033 | bituminous | 0.0010451 | 0.005966 | [10 empty] | 5.3667e-05 | 0.00051538 |  |  | 5.3667e-05 | 0.00051538 | 8.0274e-05 | 0.0007709 |  |  |  |  | 8.0274e-05 | 0.0007709 | 8.2224e-05 | 0.00078962 |  |  |  |  | 8.2224e-05 | 0.00078962 |  |  |  |  | 0.13794 | 1.3247 | 0.113 | 1.0852 | 0.113 | 1.0852 | PM control | Fabric Filter, unspecified | 2009-01-01 | SO2 control | Wet FGD - Unspecified | 2009-01-01
coal | 1356 | Ghent | KY | GH1 | 1 | Conventional Boiler | Tangential firing | 520 | 6286 | 12.0885 | bituminous | 0.050521 | 0.0060389 | 0.00039703 | 0.0047994 | 0.000397 | 0.0047991 |  |  | 0.000397 | 0.0047991 |  |  | 0.0011 | 0.013297 |  |  | 0.0011 | 0.013297 | 0.00017961 | 0.0021712 |  |  |  |  | 0.00017961 | 0.0021712 | 8.39e-05 | 0.0010142 |  |  |  |  | 8.39e-05 | 0.0010142 | 0.084433 | 1.0207 | [6 empty] | 0.084433 | 1.0207 | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-12-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
coal | 564 | Stanton Energy Center | FL | 2 coal | 2 | Conventional Boiler | Wall firing - opposed firing | 468 | 4286 | 9.1581 | coal - bituminous | [12 empty] | 0.000323 | 0.0029581 |  |  | 0.000323 | 0.0029581 | 0.0010495 | 0.0096113 |  |  |  |  | 0.0010495 | 0.0096113 | 8.4724e-05 | 0.00077591 |  |  |  |  | 8.4724e-05 | 0.00077591 | [10 empty] | NOx control | Selective Catalytic Reduction | 1996-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1996-06-01 | SO2 control | Wet FGD - Spray Type | 1996-06-01
coal | 3935 | John E. Amos | WV | AM-2 | 2 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | 0.053657 | 0.0048561 | [10 empty] | 0.000209 | 0.0017974 |  |  | 0.000209 | 0.0017974 | 0.00018274 | 0.0015715 |  |  |  |  | 0.00018274 | 0.0015715 | 8.4782e-05 | 0.0007291 |  |  |  |  | 8.4782e-05 | 0.0007291 | 0.045067 | 0.38756 | [6 empty] | 0.045067 | 0.38756 | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-12-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
coal | 2828 | Cardinal | OH | CD-U1 | 1 | Conventional Boiler | Wall firing - opposed firing | 615.2 | 5275 | 8.5744 | bituminous | 0.043095 | 0.0042617 | [10 empty] | 0.00024633 | 0.0021122 |  |  | 0.00024633 | 0.0021122 | 0.00014296 | 0.0012258 |  |  |  |  | 0.00014296 | 0.0012258 | 8.6175e-05 | 0.00073891 |  |  |  |  | 8.6175e-05 | 0.00073891 | 0.23495 | 2.0146 | [6 empty] | 0.23495 | 2.0146 | NOx control | Selective Catalytic Reduction | 2003-01-01 | Other control | Dry sorbent injection | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2008-03-01
coal | 113 | Cholla | AZ | 004 | 4 | Conventional Boiler | Tangential firing | 425 | 4268 | 10.0424 | bituminous | 0.0016079 | 0.0047511 | [10 empty] | 5.9667e-05 | 0.00059919 |  |  | 5.9667e-05 | 0.00059919 | 8.5239e-05 | 0.000856 |  |  |  |  | 8.5239e-05 | 0.000856 | 8.7302e-05 | 0.00087672 |  |  |  |  | 8.7302e-05 | 0.00087672 |  |  |  |  | 0.15058 | 1.5121 | 0.1 | 1.0042 | 0.1 | 1.0042 | PM control | Fabric Filter, unspecified | 2008-01-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
coal | 2535 | AES Cayuga, LLC | NY | Unit_2 | 2 | Conventional Boiler | Tangential firing | 168 | 1450 | 8.631 | bituminous | 0.042877 | 0.0035969 | [16 empty] | 0.00046614 | 0.0040232 |  |  |  |  | 0.00046614 | 0.0040232 | 8.7624e-05 | 0.00075628 |  |  |  |  | 8.7624e-05 | 0.00075628 | 0.72807 | 6.2839 | [6 empty] | 0.72807 | 6.2839 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning |  | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 3118 | Conemaugh | PA | CON-2 | 2 | Conventional Boiler | Tangential firing | 936 | 8985 | 9.5994 | bituminous | 0.049911 | 0.0048542 | [10 empty] | 3.0933e-06 | 2.9694e-05 |  |  | 3.0933e-06 | 2.9694e-05 | 0.00033266 | 0.0031933 |  |  | 0.00046667 | 0.0044797 | 0.00033266 | 0.0031933 | 8.913e-05 | 0.00085559 |  |  | 0.00046667 | 0.0044797 | 8.913e-05 | 0.00085559 |  |  | 0.13458 | 1.2919 |  |  |  |  | 0.13458 | 1.2919 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Spray Type | 1995-11-01
coal | 645 | Big Bend | FL | BB01_pre-SCR | 1 | Conventional Boiler | Wall firing - opposed firing | 410 | 4037 | 9.8463 | bituminous | 0.14548 | 0.0052067 | [10 empty] | 0.030062 | 0.296 |  |  | 0.030062 | 0.296 | 0.003789 | 0.037308 |  |  |  |  | 0.003789 | 0.037308 | 8.9805e-05 | 0.00088425 |  |  |  |  | 8.9805e-05 | 0.00088425 | [6 empty] | 0.082901 | 0.81627 | 0.082901 | 0.81627 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1970-10-01 | SO2 control | Wet FGD - Packed Type | 1999-12-01
coal | 645 | Big Bend | FL | BB02_SCR | 2 | Conventional Boiler | Wall firing - opposed firing | 410 | 3996 | 9.7463 | bituminous | 0.13792 | 0.0055617 | [8 empty] | 3.5806e-05 | 0.00034898 |  |  |  |  | 3.5806e-05 | 0.00034898 | 0.0063388 | 0.06178 |  |  |  |  | 0.0063388 | 0.06178 | 9.1702e-05 | 0.00089376 |  |  |  |  | 9.1702e-05 | 0.00089376 | [10 empty] | NOx control | Selective Catalytic Reduction | 2009-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-04-01 | SO2 control | Wet FGD - Packed Type | 1999-12-01
coal | 6052 | Wansley | GA | Unit 1 | 1 | Conventional Boiler | Tangential firing | 920 | 8445.789 | 9.1802 | bituminous | 0.10541 | 0.0061971 | [10 empty] | 0.00032767 | 0.003008 |  |  | 0.00032767 | 0.003008 | 0.00031074 | 0.0028526 |  |  |  |  | 0.00031074 | 0.0028526 | 9.181e-05 | 0.00084283 |  |  |  |  | 9.181e-05 | 0.00084283 | [10 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-12-01 | SO2 control | Wet FGD - Spray Type | 2008-12-01
coal | 54081 | Spruance Genco, LLC | VA | GEN1 | 1A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.096444 | 0.004413 | [10 empty] | 3.0435e-05 | 0.00039767 |  |  | 3.0435e-05 | 0.00039767 | 0.0035487 | 0.046368 |  |  |  |  | 0.0035487 | 0.046368 | 9.3168e-05 | 0.0012174 |  |  |  |  | 9.3168e-05 | 0.0012174 |  |  | 0.10313 | 1.3475 |  |  |  |  | 0.10313 | 1.3475 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 54081 | Spruance Genco, LLC | VA | GEN1 | 1B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.096444 | 0.004413 | [10 empty] | 3.0435e-05 | 0.00039767 |  |  | 3.0435e-05 | 0.00039767 | 0.0035487 | 0.046368 |  |  |  |  | 0.0035487 | 0.046368 | 9.3168e-05 | 0.0012174 |  |  |  |  | 9.3168e-05 | 0.0012174 |  |  | 0.10313 | 1.3475 |  |  |  |  | 0.10313 | 1.3475 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 6180 | Oak Grove | TX | OG1 | 1 | Conventional Boiler | Tangential firing | 817 | 8970 | 10.9792 | lignite | 0.011839 | 0.0085309 | [10 empty] | 1.5867e-05 | 0.0001742 |  |  | 1.5867e-05 | 0.0001742 | 0.00012026 | 0.0013203 |  |  | 0.00022667 | 0.0024886 | 0.00012026 | 0.0013203 | 9.3473e-05 | 0.0010263 |  |  | 0.00014 | 0.0015371 | 9.3473e-05 | 0.0010263 |  |  | 0.056335 | 0.61851 |  |  | 0.054 | 0.59288 | 0.054 | 0.59288 | NOx control | Selective Catalytic Reduction | 2009-08-01 | Other control | Activated carbon injection | 2009-08-01 | PM control | Fabric Filter, pulse | 2009-08-01 | SO2 control | Wet FGD - Spray Type | 2009-08-01
coal | 3118 | Conemaugh | PA | CON-1 | 1 | Conventional Boiler | Tangential firing | 936 | 8985 | 9.5994 | bituminous | 0.055238 | 0.0046158 | [10 empty] | 3.3533e-06 | 3.219e-05 |  |  | 3.3533e-06 | 3.219e-05 | 0.00028801 | 0.0027647 |  |  | 0.00033 | 0.0031678 | 0.00028801 | 0.0027647 | 9.451e-05 | 0.00090724 |  |  | 0.00017 | 0.0016319 | 9.451e-05 | 0.00090724 |  |  | 0.13917 | 1.336 |  |  |  |  | 0.13917 | 1.336 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-05-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 976 | Marion Generating Station | IL | 123 | 123 | Fluidized bed firing | Fluidized bed firing | 120 | 1250 | 10.4167 | bituminous | 0.1579 | 0.012084 | 0.020218 | 0.21061 |  |  |  |  | 0.020218 | 0.21061 |  |  | 1.38e-05 | 0.00014375 |  |  | 1.38e-05 | 0.00014375 | 0.020798 | 0.21665 |  |  |  |  | 0.020798 | 0.21665 | 9.7766e-05 | 0.0010184 |  |  |  |  | 9.7766e-05 | 0.0010184 |  |  | 0.47882 | 4.9877 |  |  |  |  | 0.47882 | 4.9877 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
coal | 68029 | AES Puerto Rico Cogeneration Facility | PR | Unit_2 | BLR2 | Fluidized bed firing | Fluidized bed firing | 255 | 2461.4 | 9.6525 | bituminous | 0.0037803 | 0.0026187 | [10 empty] | 0.0015407 | 0.014872 |  |  | 0.0015407 | 0.014872 | 9.5966e-05 | 0.00092632 |  |  |  |  | 9.5966e-05 | 0.00092632 | 9.8457e-05 | 0.00095036 |  |  |  |  | 9.8457e-05 | 0.00095036 | 0.00871 | 0.084074 | [6 empty] | 0.00871 | 0.084074 | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Spray Dryer |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
coal | 3098 | Elrama Power Plant | PA | ELR4-2 | 4 | Conventional Boiler | Wall firing - front firing | 185 | 1921 | 10.3838 | bituminous | 0.034678 | 0.0012869 | [10 empty] | 0.00026433 | 0.0027448 |  |  | 0.00026433 | 0.0027448 | 0.00055304 | 0.0057426 |  |  |  |  | 0.00055304 | 0.0057426 | 9.9974e-05 | 0.0010381 |  |  |  |  | 9.9974e-05 | 0.0010381 | [10 empty] | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1960-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-11-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
coal | 3098 | Elrama Power Plant | PA | ELR3-2 | 3 | Conventional Boiler | Vertical firing | 125 | 1303 | 10.424 | bituminous | 0.034678 | 0.0012869 | [10 empty] | 0.00026433 | 0.0027554 |  |  | 0.00026433 | 0.0027554 | 0.00055304 | 0.0057649 |  |  |  |  | 0.00055304 | 0.0057649 | 9.9974e-05 | 0.0010421 |  |  |  |  | 9.9974e-05 | 0.0010421 | [10 empty] | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1954-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1954-11-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
coal | 3098 | Elrama Power Plant | PA | ELR1-2 | 1 | Conventional Boiler | Vertical firing | 100 | 1254 | 12.54 | bituminous | 0.034678 | 0.0012869 | [10 empty] | 0.00026433 | 0.0033147 |  |  | 0.00026433 | 0.0033147 | 0.00055304 | 0.0069351 |  |  |  |  | 0.00055304 | 0.0069351 | 9.9974e-05 | 0.0012537 |  |  |  |  | 9.9974e-05 | 0.0012537 | [10 empty] | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1952-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1952-06-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
coal | 3098 | Elrama Power Plant | PA | ELR2-2 | 2 | Conventional Boiler | Vertical firing | 100 | 1254 | 12.54 | bituminous | 0.034678 | 0.0012869 | [10 empty] | 0.00026433 | 0.0033147 |  |  | 0.00026433 | 0.0033147 | 0.00055304 | 0.0069351 |  |  |  |  | 0.00055304 | 0.0069351 | 9.9974e-05 | 0.0012537 |  |  |  |  | 9.9974e-05 | 0.0012537 | [10 empty] | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1953-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1953-03-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
coal | 8223 | Springerville | AZ | 4 | 4 | Conventional Boiler | Wall firing - opposed firing | 450 | 4200 | 9.3333 | bituminous | 0.00089646 | 0.0049465 | [10 empty] | 0.00059567 | 0.0055596 |  |  | 0.00059567 | 0.0055596 |  |  | 0.0046462 | 0.043364 |  |  | 0.0046462 | 0.043364 |  |  | 0.000252 | 0.002352 | 0.0001 | 0.00093333 | 0.0001 | 0.00093333 | 0.069233 | 0.64618 | [6 empty] | 0.069233 | 0.64618 | NOx control | Selective Catalytic Reduction | 2009-12-01 | SO2 control | Dry FGD - Spray Dryer | 2009-12-01 | PM control | Fabric Filter, pulse | 2009-12-01
coal | 10603 | Ebensburg Power Company | PA | EPC01 | 031 | Fluidized bed firing | Fluidized bed firing | 58 | 830 | 14.3103 | coal refuse (culm or gob) | [22 empty] | 0.024333 | 0.34822 | 0.024333 | 0.34822 |  |  |  |  | 0.0001 | 0.001431 | 0.0001 | 0.001431 |  |  | 0.83703 | 11.9782 |  |  |  |  | 0.83703 | 11.9782 | PM control | Fabric Filter, pulse | 1990-11-01
coal | 68029 | AES Puerto Rico Cogeneration Facility | PR | Unit_1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 255 | 2461.4 | 9.6525 | bituminous | 0.0035929 | 0.0028647 | [10 empty] | 0.0012522 | 0.012087 |  |  | 0.0012522 | 0.012087 | 0.00010185 | 0.00098314 |  |  |  |  | 0.00010185 | 0.00098314 | 0.00010252 | 0.00098963 |  |  |  |  | 0.00010252 | 0.00098963 | 0.009 | 0.086873 | [6 empty] | 0.009 | 0.086873 | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Spray Dryer |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
coal | 2535 | AES Cayuga, LLC | NY | Unit_1 | 1 | Conventional Boiler | Tangential firing | 164 | 1462 | 8.9146 | bituminous | 0.04599 | 0.0034654 | [16 empty] | 0.00035901 | 0.0032004 |  |  |  |  | 0.00035901 | 0.0032004 | 0.00010627 | 0.00094731 |  |  |  |  | 0.00010627 | 0.00094731 | 0.45857 | 4.088 | [6 empty] | 0.45857 | 4.088 | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning |  | SO2 control | Wet FGD - Spray Type | 1995-06-01
coal | 2917 | Hamilton | OH | Unit 9 | 9 | Conventional Boiler | Tangential firing | 50.6 | 729 | 14.4071 | bituminous | 0.054811 | 0.0050889 | [10 empty] | 5.9e-05 | 0.00085002 |  |  | 5.9e-05 | 0.00085002 | 0.00011019 | 0.0015875 |  |  |  |  | 0.00011019 | 0.0015875 | 0.00010963 | 0.0015795 |  |  |  |  | 0.00010963 | 0.0015795 |  |  | 0.93565 | 13.4801 |  |  |  |  | 0.93565 | 13.4801 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1974-06-01 | SO2 control | Dry FGD - Spray Dryer | 2001-06-01 | PM control | Single cyclone | 1997-01-01 | PM control | Fabric Filter, pulse | 1997-01-01
coal | 2451 | San Juan | NM | Unit 3 | Unit 3 | Conventional Boiler | Wall firing - opposed firing | 544 | 5758 | 10.5846 | subbituminous | [12 empty] | 1.4709e-05 | 0.00015569 |  |  | 1.4709e-05 | 0.00015569 | 9.5979e-05 | 0.0010159 |  |  |  |  | 9.5979e-05 | 0.0010159 | 0.0001111 | 0.001176 |  |  |  |  | 0.0001111 | 0.001176 | 0.035548 | 0.37626 | [6 empty] | 0.035548 | 0.37626 | Other control | Activated carbon injection | 2008-04-01 | PM control | Fabric Filter, pulse | 2008-03-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
coal | 2451 | San Juan | NM | Unit 4 | Unit 4 | Conventional Boiler | Wall firing - opposed firing | 544 | 5649 | 10.3842 | subbituminous | [12 empty] | 2.0997e-05 | 0.00021804 |  |  | 2.0997e-05 | 0.00021804 | 0.00011782 | 0.0012235 |  |  |  |  | 0.00011782 | 0.0012235 | 0.00011285 | 0.0011718 |  |  |  |  | 0.00011285 | 0.0011718 | 0.058871 | 0.61133 | [6 empty] | 0.058871 | 0.61133 | Other control | Activated carbon injection | 2008-04-01 | PM control | Fabric Filter, pulse | 2007-10-01 | SO2 control | Wet FGD - Spray Type | 1998-04-01
coal | 50951 | Sunnyside Cogen Associates | UT | Config 1 | 1 | Fluidized bed firing | Fluidized bed firing | 60 | 700 | 11.6667 | bituminous | 0.019262 | 0.027727 | 0.01559 | 0.18189 |  |  |  |  | 0.01559 | 0.18189 |  |  | 3.7233e-06 | 4.3439e-05 |  |  | 3.7233e-06 | 4.3439e-05 | 0.016026 | 0.18697 |  |  |  |  | 0.016026 | 0.18697 | 0.00011316 | 0.0013202 |  |  |  |  | 0.00011316 | 0.0013202 |  |  | 0.18149 | 2.1173 |  |  | 0.18386 | 2.145 | 0.18149 | 2.1173 | NOx control | Other (specify): Anhydrous ammonia injection | 1993-01-01 | SO2 control | Dry FGD - Sorbent Injection | 1993-01-01 | PM control | Fabric Filter, pulse | 1993-01-01
coal | 994 | AES Petersburg | IN | 2ss | 2 | Conventional Boiler | Tangential firing | 445 | 4144 | 9.3124 | bituminous | 0.031571 | 0.0031575 | [10 empty] | 2.1131e-05 | 0.00019678 |  |  | 2.1131e-05 | 0.00019678 | 0.00016245 | 0.0015128 |  |  |  |  | 0.00016245 | 0.0015128 | 0.00011555 | 0.0010761 |  |  |  |  | 0.00011555 | 0.0010761 | 0.098233 | 0.91478 | [6 empty] | 0.098233 | 0.91478 | NOx control | Selective Catalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-12-01 | SO2 control | Wet FGD - Spray Type | 1996-12-01
coal | 995 | Bailly | IN | 7 | 7 | Conventional Boiler | Cyclone firing | 176 | 1638 | 9.3068 | bituminous | 0.13191 | 0.004914 | [10 empty] | 3.7367e-05 | 0.00034776 |  |  | 3.7367e-05 | 0.00034776 | 0.0005752 | 0.0053533 |  |  |  |  | 0.0005752 | 0.0053533 | 0.00011799 | 0.0010981 |  |  |  |  | 0.00011799 | 0.0010981 |  |  | 0.11433 | 1.064 |  |  |  |  | 0.11433 | 1.064 | NOx control | Selective Catalytic Reduction | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-06-01 | SO2 control | Wet FGD - Packed Type | 1992-06-01
coal | 995 | Bailly | IN | 8 | 8 | Conventional Boiler | Cyclone firing | 352 | 3374 | 9.5852 | bituminous | 0.13191 | 0.004914 | [10 empty] | 3.7367e-05 | 0.00035817 |  |  | 3.7367e-05 | 0.00035817 | 0.0005752 | 0.0055134 |  |  |  |  | 0.0005752 | 0.0055134 | 0.00011799 | 0.0011309 |  |  |  |  | 0.00011799 | 0.0011309 |  |  | 0.11433 | 1.0958 |  |  |  |  | 0.11433 | 1.0958 | NOx control | Selective Catalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-02-01 | SO2 control | Wet FGD - Packed Type | 1992-06-01
coal | 990 | Harding Street | IN | 70ss | 70 | Conventional Boiler | Tangential firing | 463 | 4123 | 8.905 | bituminous | [18 empty] | 0.00091 | 0.0081035 |  |  |  |  | 0.00091 | 0.0081035 | 0.00011806 | 0.0010513 |  |  |  |  | 0.00011806 | 0.0010513 |  |  | 0.24875 | 2.2151 |  |  |  |  | 0.24875 | 2.2151 | NOx control | Selective Catalytic Reduction | 2005-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-12-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
coal | 6639 | R D Green | KY | 2 | G2 | Conventional Boiler | Wall firing - opposed firing | 239 | 2726.6 | 11.4084 | bituminous, Petroleum coke | 0.041716 | 0.0049245 | [10 empty] | 1.88e-05 | 0.00021448 |  |  | 1.88e-05 | 0.00021448 | 0.00022267 | 0.0025404 |  |  |  |  | 0.00022267 | 0.0025404 | 0.00011813 | 0.0013477 |  |  |  |  | 0.00011813 | 0.0013477 | 0.080267 | 0.91571 | [6 empty] | 0.080267 | 0.91571 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-01-01 | SO2 control | Wet FGD - Spray Type | 1981-01-01
coal | 52007 | Mecklenburg Power Station | VA | Unit 1 & 2 | BLR1 | Conventional Boiler | Wall firing - front firing | 76 | 916 | 12.0526 | bituminous | 0.14715 | 0.0081241 | [10 empty] | 0.00019873 | 0.0023979 |  |  | 0.00019873 | 0.0023979 | 0.00097177 | 0.011725 |  |  |  |  | 0.00097177 | 0.011725 | 0.0001202 | 0.0014503 | 0.00012247 | 0.0014777 |  |  | 0.0001202 | 0.0014503 |  |  | 0.16626 | 2.006 |  |  |  |  | 0.16626 | 2.006 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01
coal | 52007 | Mecklenburg Power Station | VA | Unit 1 & 2 | BLR2 | Conventional Boiler | Wall firing - front firing | 76 | 918 | 12.0789 | bituminous | 0.14715 | 0.0081241 | [10 empty] | 0.00019873 | 0.0023979 |  |  | 0.00019873 | 0.0023979 | 0.00097177 | 0.011725 |  |  |  |  | 0.00097177 | 0.011725 | 0.0001202 | 0.0014503 | 0.00012247 | 0.0014777 |  |  | 0.0001202 | 0.0014503 |  |  | 0.16626 | 2.006 |  |  |  |  | 0.16626 | 2.006 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01
coal | 130 | Cross | SC | C1 | 1 | Conventional Boiler | Wall firing - opposed firing | 610 | 6502 | 10.659 | bituminous | 0.068973 | 0.0099661 | [10 empty] | 2.0667e-05 | 0.00022029 |  |  | 2.0667e-05 | 0.00022029 | 0.00024375 | 0.0025981 |  |  |  |  | 0.00024375 | 0.0025981 | 0.00012186 | 0.0012989 |  |  |  |  | 0.00012186 | 0.0012989 | [10 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-05-01 | SO2 control | Wet FGD - Spray Type | 1995-05-01
coal | 3944 | Harrison Power Station | WV | Boiler3 | 3 | Conventional Boiler | Wall firing - unspecified | 692 | 5876 | 8.4913 | bituminous | 0.015575 | 0.0065976 | [10 empty] | 7.44e-07 | 6.3175e-06 |  |  | 7.44e-07 | 6.3175e-06 | 0.00062058 | 0.0052696 |  |  |  |  | 0.00062058 | 0.0052696 | 0.00012657 | 0.0010747 |  |  |  |  | 0.00012657 | 0.0010747 |  |  | 0.20523 | 1.7427 |  |  |  |  | 0.20523 | 1.7427 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1972-12-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
coal | 728 | Yates | GA | Y1BR | Y1BR | Conventional Boiler | Tangential firing | 107 | 1094.742 | 10.2312 | bituminous | 0.037844 | 0.0072914 | [10 empty] | 0.000363 | 0.0037139 |  |  | 0.000363 | 0.0037139 | 0.00016306 | 0.0016683 |  |  |  |  | 0.00016306 | 0.0016683 | 0.00012767 | 0.0013062 |  |  |  |  | 0.00012767 | 0.0013062 | 0.0937 | 0.95867 | [6 empty] | 0.0937 | 0.95867 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Spray Type | 1992-10-01
coal | 469 | Cherokee | CO | Unit 4 | 4 | Conventional Boiler | Tangential firing | 383 | 3520 | 9.1906 | bituminous | 0.0012465 | 0.0081386 | [10 empty] | 4.0333e-06 | 3.7069e-05 |  |  | 4.0333e-06 | 3.7069e-05 | 0.00023684 | 0.0021767 |  |  |  |  | 0.00023684 | 0.0021767 | 0.00012964 | 0.0011915 |  |  |  |  | 0.00012964 | 0.0011915 | 0.12537 | 1.1522 |  |  | 0.11387 | 1.0465 |  |  | 0.11387 | 1.0465 | SO2 control | Dry FGD - Spray Dryer | 2002-10-01 | PM control | Fabric Filter, reverse air | 1989-04-01
coal | 3944 | Harrison Power Station | WV | Boiler2 | 2 | Conventional Boiler | Wall firing - unspecified | 692 | 6042 | 8.7312 | bituminous | 0.034284 | 0.009761 | [10 empty] | 0.00011833 | 0.0010332 |  |  | 0.00011833 | 0.0010332 | 0.00065681 | 0.0057348 |  |  |  |  | 0.00065681 | 0.0057348 | 0.00012983 | 0.0011336 |  |  |  |  | 0.00012983 | 0.0011336 |  |  | 0.070078 | 0.61187 |  |  |  |  | 0.070078 | 0.61187 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1973-12-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
coal | 2706 | Asheville Steam Electric Plant | NC | Ash_Cfg_2 | 2 | Conventional Boiler | Wall firing - front firing | 204 | 1902 | 9.3235 | bituminous | [22 empty] | 0.00022 | 0.0020512 | 0.00022 | 0.0020512 |  |  |  |  | 0.00013533 | 0.0012618 | 0.00013533 | 0.0012618 |  |  | 0.046388 | 0.4325 |  |  | 0.044414 | 0.41409 | 0.044414 | 0.41409 | NOx control | Selective Catalytic Reduction | 2006-06-14 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Spray/Tray Type | 2006-05-15
coal | 6139 | Welsh | TX | WE-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | 9.2401 | subbituminous | 0.0020131 | 0.0055316 | [10 empty] | 0.00022433 | 0.0020729 |  |  | 0.00022433 | 0.0020729 | 0.00019445 | 0.0017967 |  |  |  |  | 0.00019445 | 0.0017967 | 0.00013661 | 0.0012623 |  |  |  |  | 0.00013661 | 0.0012623 | 0.47975 | 4.433 | [6 empty] | 0.47975 | 4.433 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-03-01
coal | 3399 | Cumberland | TN | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 1300 | 14130 | 10.8692 | bituminous | 0.1539 | 0.007621 | [10 empty] | 6.8667e-05 | 0.00074635 |  |  | 6.8667e-05 | 0.00074635 | 0.00033471 | 0.003638 |  |  |  |  | 0.00033471 | 0.003638 | 0.00013823 | 0.0015025 |  |  |  |  | 0.00013823 | 0.0015025 |  |  | 0.20866 | 2.268 |  |  |  |  | 0.20866 | 2.268 | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Hydrated Lime for opacity | 2006-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-06-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 6076 | Colstrip | MT | Unit3 | 3 | Conventional Boiler | Tangential firing | 805 | 7573 | 9.4075 | subbituminous | 0.01049 | 0.0051552 | [10 empty] | 2.2085e-05 | 0.00020777 |  |  | 2.2085e-05 | 0.00020777 | 6.2094e-05 | 0.00058415 |  |  |  |  | 6.2094e-05 | 0.00058415 | 0.00014115 | 0.0013279 |  |  |  |  | 0.00014115 | 0.0013279 |  |  | 0.045224 | 0.42544 |  |  |  |  | 0.045224 | 0.42544 | Other control | Activated carbon injection | 2009-12-01 | SO2 control | Wet FGD - Venturi Type | 1984-01-01 | PM control | PM scrubber - Venturi | 1984-01-01
coal | 1082 | Walter Scott Jr. Energy Center | IA | 3 | 3 | Conventional Boiler | Wall firing - unspecified | 765 | 7700 | 10.0654 | [23 empty] | 0.00011 | 0.0011072 | 0.00011 | 0.0011072 |  |  |  |  | 0.000142 | 0.0014293 | 0.000142 | 0.0014293 | [10 empty] | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01
coal | 3399 | Cumberland | TN | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1300 | 14130 | 10.8692 | bituminous | 0.14679 | 0.0062029 | [10 empty] | 7.3667e-05 | 0.0008007 |  |  | 7.3667e-05 | 0.0008007 | 0.00031666 | 0.0034419 |  |  |  |  | 0.00031666 | 0.0034419 | 0.00014362 | 0.0015611 |  |  |  |  | 0.00014362 | 0.0015611 |  |  | 0.13268 | 1.4421 |  |  |  |  | 0.13268 | 1.4421 | NOx control | Selective Catalytic Reduction | 2003-05-01 | Other control | Other (specify): Hydrated Lime for Opacity | 2006-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-06-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 10771 | Hopewell | VA | 1 & 2 | 10771-01 | Conventional Boiler | Stoker - spreader | 34 | 433 | 12.7353 | bituminous | 0.10467 | 0.0035667 | [10 empty] | 0.00087433 | 0.010993 |  |  | 0.00087433 | 0.010993 | 0.00014673 | 0.001845 |  |  |  |  | 0.00014673 | 0.001845 | 0.00014608 | 0.0018367 |  |  |  |  | 0.00014608 | 0.0018367 |  |  | 0.046315 | 0.58234 |  |  |  |  | 0.046315 | 0.58234 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01
coal | 10771 | Hopewell | VA | 1 & 2 | 10771-02 | Conventional Boiler | Stoker - underfeed | 34 | 422 | 12.4118 | bituminous | 0.10467 | 0.0035667 | [10 empty] | 0.00087433 | 0.010993 |  |  | 0.00087433 | 0.010993 | 0.00014673 | 0.001845 |  |  |  |  | 0.00014673 | 0.001845 | 0.00014608 | 0.0018367 |  |  |  |  | 0.00014608 | 0.0018367 |  |  | 0.046315 | 0.58234 |  |  |  |  | 0.046315 | 0.58234 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01
coal | 1356 | Ghent | KY | GH3 | 3 | Conventional Boiler | Wall firing - opposed firing | 525 | 5868 | 11.1771 | bituminous | 0.096774 | 0.0069281 | 0.00056596 | 0.0063258 | 0.000593 | 0.006628 |  |  | 0.00056596 | 0.0063258 |  |  | 0.0009 | 0.010059 |  |  | 0.0009 | 0.010059 | 0.00052655 | 0.0058854 |  |  |  |  | 0.00052655 | 0.0058854 | 0.00014621 | 0.0016342 |  |  |  |  | 0.00014621 | 0.0016342 | 0.21783 | 2.4348 | [6 empty] | 0.21783 | 2.4348 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1981-05-01 | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
coal | 6064 | Nearman Creek | KS | N1 | N1 | Conventional Boiler | Wall firing - front firing | 257.4 | 2433 | 9.4522 | [7 empty] | 3e-05 | 0.00028357 | 3e-05 | 0.00028357 | [12 empty] | 0.00041 | 0.0038754 | 0.00041 | 0.0038754 |  |  |  |  | 0.00014667 | 0.0013863 | 0.00014667 | 0.0013863 | [10 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1988-01-01
coal | 469 | Cherokee | CO | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 165 | 1877 | 11.3758 | bituminous | 0.00089616 | 0.0084623 | [10 empty] | 1.9067e-05 | 0.0002169 |  |  | 1.9067e-05 | 0.0002169 | 0.0003054 | 0.0034742 |  |  |  |  | 0.0003054 | 0.0034742 | 0.00014827 | 0.0016867 |  |  |  |  | 0.00014827 | 0.0016867 | 0.1291 | 1.4686 |  |  | 0.11097 | 1.2624 |  |  | 0.11097 | 1.2624 | SO2 control | Dry FGD - Spray Dryer | 2002-06-01 | PM control | Fabric Filter, reverse air | 1988-02-01
coal | 10774 | Southampton Power Station | VA | Unit 1 & 2 | 1 | Conventional Boiler | Stoker - spreader | 34 | 442 | 13 | bituminous | 0.10138 | 0.0053007 | [10 empty] | 0.0039549 | 0.051704 |  |  | 0.0039549 | 0.051704 | 0.00015527 | 0.0020299 |  |  |  |  | 0.00015527 | 0.0020299 | 0.00014995 | 0.0019604 |  |  |  |  | 0.00014995 | 0.0019604 |  |  | 0.05739 | 0.75029 |  |  |  |  | 0.05739 | 0.75029 | PM control | Multiple cyclone | 1992-03-01 | PM control | Multiple cyclone | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01
coal | 10774 | Southampton Power Station | VA | Unit 1 & 2 | 2 | Conventional Boiler | Stoker - spreader | 34 | 447 | 13.1471 | bituminous | 0.10138 | 0.0053007 | [10 empty] | 0.0039549 | 0.051704 |  |  | 0.0039549 | 0.051704 | 0.00015527 | 0.0020299 |  |  |  |  | 0.00015527 | 0.0020299 | 0.00014995 | 0.0019604 |  |  |  |  | 0.00014995 | 0.0019604 |  |  | 0.05739 | 0.75029 |  |  |  |  | 0.05739 | 0.75029 | PM control | Multiple cyclone | 1992-03-01 | PM control | Multiple cyclone | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01
coal | 6096 | Nebraska City | NE | NC2 | NC2 | Conventional Boiler | Wall firing - front firing | 682 | 6920.254 | 10.147 | bituminous |  | 0.0036238 | [10 empty] | 0.0008075 | 0.0081937 |  |  | 0.0008075 | 0.0081937 | 0.0002764 | 0.0028046 |  |  |  |  | 0.0002764 | 0.0028046 | 0.00015207 | 0.0015431 |  |  |  |  | 0.00015207 | 0.0015431 | 0.092367 | 0.93724 | [6 empty] | 0.092367 | 0.93724 | NOx control | Selective Catalytic Reduction | 2009-05-01 | Other control | Activated carbon injection | 2009-05-01 | SO2 control | Dry FGD - Spray Dryer | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01
coal | 6019 | W H Zimmer | OH | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1408 | 12656 | 8.9886 | bituminous, bituminous, bituminous | 0.087771 | 0.0066769 | [10 empty] | 2.18e-05 | 0.00019595 |  |  | 2.18e-05 | 0.00019595 | 0.00087784 | 0.0078906 |  |  |  |  | 0.00087784 | 0.0078906 | 0.00015864 | 0.001426 |  |  |  |  | 0.00015864 | 0.001426 |  |  | 0.4049 | 3.6395 |  |  |  |  | 0.4049 | 3.6395 | Other control | Other (specify): Magnesium Hydroxide Injection |  | NOx control | Selective Catalytic Reduction | 2004-01-01 | Other control | Dry sorbent injection | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-03-01 | SO2 control | Wet FGD - Spray Type | 2004-06-01
coal | 1356 | Ghent | KY | GH4 | 4 | Conventional Boiler | Wall firing - opposed firing | 525 | 5967 | 11.3657 | bituminous | 0.12564 | 0.0061154 | 0.00059134 | 0.006721 | 0.00060033 | 0.0068232 |  |  | 0.00059134 | 0.006721 |  |  | 0.00093333 | 0.010608 |  |  | 0.00093333 | 0.010608 | 0.00069665 | 0.0079179 |  |  |  |  | 0.00069665 | 0.0079179 | 0.0001689 | 0.0019196 |  |  |  |  | 0.0001689 | 0.0019196 | 0.0991 | 1.1263 | [6 empty] | 0.0991 | 1.1263 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1984-06-01 | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | SO2 control | Wet FGD - Spray Type | 2008-06-01
coal | 994 | AES Petersburg | IN | 1s | 1 | Conventional Boiler | Tangential firing | 255 | 2200 | 8.6275 | bituminous | 0.018921 | 0.0033041 | [10 empty] | 2.9085e-05 | 0.00025093 |  |  | 2.9085e-05 | 0.00025093 | 0.00017578 | 0.0015165 |  |  |  |  | 0.00017578 | 0.0015165 | 0.00016914 | 0.0014592 |  |  |  |  | 0.00016914 | 0.0014592 | 0.047471 | 0.40955 | [6 empty] | 0.047471 | 0.40955 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1967-12-01 | SO2 control | Wet FGD - Spray Type | 1996-12-01
coal | 508 | Lamar Plant | CO | 001 | 4 | Fluidized bed firing | Fluidized bed firing | 44 | 180 | 4.0909 | [23 empty] | 0.00047688 | 0.0019509 | 0.00047688 | 0.0019509 |  |  |  |  | 0.0001694 | 0.00069298 | 0.0001694 | 0.00069298 | [10 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified | 2009-05-01
coal | 7213 | Clover | VA | Unit 1 | 1 | Conventional Boiler | Tangential firing | 431 | 4923 | 11.4223 | bituminous | 0.12876 | 0.0043059 | [10 empty] | 0.00035767 | 0.0040854 |  |  | 0.00035767 | 0.0040854 | 0.00037307 | 0.0042613 |  |  |  |  | 0.00037307 | 0.0042613 | 0.00017153 | 0.0019593 |  |  |  |  | 0.00017153 | 0.0019593 |  |  | 0.043842 | 0.50077 |  |  |  |  | 0.043842 | 0.50077 | PM control | Fabric Filter, reverse air | 2003-05-01 | SO2 control | Wet FGD - Spray Type | 2003-05-01
coal | 2727 | Marshall | NC | U4 | Unit 4 | Conventional Boiler | Tangential firing | 700 | 6029.8 | 8.614 | bituminous | 0.073535 | 0.0088441 |  |  | 0.00017333 | 0.0014931 |  |  | 0.00017333 | 0.0014931 |  |  | 1.995e-05 | 0.00017185 |  |  | 1.995e-05 | 0.00017185 | 0.00028343 | 0.0024415 |  |  | 7.5417e-05 | 0.00064964 | 7.5417e-05 | 0.00064964 | 0.00017169 | 0.0014789 |  |  | 5.71e-06 | 4.9186e-05 | 0.00017169 | 0.0014789 |  |  | 0.094491 | 0.81395 |  |  |  |  | 0.094491 | 0.81395 | NOx control | Selective Noncatalytic Reduction | 2006-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2006-05-01 | SO2 control | Wet FGD - Spray Type | 2006-10-01
coal | 2727 | Marshall | NC | U3 | Unit 3 | Conventional Boiler | Tangential firing | 700 | 6103.1 | 8.7187 | bituminous | 0.095399 | 0.0065798 |  |  | 0.00016667 | 0.0014531 |  |  | 0.00016667 | 0.0014531 |  |  | 2.3867e-05 | 0.00020809 |  |  | 2.3867e-05 | 0.00020809 | 0.00032635 | 0.0028454 |  |  |  |  | 0.00032635 | 0.0028454 | 0.00017206 | 0.0015002 |  |  |  |  | 0.00017206 | 0.0015002 |  |  | 0.13037 | 1.1367 |  |  |  |  | 0.13037 | 1.1367 | NOx control | Selective Catalytic Reduction | 2008-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2006-12-01 | SO2 control | Wet FGD - Spray Type | 2007-03-01
coal | 6018 | East Bend Station | KY | 2 | 2 | Conventional Boiler | Wall firing - front firing | 650.7246 | 6313 | 9.7015 | bituminous | 0.084793 | 0.0061393 |  |  | 0.00018 | 0.0017463 |  |  | 0.00018 | 0.0017463 |  |  | 2.6033e-05 | 0.00025256 |  |  | 2.6033e-05 | 0.00025256 | 0.00052846 | 0.0051268 |  |  |  |  | 0.00052846 | 0.0051268 | 0.00017505 | 0.0016983 |  |  |  |  | 0.00017505 | 0.0016983 |  |  | 0.060856 | 0.59039 |  |  |  |  | 0.060856 | 0.59039 | Other control | Dry sorbent injection | 2005-01-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1981-01-01 | NOx control | Selective Catalytic Reduction | 2002-01-01 | SO2 control | Wet FGD - Spray Type | 1981-01-01
coal | 2727 | Marshall | NC | U12007 | Unit 1 | Conventional Boiler | Tangential firing | 400 | 3658.2 | 9.1455 | bituminous | 0.073401 | 0.0070391 |  |  | 0.00017667 | 0.0016157 |  |  | 0.00017667 | 0.0016157 |  |  | 5.3933e-05 | 0.00049325 |  |  | 5.3933e-05 | 0.00049325 | 0.0002859 | 0.0026147 |  |  |  |  | 0.0002859 | 0.0026147 | 0.00017508 | 0.0016012 |  |  |  |  | 0.00017508 | 0.0016012 |  |  | 0.082924 | 0.75838 |  |  |  |  | 0.082924 | 0.75838 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-12-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
coal | 2727 | Marshall | NC | U22007 | Unit 2 | Conventional Boiler | Tangential firing | 400 | 3663.2 | 9.158 | bituminous | 0.073401 | 0.0070391 |  |  | 0.00017667 | 0.0016179 |  |  | 0.00017667 | 0.0016179 |  |  | 5.3933e-05 | 0.00049392 |  |  | 5.3933e-05 | 0.00049392 | 0.0002859 | 0.0026183 |  |  |  |  | 0.0002859 | 0.0026183 | 0.00017508 | 0.0016034 |  |  |  |  | 0.00017508 | 0.0016034 |  |  | 0.082924 | 0.75941 |  |  |  |  | 0.082924 | 0.75941 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2002-01-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
coal | 3295 | Urquhart | SC | URQ003 | URQ3 | Conventional Boiler | Tangential firing | 103 | 1048 | 10.1748 | bituminous | 0.014292 | 0.011768 | [10 empty] | 7.79e-06 | 7.9261e-05 |  |  | 7.79e-06 | 7.9261e-05 |  |  | 0.000639 | 0.0065017 |  |  | 0.000639 | 0.0065017 |  |  | 0.00017833 | 0.0018145 |  |  | 0.00017833 | 0.0018145 | [10 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1969-11-01
coal | 7213 | Clover | VA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 434 | 5041 | 11.6152 | bituminous | 0.073712 | 0.0042885 | [10 empty] | 0.0012983 | 0.01508 |  |  | 0.0012983 | 0.01508 | 0.00033766 | 0.0039219 |  |  |  |  | 0.00033766 | 0.0039219 | 0.00018542 | 0.0021537 |  |  |  |  | 0.00018542 | 0.0021537 |  |  | 0.079175 | 0.91963 |  |  |  |  | 0.079175 | 0.91963 | NOx control | Selective Noncatalytic Reduction | 2003-03-01 | PM control | Fabric Filter, reverse air | 2003-05-01 | SO2 control | Wet FGD - Spray Type | 2003-05-01
coal | 6664 | Louisa | IA | 101 | 101 | Conventional Boiler | Wall firing - unspecified | 805 | 8624 | 10.713 | subbituminous | 0.00067397 | 0.003016 | [10 empty] | 1.03e-05 | 0.00011034 |  |  | 1.03e-05 | 0.00011034 | 0.00019104 | 0.0020466 |  |  |  |  | 0.00019104 | 0.0020466 | 0.00019223 | 0.0020594 |  |  |  |  | 0.00019223 | 0.0020594 | 0.2683 | 2.8743 | [6 empty] | 0.2683 | 2.8743 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-12-01 | PM control | Fabric Filter, pulse | 2007-12-01
coal | 1382 | HMP&L Station Two Henderson | KY | 2 | H2 | Conventional Boiler | Wall firing - rear firing | 173.1 | 1866.2 | 10.7811 | bituminous | 0.14041 | 0.0069788 | [10 empty] | 2.03e-05 | 0.00021886 |  |  | 2.03e-05 | 0.00021886 | 0.00030516 | 0.00329 |  |  |  |  | 0.00030516 | 0.00329 | 0.00019495 | 0.0021018 |  |  |  |  | 0.00019495 | 0.0021018 | 0.2149 | 2.3168 | [6 empty] | 0.2149 | 2.3168 | NOx control | Selective Catalytic Reduction | 2004-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-04-01 | SO2 control | Wet FGD - Tray Type | 1995-06-01
coal | 2080 | Montrose | MO | 2 | 2 | Conventional Boiler | Tangential firing | 188 | 2130 | 11.3298 | coal - subbituminous | [22 empty] | 0.0003 | 0.0033989 | 0.0003 | 0.0033989 |  |  |  |  | 0.0002 | 0.002266 | 0.0002 | 0.002266 | [10 empty] | Other control | Other (specify): SO3 injection for Opacity control. | 1993-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-03-01
coal | 2080 | Montrose | MO | 3 | 3 | Conventional Boiler | Tangential firing | 188 | 2250 | 11.9681 | coal - subbituminous | [22 empty] | 0.0003 | 0.0035904 | 0.0003 | 0.0035904 |  |  |  |  | 0.0002 | 0.0023936 | 0.0002 | 0.0023936 | [10 empty] | Other control | Other (specify): SO3 injection for opacity control. | 1993-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1964-03-01
coal | 6264 | Mountaineer | WV | Mt-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11960 | 9.0606 | bituminous | 0.069485 | 0.005416 | [10 empty] | 0.000237 | 0.0021474 |  |  | 0.000237 | 0.0021474 | 0.00021405 | 0.0019394 |  |  |  |  | 0.00021405 | 0.0019394 | 0.00020348 | 0.0018437 |  |  |  |  | 0.00020348 | 0.0018437 | 0.0314 | 0.2845 | [6 empty] | 0.0314 | 0.2845 | NOx control | Selective Catalytic Reduction | 2002-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-09-01 | SO2 control | Wet FGD - Spray Type | 2007-01-01
coal | 3161 | Eddystone Generating Station | PA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 339 | 2808 | 8.2832 | bituminous | 0.048809 | 0.0036145 | [10 empty] | 0.0017493 | 0.01449 |  |  | 0.0017493 | 0.01449 | 0.00060871 | 0.0050421 |  |  |  |  | 0.00060871 | 0.0050421 | 0.00020418 | 0.0016912 |  |  |  |  | 0.00020418 | 0.0016912 | 0.3802 | 3.1493 | [6 empty] | 0.3802 | 3.1493 | NOx control | Selective Noncatalytic Reduction | 2003-06-01 | PM control | Multiple cyclone | 1960-11-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1960-11-01 | PM control | PM scrubber - Venturi | 1982-12-01 | SO2 control | Wet FGD - Spray Type | 1982-12-01
coal | 568 | Bridgeport Station | CT | BHSEMU3OS2-Coal | BHB3 | Conventional Boiler | Tangential firing | 403 | 4100 | 10.1737 | subbituminous | 0.0081435 | 0.00081435 | [10 empty] | 3.9033e-05 | 0.00039711 |  |  | 3.9033e-05 | 0.00039711 | 0.0018993 | 0.019323 |  |  |  |  | 0.0018993 | 0.019323 | 0.00021086 | 0.0021453 |  |  |  |  | 0.00021086 | 0.0021453 |  |  | 0.18066 | 1.8379 |  |  |  |  | 0.18066 | 1.8379 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-08-01 | Other control | Activated carbon injection | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-01-01
coal | 10143 | Colver Power Project | PA | AAB01 | AAB01 | Fluidized bed firing | Fluidized bed firing | 131 | 1204 | 9.1908 | coal refuse (culm or gob) | 0.059321 | 0.013047 | [10 empty] | 0.00029367 | 0.002699 |  |  | 0.00029367 | 0.002699 | 0.032027 | 0.29435 | 0.032033 | 0.29441 |  |  | 0.032027 | 0.29435 | 0.00022607 | 0.0020778 | 0.000226 | 0.0020771 |  |  | 0.000226 | 0.0020771 |  |  | 0.59697 | 5.4867 |  |  |  |  | 0.59697 | 5.4867 | NOx control | Selective Noncatalytic Reduction | 1995-05-01 | PM control | Fabric Filter, pulse | 1995-05-01
coal | 2451 | San Juan | NM | Unit 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 370 | 3707 | 10.0189 | subbituminous | [12 empty] | 0.00025289 | 0.0025337 |  |  | 0.00025289 | 0.0025337 | 0.00011135 | 0.0011156 |  |  |  |  | 0.00011135 | 0.0011156 | 0.00022659 | 0.0022701 |  |  |  |  | 0.00022659 | 0.0022701 | 0.065474 | 0.65598 | [6 empty] | 0.065474 | 0.65598 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, pulse | 2008-10-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
coal | 2451 | San Juan | NM | Unit 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 370 | 3688 | 9.9676 | subbituminous | [12 empty] | 2.2185e-05 | 0.00022113 |  |  | 2.2185e-05 | 0.00022113 | 0.00012406 | 0.0012366 |  |  |  |  | 0.00012406 | 0.0012366 | 0.00025217 | 0.0025135 |  |  |  |  | 0.00025217 | 0.0025135 | 0.083286 | 0.83016 | [6 empty] | 0.083286 | 0.83016 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, pulse | 2009-04-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
coal | 628 | Crystal River Power Plant | FL | CryR_Cfg_5c | 5 | Conventional Boiler | Wall firing - opposed firing | 767 | 7423 | 9.678 | bituminous | 0.071422 | 0.004342 | [10 empty] | 3.76e-05 | 0.00036389 |  |  | 3.76e-05 | 0.00036389 | 0.00027384 | 0.0026503 |  |  |  |  | 0.00027384 | 0.0026503 | 0.00025606 | 0.0024781 |  |  |  |  | 0.00025606 | 0.0024781 |  |  | 0.065224 | 0.63124 |  |  |  |  | 0.065224 | 0.63124 | NOx control | Selective Catalytic Reduction | 2009-05-15 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-01-01 | SO2 control | Wet FGD - Spray/Tray Type | 2009-11-30
coal | 60 | Whelan Energy Center Unit 1 (WEC1) | NE | 1 | 1 | Conventional Boiler | Tangential firing | 83.6 | 845.1 | 10.1089 | subbituminous | [12 empty] | 0.00433 | 0.043771 |  |  | 0.00433 | 0.043771 | 0.0001624 | 0.0016417 |  |  |  |  | 0.0001624 | 0.0016417 | 0.00026261 | 0.0026546 |  |  |  |  | 0.00026261 | 0.0026546 |  |  | 0.70876 | 7.1648 |  |  |  |  | 0.70876 | 7.1648 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
coal | 1382 | HMP&L Station Two Henderson | KY | 1 | H1 | Conventional Boiler | Wall firing - rear firing | 166.1 | 1799 | 10.8308 | bituminous | 0.10266 | 0.0073432 | [10 empty] | 2.2033e-05 | 0.00023864 |  |  | 2.2033e-05 | 0.00023864 | 0.00025197 | 0.002729 |  |  |  |  | 0.00025197 | 0.002729 | 0.0002677 | 0.0028994 |  |  |  |  | 0.0002677 | 0.0028994 | 0.17537 | 1.8994 | [6 empty] | 0.17537 | 1.8994 | NOx control | Selective Catalytic Reduction | 2003-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-06-01 | SO2 control | Wet FGD - Tray Type | 1995-06-01
coal | 54081 | Spruance Genco, LLC | VA | GEN4 | 4A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.085854 | 0.0050534 | [10 empty] | 2.5249e-05 | 0.00032991 |  |  | 2.5249e-05 | 0.00032991 | 7.6841e-05 | 0.001004 |  |  |  |  | 7.6841e-05 | 0.001004 | 0.00030017 | 0.0039221 |  |  |  |  | 0.00030017 | 0.0039221 | 0.0423 | 0.5527 | 0.18821 | 2.4592 |  |  | 0.089953 | 1.1754 | 0.0423 | 0.5527 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 54081 | Spruance Genco, LLC | VA | GEN4 | 4B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.085854 | 0.0050534 | [10 empty] | 2.5249e-05 | 0.00032991 |  |  | 2.5249e-05 | 0.00032991 | 7.6841e-05 | 0.001004 |  |  |  |  | 7.6841e-05 | 0.001004 | 0.00030017 | 0.0039221 |  |  |  |  | 0.00030017 | 0.0039221 | 0.0423 | 0.5527 | 0.18821 | 2.4592 |  |  | 0.089953 | 1.1754 | 0.0423 | 0.5527 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 3149 | PPL Montour | PA | U1 | 1 | Conventional Boiler | Tangential firing | 797 | 7239 | 9.0828 | bituminous | 0.070132 | [11 empty] | 7.9167e-05 | 0.00071906 |  |  | 7.9167e-05 | 0.00071906 | 0.0003015 | 0.0027385 |  |  |  |  | 0.0003015 | 0.0027385 | 0.0003015 | 0.0027385 |  |  |  |  | 0.0003015 | 0.0027385 |  |  | 0.45804 | 4.1603 |  |  |  |  | 0.45804 | 4.1603 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2001-05-01 | NOx control | Selective Catalytic Reduction | 2001-05-01 | SO2 control | Wet FGD - Tray Type | 2008-05-01
coal | 54081 | Spruance Genco, LLC | VA | GEN2 | 2A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.085779 | 0.005917 | [10 empty] | 2.8317e-06 | 3.7e-05 |  |  | 2.8317e-06 | 3.7e-05 | 3.3866e-05 | 0.0004425 |  |  |  |  | 3.3866e-05 | 0.0004425 | 0.00030625 | 0.0040015 |  |  |  |  | 0.00030625 | 0.0040015 | 0.0241 | 0.3149 | 0.13135 | 1.7163 |  |  |  |  | 0.0241 | 0.3149 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 54081 | Spruance Genco, LLC | VA | GEN2 | 2B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | 0.085779 | 0.005917 | [10 empty] | 2.8317e-06 | 3.7e-05 |  |  | 2.8317e-06 | 3.7e-05 | 3.3866e-05 | 0.0004425 |  |  |  |  | 3.3866e-05 | 0.0004425 | 0.00030625 | 0.0040015 |  |  |  |  | 0.00030625 | 0.0040015 | 0.0241 | 0.3149 | 0.13135 | 1.7163 |  |  |  |  | 0.0241 | 0.3149 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
coal | 3122 | Homer City Station | PA | HC3CONFIG | 3 | Conventional Boiler | Wall firing - opposed firing | 680 | 6175 | 9.0809 | bituminous | 0.11845 | 0.0057936 | [10 empty] | 5.6633e-05 | 0.00051428 |  |  | 5.6633e-05 | 0.00051428 | 0.00040608 | 0.0036876 |  |  |  |  | 0.00040608 | 0.0036876 | 0.00033333 | 0.0030269 |  |  |  |  | 0.00033333 | 0.0030269 | 0.22583 | 2.0508 | [6 empty] | 0.22583 | 2.0508 | NOx control | Selective Catalytic Reduction | 2001-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1977-12-01 | SO2 control | Wet FGD - Spray Type | 2001-09-01
coal | 3149 | PPL Montour | PA | U2 | 2 | Conventional Boiler | Tangential firing | 792 | 7239 | 9.1402 | bituminous | 0.0814 | [11 empty] | 7.64e-05 | 0.00069831 |  |  | 7.64e-05 | 0.00069831 | 0.00035654 | 0.0032588 |  |  |  |  | 0.00035654 | 0.0032588 | 0.00035654 | 0.0032588 |  |  |  |  | 0.00035654 | 0.0032588 |  |  | 0.27722 | 2.5338 |  |  |  |  | 0.27722 | 2.5338 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-05-01 | NOx control | Selective Catalytic Reduction | 2000-05-01 | SO2 control | Wet FGD - Tray Type | 2008-03-01
coal | 8219 | Ray D Nixon | CO | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 225 | 2095 | 9.3111 | subbituminous | [22 empty] | 0.0005845 | 0.0054423 | 0.0005845 | 0.0054423 |  |  |  |  | 0.00036333 | 0.003383 | 0.00036333 | 0.003383 | [6 empty] | 0.39067 | 3.6375 | 0.39067 | 3.6375 | PM control | Fabric Filter, reverse air | 1980-04-01
coal | 1943 | Hoot Lake | MN | 2 | 002 | Conventional Boiler | Tangential firing | 60.7 | 747.2 | 12.3097 | subbituminous | 0.0022412 | 0.0037562 | [10 empty] | 0.00066676 | 0.0082077 |  |  | 0.00066676 | 0.0082077 | 0.00068829 | 0.0084727 |  |  |  |  | 0.00068829 | 0.0084727 | 0.00036715 | 0.0045195 |  |  |  |  | 0.00036715 | 0.0045195 | 0.57277 | 7.0506 | [6 empty] | 0.57277 | 7.0506 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-06-01
coal | 7504 | Neil Simpson II | WY | NS2Cfg | 2 | Conventional Boiler | Wall firing - front firing | 88 | 1100 | 12.5 | subbituminous | 0.00078445 | 0.0054912 | [10 empty] | 5e-05 | 0.000625 |  |  | 5e-05 | 0.000625 | 0.0001475 | 0.0018437 | 0.00014767 | 0.0018458 |  |  | 0.0001475 | 0.0018437 | 0.00036953 | 0.0046191 | 0.00036967 | 0.0046208 |  |  | 0.00036953 | 0.0046191 | 0.0921 | 1.1513 | [6 empty] | 0.0921 | 1.1513 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1995-09-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-09-01
coal | 55479 | Wygen 1 | WY | WYG1Cfg | 3 | Conventional Boiler | Wall firing - front firing | 91 | 1053 | 11.5714 | subbituminous | 0.00085128 | 0.0081723 | [10 empty] | 4.55e-05 | 0.0005265 |  |  | 4.55e-05 | 0.0005265 | 0.00015658 | 0.0018119 | 0.0001535 | 0.0017762 |  |  | 0.0001535 | 0.0017762 | 0.00039128 | 0.0045277 | 0.000384 | 0.0044434 |  |  | 0.000384 | 0.0044434 | 0.12767 | 1.4773 | [6 empty] | 0.12767 | 1.4773 | NOx control | Selective Catalytic Reduction | 2003-04-01 | SO2 control | Dry FGD - Spray Dryer | 2003-04-01 | PM control | Fabric Filter, pulse | 2003-04-01
coal | 2080 | Montrose | MO | 1 | 1 | Conventional Boiler | Tangential firing | 188 | 2140 | 11.383 | coal - subbituminous | [22 empty] | 0.0003 | 0.0034149 | 0.0003 | 0.0034149 |  |  |  |  | 0.0004 | 0.0045532 | 0.0004 | 0.0045532 | [10 empty] | Other control | Other (specify): SO3 injection for Opacity control. | 1993-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1958-06-01
coal | 56319 | Wygen 2 | WY | WYG2Cfg | 0001 | Conventional Boiler | Wall firing - front firing | 96 | 1300 | 13.5417 | subbituminous | 0.00084991 | 0.0018188 | [10 empty] | 8.72e-05 | 0.0011808 |  |  | 8.72e-05 | 0.0011808 | 0.0004 | 0.0054167 | 0.00039233 | 0.0053128 |  |  | 0.00039233 | 0.0053128 | 0.0004 | 0.0054167 | 0.00040867 | 0.005534 |  |  | 0.0004 | 0.0054167 | 0.048 | 0.65 | [6 empty] | 0.048 | 0.65 | NOx control | Selective Catalytic Reduction | 2008-01-01 | SO2 control | Dry FGD - Spray Dryer | 2008-01-01 | PM control | Fabric Filter, pulse | 2008-01-01
coal | 1241 | La Cygne | KS | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 685 | 7700 | 11.2409 | subbituminous | 0.001474 | 0.005312 | [10 empty] | 4.1067e-05 | 0.00046163 |  |  | 4.1067e-05 | 0.00046163 | 0.00073104 | 0.0082176 |  |  | 0.0009 | 0.010117 | 0.00073104 | 0.0082176 | 0.00079747 | 0.0089642 |  |  | 0.00040244 | 0.0045238 | 0.00040244 | 0.0045238 |  |  | 0.68768 | 7.7301 |  |  |  |  | 0.68768 | 7.7301 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
coal | 10671 | AES Shady Point,LLC | OK | Unit 1 | 1A | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | 0.0084538 | 0.0060328 | [10 empty] | 0.0019035 | 0.026422 |  |  | 0.0019035 | 0.026422 | 0.00653 | 0.090639 |  |  |  |  | 0.00653 | 0.090639 | 0.00040693 | 0.0056483 |  |  |  |  | 0.00040693 | 0.0056483 | 0.34833 | 4.835 | [6 empty] | 0.34833 | 4.835 | PM control | Fabric Filter, pulse | 1991-01-01
coal | 10671 | AES Shady Point,LLC | OK | Unit 1 | 1b | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | 0.0084538 | 0.0060328 | [10 empty] | 0.0019035 | 0.026422 |  |  | 0.0019035 | 0.026422 | 0.00653 | 0.090639 |  |  |  |  | 0.00653 | 0.090639 | 0.00040693 | 0.0056483 |  |  |  |  | 0.00040693 | 0.0056483 | 0.34833 | 4.835 | [6 empty] | 0.34833 | 4.835 | PM control | Fabric Filter, pulse | 1991-01-01
coal | 10671 | AES Shady Point,LLC | OK | Unit 2 | 2a | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | 0.0084538 | 0.0060328 | [10 empty] | 0.0019035 | 0.026422 |  |  | 0.0019035 | 0.026422 | 0.00653 | 0.090639 |  |  |  |  | 0.00653 | 0.090639 | 0.00040693 | 0.0056483 |  |  |  |  | 0.00040693 | 0.0056483 | 0.34833 | 4.835 | [6 empty] | 0.34833 | 4.835 | PM control | Fabric Filter, pulse | 1991-01-01
coal | 10671 | AES Shady Point,LLC | OK | Unit 2 | 2b | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | 0.0084538 | 0.0060328 | [10 empty] | 0.0019035 | 0.026422 |  |  | 0.0019035 | 0.026422 | 0.00653 | 0.090639 |  |  |  |  | 0.00653 | 0.090639 | 0.00040693 | 0.0056483 |  |  |  |  | 0.00040693 | 0.0056483 | 0.34833 | 4.835 | [6 empty] | 0.34833 | 4.835 | PM control | Fabric Filter, pulse | 1991-01-01
coal | 3140 | PPL Brunner Island | PA | U2 | 2 | Conventional Boiler | Tangential firing | 393 | 3790 | 9.6438 | bituminous | 0.077108 | [11 empty] | 6.9167e-05 | 0.00066703 |  |  | 6.9167e-05 | 0.00066703 | 0.00039814 | 0.0038395 |  |  |  |  | 0.00039814 | 0.0038395 | 0.00040754 | 0.0039302 |  |  |  |  | 0.00040754 | 0.0039302 |  |  | 0.40277 | 3.8842 |  |  |  |  | 0.40277 | 3.8842 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2009-10-01 | SO2 control | Wet FGD - Tray Type | 2009-11-01
coal | 3140 | PPL Brunner Island | PA | U1 | 1 | Conventional Boiler | Tangential firing | 330 | 3345 | 10.1364 | bituminous | 0.077108 | [11 empty] | 6.9167e-05 | 0.0007011 |  |  | 6.9167e-05 | 0.0007011 | 0.00039814 | 0.0040357 |  |  |  |  | 0.00039814 | 0.0040357 | 0.00040754 | 0.0041309 |  |  |  |  | 0.00040754 | 0.0041309 |  |  | 0.40277 | 4.0826 |  |  |  |  | 0.40277 | 4.0826 | PM control | Fabric Filter, pulse | 1965-01-01 | SO2 control | Wet FGD - Tray Type | 2009-11-01
coal | 883 | Waukegan | IL | WK8CONFIG | 8 | Conventional Boiler | Tangential firing | 383 | 3960.892 | 10.3418 | subbituminous | 0.00083517 | 0.0038684 | [10 empty] | 0.00018 | 0.0018615 |  |  | 0.00018 | 0.0018615 | 0.00094097 | 0.0097312 |  |  |  |  | 0.00094097 | 0.0097312 | 0.00041367 | 0.0042781 |  |  |  |  | 0.00041367 | 0.0042781 | 0.5669 | 5.8627 | [6 empty] | 0.5669 | 5.8627 | Other control | Activated carbon injection | 2008-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1962-07-01
coal | 2718 | G G Allen | NC | 2-2009 | ES-2 | Conventional Boiler | Tangential firing | 177 | 1509 | 8.5254 | bituminous | 0.080202 | 0.0070922 | [10 empty] | 6.376e-06 | 5.4358e-05 |  |  | 6.376e-06 | 5.4358e-05 | 0.0011427 | 0.0097422 |  |  |  |  | 0.0011427 | 0.0097422 | 0.00041785 | 0.0035624 |  |  |  |  | 0.00041785 | 0.0035624 |  |  | 0.11925 | 1.0166 |  |  |  |  | 0.11925 | 1.0166 | NOx control | Selective Noncatalytic Reduction | 2007-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1988-10-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
coal | 2718 | G G Allen | NC | 5-2009 | ES-5 | Conventional Boiler | Tangential firing | 285.3 | 2705 | 9.4812 | bituminous | 0.080202 | 0.0070922 | [10 empty] | 6.376e-06 | 6.0452e-05 |  |  | 6.376e-06 | 6.0452e-05 | 0.0011427 | 0.010834 |  |  |  |  | 0.0011427 | 0.010834 | 0.00041785 | 0.0039617 |  |  |  |  | 0.00041785 | 0.0039617 |  |  | 0.11925 | 1.1306 |  |  |  |  | 0.11925 | 1.1306 | NOx control | Selective Noncatalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2000-06-01 | SO2 control | Wet FGD - Spray Type | 2009-03-01
coal | 2718 | G G Allen | NC | 1-2009 | ES-1 | Conventional Boiler | Tangential firing | 176.2 | 1738 | 9.8638 | bituminous | 0.080202 | 0.0070922 | [10 empty] | 6.376e-06 | 6.2892e-05 |  |  | 6.376e-06 | 6.2892e-05 | 0.0011427 | 0.011272 |  |  |  |  | 0.0011427 | 0.011272 | 0.00041785 | 0.0041216 |  |  |  |  | 0.00041785 | 0.0041216 |  |  | 0.11925 | 1.1762 |  |  |  |  | 0.11925 | 1.1762 | NOx control | Selective Noncatalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1988-10-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
coal | 3788 | Potomac River | VA | 1 | 1 | Conventional Boiler | Tangential firing | 93 | 970 | 10.4301 | coal - bituminous | [22 empty] | 0.00181 | 0.018878 | 0.00181 | 0.018878 |  |  |  |  | 0.000436 | 0.0045475 | 0.000436 | 0.0045475 | [10 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1949-10-01
coal | 1374 | Elmer Smith Station | KY | Unit001 | 1374 | Conventional Boiler | Cyclone firing | 153 | 1370 | 8.9542 | bituminous, petroleum coke | 0.0083227 | 0.0069574 |  |  | 0.00128 | 0.010617 |  |  | 0.00128 | 0.010617 |  |  | 2.1e-05 | 0.00017419 |  |  | 2.1e-05 | 0.00017419 | 0.0026737 | 0.022178 |  |  |  |  | 0.0026737 | 0.022178 | 0.00044245 | 0.00367 |  |  |  |  | 0.00044245 | 0.00367 | 0.67907 | 5.6327 | [6 empty] | 0.67907 | 5.6327 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 1374 | Elmer Smith Station | KY | Unit001 | 1374-2 | Conventional Boiler | Tangential firing | 291.5 | 2317 | 7.9485 | bituminous, petroleum coke | 0.0083227 | 0.0069574 |  |  | 0.00128 | 0.010617 |  |  | 0.00128 | 0.010617 |  |  | 2.1e-05 | 0.00017419 |  |  | 2.1e-05 | 0.00017419 | 0.0026737 | 0.022178 |  |  |  |  | 0.0026737 | 0.022178 | 0.00044245 | 0.00367 |  |  |  |  | 0.00044245 | 0.00367 | 0.67907 | 5.6327 | [6 empty] | 0.67907 | 5.6327 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 874 | Joliet 9 | IL | JOL5 CONFIG | 5 | Conventional Boiler | Cyclone firing | 326 | 3572.378 | 10.9582 | subbituminous | 0.0011961 | 0.005813 | [10 empty] | 0.00021667 | 0.0023743 |  |  | 0.00021667 | 0.0023743 | 0.00054129 | 0.0059316 |  |  |  |  | 0.00054129 | 0.0059316 | 0.00047383 | 0.0051923 |  |  |  |  | 0.00047383 | 0.0051923 | 0.4335 | 4.7504 | [6 empty] | 0.4335 | 4.7504 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-03-01
coal | 2718 | G G Allen | NC | 3-2009 | ES-3 | Conventional Boiler | Tangential firing | 281.5 | 2228 | 7.9147 | bituminous | 0.08189 | 0.005594 | [10 empty] | 3.8917e-05 | 0.00030802 |  |  | 3.8917e-05 | 0.00030802 | 0.0010591 | 0.0083824 |  |  |  |  | 0.0010591 | 0.0083824 | 0.00048488 | 0.0038377 |  |  |  |  | 0.00048488 | 0.0038377 |  |  | 0.097062 | 0.76822 |  |  |  |  | 0.097062 | 0.76822 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2002-06-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
coal | 2718 | G G Allen | NC | 4-2009 | ES-4 | Conventional Boiler | Tangential firing | 297.3 | 2380 | 8.0054 | bituminous | 0.08189 | 0.005594 | [10 empty] | 3.8917e-05 | 0.00031154 |  |  | 3.8917e-05 | 0.00031154 | 0.0010591 | 0.0084784 |  |  |  |  | 0.0010591 | 0.0084784 | 0.00048488 | 0.0038817 |  |  |  |  | 0.00048488 | 0.0038817 |  |  | 0.097062 | 0.77701 |  |  |  |  | 0.097062 | 0.77701 | NOx control | Selective Noncatalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1999-02-01 | SO2 control | Wet FGD - Spray Type | 2009-04-01
coal | 2324 | Reid Gardner | NV | 1 | 1 | Conventional Boiler | Wall firing - front firing | 111 | 1215 | 10.9459 | bituminous | 0.023897 | 0.0081769 | [10 empty] | 0.000713 | 0.0078045 |  |  | 0.000713 | 0.0078045 | 0.0057131 | 0.062535 |  |  |  |  | 0.0057131 | 0.062535 | 0.00052785 | 0.0057778 |  |  |  |  | 0.00052785 | 0.0057778 |  |  | 0.062147 | 0.68026 |  |  | 0.055 | 0.60203 | 0.055 | 0.60203 | PM control | Fabric Filter, pulse | 2008-12-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
coal | 465 | Arapahoe | CO | Unit 3 | 3 | Conventional Boiler | Vertical firing | 48 | 754.8 | 15.725 | subbituminous | 0.0011861 | 0.0058214 | [10 empty] | 3.5733e-06 | 5.6191e-05 |  |  | 3.5733e-06 | 5.6191e-05 | 0.00021753 | 0.0034207 |  |  |  |  | 0.00021753 | 0.0034207 | 0.00054868 | 0.008628 |  |  |  |  | 0.00054868 | 0.008628 | 0.50068 | 7.8732 |  |  | 0.41341 | 6.5009 |  |  | 0.41341 | 6.5009 | SO2 control | Dry FGD - Sorbent Injection | 2002-12-01 | PM control | Fabric Filter, reverse air | 1979-06-01
coal | 2408 | PSEG Mercer Generating Station | NJ | MERU1E1PT1OS1-Coal | E1 | Conventional Boiler | Wall firing - unspecified | 343 | 3100 | 9.0379 | bituminous | [22 empty] | 0.081854 | 0.73979 | 0.081854 | 0.73979 |  |  |  |  | 0.00055216 | 0.0049903 | 0.00055216 | 0.0049903 | [10 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1994-05-01 | NOx control | Selective Catalytic Reduction | 2004-06-01 | Other control | Activated carbon injection | 2007-01-01 | PM control | Fabric Filter, pulse | 2008-12-01
coal | 1295 | Quindaro | KS | Unit 1 | 1 | Conventional Boiler | Cyclone firing | 77 | 782 | 10.1558 | coal - subbituminous | [6 empty] | 8e-05 | 0.00081247 | 8e-05 | 0.00081247 | [12 empty] | 0.00038 | 0.0038592 | 0.00038 | 0.0038592 |  |  |  |  | 0.00056667 | 0.005755 | 0.00056667 | 0.005755 | [10 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-11-01
coal | 6098 | Big Stone | SD | 001 | 001 | Conventional Boiler | Cyclone firing | 495 | 5309 | 10.7253 | subbituminous | [22 empty] | 0.0018333 | 0.019663 | 0.0018333 | 0.019663 |  |  |  |  | 0.00057 | 0.0061134 | 0.00057 | 0.0061134 | [10 empty] | PM control | Fabric Filter, pulse | 2007-12-01
coal | 887 | Joppa Steam | IL | 1 | 1 | Conventional Boiler | Tangential firing | 183.3 | 1800 | 9.82 | subbituminous | 0.0017313 | 0.0050549 | [10 empty] | 7.4667e-05 | 0.00073322 |  |  | 7.4667e-05 | 0.00073322 | 0.00064118 | 0.0062964 |  |  |  |  | 0.00064118 | 0.0062964 | 0.00057567 | 0.0056531 |  |  |  |  | 0.00057567 | 0.0056531 | 0.5832 | 5.727 | [6 empty] | 0.5832 | 5.727 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-01-01
coal | 50888 | Northampton Generating Company, L.P. | PA | GEN1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 121 | 1146 | 9.4711 | coal refuse (culm or gob) | 0.021589 | 0.0095487 | [10 empty] | 5.8133e-06 | 5.5059e-05 |  |  | 5.8133e-06 | 5.5059e-05 | 0.026313 | 0.24921 |  |  |  |  | 0.026313 | 0.24921 | 0.00058282 | 0.0055199 |  |  |  |  | 0.00058282 | 0.0055199 |  |  | 0.12354 | 1.17 |  |  |  |  | 0.12354 | 1.17 | NOx control | Selective Noncatalytic Reduction | 1995-08-01 | PM control | Fabric Filter, pulse | 1995-08-01
coal | 50974 | Scrubgrass Generating Company L.P. | PA | Gen 1 | #1 CFB boiler | Fluidized bed firing | Fluidized bed firing | 48.5 | 650 | 13.4021 | coal refuse (culm or gob) | 0.15666 | 0.024961 | [10 empty] | 0.0014333 | 0.018471 |  |  | 0.0014333 | 0.018471 | 0.15343 | 1.9772 |  |  |  |  | 0.15343 | 1.9772 | 0.10349 | 1.3337 |  |  | 0.0006 | 0.007732 | 0.0006 | 0.007732 |  |  | 0.73514 | 9.4735 |  |  |  |  | 0.73514 | 9.4735 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01
coal | 50974 | Scrubgrass Generating Company L.P. | PA | Gen 1 | #2 CFB Boiler | Fluidized bed firing | Fluidized bed firing | 48.5 | 600 | 12.3711 | coal refuse (culm or gob) | 0.15666 | 0.024961 | [10 empty] | 0.0014333 | 0.018471 |  |  | 0.0014333 | 0.018471 | 0.15343 | 1.9772 |  |  |  |  | 0.15343 | 1.9772 | 0.10349 | 1.3337 |  |  | 0.0006 | 0.007732 | 0.0006 | 0.007732 |  |  | 0.73514 | 9.4735 |  |  |  |  | 0.73514 | 9.4735 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01
coal | 465 | Arapahoe | CO | Unit 4 | 4 | Conventional Boiler | Vertical firing | 118 | 1709.4 | 14.4864 | subbituminous | 0.0027021 | 0.0056382 | [10 empty] | 3.7732e-06 | 5.4661e-05 |  |  | 3.7732e-06 | 5.4661e-05 | 0.0061502 | 0.089095 |  |  |  |  | 0.0061502 | 0.089095 | 0.00062002 | 0.0089819 |  |  |  |  | 0.00062002 | 0.0089819 | 0.388 | 5.6207 |  |  | 0.36976 | 5.3565 |  |  | 0.36976 | 5.3565 | SO2 control | Dry FGD - Sorbent Injection | 1993-06-01 | PM control | Fabric Filter, reverse air | 1985-04-01
coal | 469 | Cherokee | CO | Unit 1 | 1 | Conventional Boiler | Vertical firing | 117 | 1392 | 11.8974 | bituminous | 0.00082909 | 0.0070235 | [10 empty] | 3.1033e-05 | 0.00036922 |  |  | 3.1033e-05 | 0.00036922 | 0.00022537 | 0.0026813 |  |  |  |  | 0.00022537 | 0.0026813 | 0.00063932 | 0.0076063 |  |  |  |  | 0.00063932 | 0.0076063 | 0.51596 | 6.1386 |  |  | 0.48371 | 5.7549 |  |  | 0.48371 | 5.7549 | SO2 control | Dry FGD - Sorbent Injection | 1998-02-01 | PM control | Fabric Filter, reverse air | 1989-09-01
coal | 861 | Coffeen | IL | 001 | 1 | Conventional Boiler | Cyclone firing | 360 | 3282 | 9.1167 | subbituminous | 0.021606 | [11 empty] | 0.00011233 | 0.0010241 |  |  | 0.00011233 | 0.0010241 | 0.0015179 | 0.013838 |  |  |  |  | 0.0015179 | 0.013838 | 0.00067536 | 0.006157 |  |  |  |  | 0.00067536 | 0.006157 | 0.0084667 | 0.077188 | [6 empty] | 0.0084667 | 0.077188 | NOx control | Selective Catalytic Reduction | 2003-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1973-01-01 | SO2 control | Wet FGD - Unspecified | 2009-11-01
coal | 3954 | Mt. Storm | WV | Unit 1&2 | 1 | Conventional Boiler | Tangential firing | 552.8 | 6446 | 11.6606 | bituminous | 0.084592 | 0.0048812 | [10 empty] | 0.000238 | 0.0028349 |  |  | 0.000238 | 0.0028349 | 0.00084001 | 0.010006 |  |  |  |  | 0.00084001 | 0.010006 | 0.00070686 | 0.0084196 |  |  |  |  | 0.00070686 | 0.0084196 |  |  | 0.20227 | 2.4093 |  |  |  |  | 0.20227 | 2.4093 | NOx control | Selective Catalytic Reduction | 2003-05-01 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1965-09-01 | SO2 control | Wet FGD - Spray Type | 2002-03-01 | SO2 control | Wet FGD - Spray Type | 2002-03-01
coal | 3954 | Mt. Storm | WV | Unit 1&2 | 2 | Conventional Boiler | Tangential firing | 555.9 | 6760 | 12.1605 | bituminous | 0.084592 | 0.0048812 | [10 empty] | 0.000238 | 0.0028349 |  |  | 0.000238 | 0.0028349 | 0.00084001 | 0.010006 |  |  |  |  | 0.00084001 | 0.010006 | 0.00070686 | 0.0084196 |  |  |  |  | 0.00070686 | 0.0084196 |  |  | 0.20227 | 2.4093 |  |  |  |  | 0.20227 | 2.4093 | NOx control | Selective Catalytic Reduction | 2003-05-01 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1965-09-01 | SO2 control | Wet FGD - Spray Type | 2002-03-01 | SO2 control | Wet FGD - Spray Type | 2002-03-01
coal | 469 | Cherokee | CO | Unit 2 | 2 | Conventional Boiler | Vertical firing | 114 | 1392 | 12.2105 | bituminous | 0.0010927 | 0.0075975 | [10 empty] | 3.6633e-05 | 0.00044731 |  |  | 3.6633e-05 | 0.00044731 | 0.00018637 | 0.0022756 |  |  |  |  | 0.00018637 | 0.0022756 | 0.00071596 | 0.0087422 |  |  |  |  | 0.00071596 | 0.0087422 | 0.52593 | 6.4218 |  |  | 0.44218 | 5.3993 |  |  | 0.44218 | 5.3993 | SO2 control | Dry FGD - Sorbent Injection | 2002-12-01 | PM control | Fabric Filter, reverse air | 1985-05-01
coal | 10849 | Silver Bay Power | MN | GEN1 | BLR1 | Conventional Boiler | Wall firing - front firing | 45 | 371.9119 | 8.2647 | subbituminous | 0.0092308 | 0.0042735 | [10 empty] | 2.8519e-05 | 0.0002357 |  |  | 2.8519e-05 | 0.0002357 |  |  | 0.0016633 | 0.013747 |  |  | 0.0016633 | 0.013747 |  |  | 0.00075068 | 0.0062042 |  |  | 0.00075068 | 0.0062042 | 0.44133 | 3.6475 |  |  |  |  | 0.33667 | 2.7825 | 0.33667 | 2.7825 | PM control | Fabric Filter, reverse air | 1980-01-01
coal | 2103 | Labadie | MO | 002 | 2 | Conventional Boiler | Tangential firing | 623 | 6183 | 9.9246 | [23 empty] | 0.00027303 | 0.0027097 | 0.00027303 | 0.0027097 |  |  |  |  | 0.00075408 | 0.0074839 | 0.00075408 | 0.0074839 | [10 empty] | Other control | Other (specify): FGC SO3 Injection | 1992-11-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1982-12-01
coal | 2554 | Dunkirk Generating Plant | NY | 4 | 4 | Conventional Boiler | Tangential firing | 195 | 1836 | 9.4154 | subbituminous | [12 empty] | 1e-05 | 9.4154e-05 |  |  | 1e-05 | 9.4154e-05 | 0.00096696 | 0.0091043 |  |  |  |  | 0.00096696 | 0.0091043 | 0.00076075 | 0.0071628 |  |  |  |  | 0.00076075 | 0.0071628 |  |  | 0.40714 | 3.8333 |  |  |  |  | 0.40714 | 3.8333 | NOx control | Selective Noncatalytic Reduction |  | Other control | Dry sorbent injection |  | PM control | Fabric Filter, unspecified | 2009-05-01
coal | 8042 | Belews Creek Steam Station | NC | 1-2008 | Unit 1 | Conventional Boiler | Wall firing - opposed firing | 1185.8 | 10800 | 9.1078 | bituminous | 0.08641 | 0.0051332 | [10 empty] | 2.5667e-06 | 2.3377e-05 |  |  | 2.5667e-06 | 2.3377e-05 | 0.00063354 | 0.0057702 |  |  |  |  | 0.00063354 | 0.0057702 | 0.00080668 | 0.0073471 |  |  |  |  | 0.00080668 | 0.0073471 |  |  | 0.04836 | 0.44045 |  |  |  |  | 0.04836 | 0.44045 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1973-01-01 | SO2 control | Wet FGD - Spray Type | 2008-01-01
coal | 10151 | Grant Town Power Plant | WV | GEN1 | BLR1A | Fluidized bed firing | Fluidized bed firing | 47.5 | 675 | 14.2105 | coal refuse (culm or gob) | 0.044245 | 0.013111 | [10 empty] | 0.00013387 | 0.0019023 |  |  | 0.00013387 | 0.0019023 | 0.048369 | 0.68734 |  |  |  |  | 0.048369 | 0.68734 | 0.00081597 | 0.011595 |  |  |  |  | 0.00081597 | 0.011595 | 0.64453 | 9.1592 | [6 empty] | 0.64453 | 9.1592 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | PM control | Fabric Filter, pulse | 1992-07-01 | PM control | Fabric Filter, pulse | 2005-05-01
coal | 10151 | Grant Town Power Plant | WV | GEN1 | BLR1B | Fluidized bed firing | Fluidized bed firing | 47.5 | 675 | 14.2105 | coal refuse (culm or gob) | 0.044245 | 0.013111 | [10 empty] | 0.00013387 | 0.0019023 |  |  | 0.00013387 | 0.0019023 | 0.048369 | 0.68734 |  |  |  |  | 0.048369 | 0.68734 | 0.00081597 | 0.011595 |  |  |  |  | 0.00081597 | 0.011595 | 0.64453 | 9.1592 | [6 empty] | 0.64453 | 9.1592 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | PM control | Fabric Filter, pulse | 1992-07-01 | PM control | Fabric Filter, pulse | 2005-05-01
coal | 3954 | Mt. Storm | WV | Unit 3 | 3 | Conventional Boiler | Tangential firing | 559.8 | 5923 | 10.5806 | bituminous | 0.044478 | 0.0046647 | [10 empty] | 0.00048133 | 0.0050928 |  |  | 0.00048133 | 0.0050928 | 0.00028488 | 0.0030142 |  |  |  |  | 0.00028488 | 0.0030142 | 0.00087828 | 0.0092927 |  |  |  |  | 0.00087828 | 0.0092927 | 0.098267 | 1.0397 | [6 empty] | 0.098267 | 1.0397 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 1250 | Lawrence Energy Center | KS | 3 | 3 | Conventional Boiler | Tangential firing | 58 | 645 | 11.1207 | bituminous | 0.0008221 | 0.0051521 | [10 empty] | 0.0086667 | 0.096379 |  |  | 0.0086667 | 0.096379 | [10 empty] | 0.0009 | 0.010009 |  |  | 0.0009 | 0.010009 | 233.3253 | 2594.7381 |  |  | 0.3975 | 4.4205 |  |  | 0.3975 | 4.4205 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
coal | 3403 | Gallatin | TN | 2 | 2 | Conventional Boiler | Tangential firing | 300 | 2750 | 9.1667 | subbituminous | 0.009126 | 0.0077945 | [10 empty] | 2.8333e-06 | 2.5972e-05 |  |  | 2.8333e-06 | 2.5972e-05 | 0.0015582 | 0.014284 |  |  |  |  | 0.0015582 | 0.014284 | 0.00090896 | 0.0083322 |  |  |  |  | 0.00090896 | 0.0083322 |  |  | 0.59524 | 5.4564 |  |  |  |  | 0.59524 | 5.4564 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-09-01
coal | 3788 | Potomac River | VA | 4 | 4 | Conventional Boiler | Tangential firing | 108 | 961 | 8.8981 | coal - bituminous | [22 empty] | 0.00113 | 0.010055 | 0.00113 | 0.010055 |  |  |  |  | 0.000981 | 0.0087291 | 0.000981 | 0.0087291 | [6 empty] | 0.27 | 2.4025 | 0.27 | 2.4025 | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1956-02-01
coal | 1393 | RS Nelson | LA | 001 | 6 | Conventional Boiler | Tangential firing | 580 | 5761 | 9.9328 | bituminous | 0.0010387 | 0.0050798 | [10 empty] | 0.00012867 | 0.001278 |  |  | 0.00012867 | 0.001278 |  |  | 0.00258 | 0.025627 |  |  | 0.00258 | 0.025627 |  |  | 0.0010497 | 0.010426 |  |  | 0.0010497 | 0.010426 |  |  | 0.64056 | 6.3626 |  |  |  |  | 0.64056 | 6.3626 | PM control | Electrostatic precipitator, unspecified | 1982-05-01
coal | 2554 | Dunkirk Generating Plant | NY | 1 | 1 | Conventional Boiler | Tangential firing | 85 | 922.2 | 10.8494 | subbituminous | [12 empty] | 1e-05 | 0.00010849 |  |  | 1e-05 | 0.00010849 | 0.00091345 | 0.0099103 |  |  |  |  | 0.00091345 | 0.0099103 | 0.0012551 | 0.013617 |  |  |  |  | 0.0012551 | 0.013617 |  |  | 0.40826 | 4.4294 |  |  |  |  | 0.40826 | 4.4294 | NOx control | Selective Noncatalytic Reduction |  | Other control | Dry sorbent injection |  | PM control | Fabric Filter, unspecified | 2009-12-01
coal | 2408 | PSEG Mercer Generating Station | NJ | MERU2E2PT2OS1-Coal | E2 | Conventional Boiler | Wall firing - unspecified | 343 | 3100 | 9.0379 | bituminous | [22 empty] | 0.049984 | 0.45175 | 0.049984 | 0.45175 |  |  |  |  | 0.0012821 | 0.011587 | 0.0012821 | 0.011587 | [10 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1991-08-01 | NOx control | Selective Catalytic Reduction | 2004-06-01 | Other control | Activated carbon injection | 2007-01-01 | PM control | Fabric Filter, pulse | 2008-12-01
coal | 50776 | PANTHER CREEK ENERGY FACILITY | PA | BG1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 46.5 | 600 | 12.9032 | coal refuse (culm or gob) | 0.019015 | 0.0058435 | [10 empty] | 0.00143 | 0.018452 |  |  | 0.00143 | 0.018452 | 0.01181 | 0.15239 |  |  | 0.0185 | 0.23871 | 0.01181 | 0.15239 | 0.0018815 | 0.024277 |  |  | 0.0015 | 0.019355 | 0.0015 | 0.019355 |  |  | 0.093701 | 1.209 |  |  |  |  | 0.093701 | 1.209 | NOx control | Selective Noncatalytic Reduction | 1992-10-01 | PM control | Fabric Filter, pulse | 1992-10-01
coal | 50776 | PANTHER CREEK ENERGY FACILITY | PA | BG2 | BLR2 | Fluidized bed firing | Fluidized bed firing | 46.5 | 600 | 12.9032 | coal refuse (culm or gob) | 0.019015 | 0.0058435 | [10 empty] | 0.00143 | 0.018452 |  |  | 0.00143 | 0.018452 | 0.01181 | 0.15239 |  |  | 0.019467 | 0.25118 | 0.01181 | 0.15239 | 0.0018815 | 0.024277 |  |  | 0.0015333 | 0.019785 | 0.0015333 | 0.019785 |  |  | 0.093701 | 1.209 |  |  |  |  | 0.093701 | 1.209 | NOx control | Selective Noncatalytic Reduction | 1992-10-01 | PM control | Fabric Filter, pulse | 1992-10-01
coal | 2107 | Sioux | MO | 002 | 2 | Conventional Boiler | Cyclone firing | 524 | 4920 | 9.3893 | subbituminous, bituminous | 0.015747 | 0.0088813 | [10 empty] | 0.00011103 | 0.0010425 |  |  | 0.00011103 | 0.0010425 | 0.016034 | 0.15055 |  |  |  |  | 0.016034 | 0.15055 | 0.0016224 | 0.015234 |  |  |  |  | 0.0016224 | 0.015234 | 1.6986 | 15.949 | [6 empty] | 1.6986 | 15.949 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1997-12-01 | SO2 control | Wet FGD - Unspecified
coal | 1295 | Quindaro | KS | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 119.8 | 1394 | 11.6361 | bituminous | [6 empty] | 0.00010333 | 0.0012024 | 0.00010333 | 0.0012024 | [12 empty] | 0.00076333 | 0.0088822 | 0.00076333 | 0.0088822 |  |  |  |  | 0.0018706 | 0.021766 | 0.0018706 | 0.021766 | [10 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1986-05-01
coal | 6085 | R.M. Schahfer | IN | R.M.0014 | 14 | Conventional Boiler | Cyclone firing | 468 | 4650 | 9.9359 | subbituminous | 0.021805 | [11 empty] | 0.0001022 | 0.0010154 |  |  | 0.0001022 | 0.0010154 | 0.0078754 | 0.078249 |  |  |  |  | 0.0078754 | 0.078249 | 0.0018984 | 0.018862 |  |  |  |  | 0.0018984 | 0.018862 |  |  | 0.81868 | 8.1343 |  |  |  |  | 0.81868 | 8.1343 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-06-01
coal | 2161 | James River Power Station | MO | Unit_4_JRPS | 4 | Conventional Boiler | Wall firing - front firing | 60 | 600 | 10 | subbituminous | 0.00086054 | 0.0039866 | [10 empty] | 0.00093333 | 0.0093333 |  |  | 0.00093333 | 0.0093333 |  |  | 0.00083333 | 0.0083333 |  |  | 0.00083333 | 0.0083333 |  |  | 0.0019 | 0.019 |  |  | 0.0019 | 0.019 | 0.5961 | 5.961 | [6 empty] | 0.5961 | 5.961 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-08-01
coal | 1626 | Salem Harbor | MA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 81.419 | 981 | 12.0488 | bituminous | 0.0016769 | 0.0029538 | [10 empty] | 0.0055929 | 0.067387 |  |  | 0.0055929 | 0.067387 | 0.0020396 | 0.024575 |  |  |  |  | 0.0020396 | 0.024575 | 0.0019641 | 0.023665 |  |  |  |  | 0.0019641 | 0.023665 |  |  | 0.76238 | 9.1857 |  |  |  |  | 0.76238 | 9.1857 | NOx control | Selective Noncatalytic Reduction | 1993-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-07-01
coal | 4072 | Pulliam | WI | 8 | 8 | Conventional Boiler | Wall firing - rear firing | 137.9 | 1510 | 10.95 | subbituminous | 0.0020726 | 0.0059691 | [10 empty] | 0.00023133 | 0.0025331 |  |  | 0.00023133 | 0.0025331 |  |  | 0.001182 | 0.012943 |  |  | 0.001182 | 0.012943 |  |  | 0.00197 | 0.021571 |  |  | 0.00197 | 0.021571 | 0.60707 | 6.6474 | [6 empty] | 0.60707 | 6.6474 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1964-12-01
coal | 3845 | TransAlta Centralia Generation | WA | BW21CONFIG | BD21 | Conventional Boiler | Tangential firing | 603 | 7743 | 12.8408 | subbituminous | 0.0049169 | 0.0085167 | [10 empty] | 2.01e-05 | 0.0002581 |  |  | 2.01e-05 | 0.0002581 | 0.0021218 | 0.027245 |  |  |  |  | 0.0021218 | 0.027245 | 0.0021766 | 0.027949 |  |  |  |  | 0.0021766 | 0.027949 | 0.057067 | 0.73278 |  |  |  |  | 0.0213 | 0.27351 | 0.0213 | 0.27351 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-01-01 | SO2 control | Wet FGD - Spray Type | 2002-06-01
coal | 3775 | Clinch River | VA | CR-1 | 1 | Conventional Boiler | Vertical firing | 230 | 2100.9 | 9.1343 | bituminous | 0.077039 | 0.0071692 | [10 empty] | 0.00029 | 0.002649 |  |  | 0.00029 | 0.002649 | 0.029092 | 0.26574 |  |  |  |  | 0.029092 | 0.26574 | 0.0022046 | 0.020138 |  |  |  |  | 0.0022046 | 0.020138 | 0.86497 | 7.9009 | [6 empty] | 0.86497 | 7.9009 | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1975-02-01
coal | 3788 | Potomac River | VA | 3 | 3 | Conventional Boiler | Tangential firing | 108 | 961 | 8.8981 | coal - bituminous | [22 empty] | 0.04556 | 0.4054 | 0.04556 | 0.4054 |  |  |  |  | 0.002223 | 0.019781 | 0.002223 | 0.019781 | [10 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1954-06-01
coal | 3845 | TransAlta Centralia Generation | WA | BW22CONFIG | BD22 | Conventional Boiler | Tangential firing | 567 | 7743 | 13.6561 | subbituminous | 0.0037696 | 0.0053979 | [10 empty] | 2.1833e-05 | 0.00029816 |  |  | 2.1833e-05 | 0.00029816 | 0.0022946 | 0.031335 |  |  |  |  | 0.0022946 | 0.031335 | 0.0022946 | 0.031335 |  |  |  |  | 0.0022946 | 0.031335 | 0.0525 | 0.71694 |  |  |  |  | 0.023333 | 0.31864 | 0.023333 | 0.31864 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1971-12-01 | SO2 control | Wet FGD - Spray Type | 2001-10-01
coal | 6147 | Monticello | TX | 2 | 2 | Conventional Boiler | Tangential firing | 583 | 7000 | 12.0069 | lignite | [12 empty] | 2.0067e-05 | 0.00024094 |  |  | 2.0067e-05 | 0.00024094 | 0.00074886 | 0.0089914 |  |  |  |  | 0.00074886 | 0.0089914 | 0.0026295 | 0.031571 |  |  |  |  | 0.0026295 | 0.031571 |  |  | 0.81611 | 9.7989 |  |  |  |  | 0.81611 | 9.7989 | NOx control | Selective Noncatalytic Reduction | 2008-11-01 | Other control | Activated carbon injection | 2009-02-01 | PM control | Fabric Filter, shake and deflate | 1975-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1975-12-01
coal | 6288 | Healy | AK | 1 | 001 | Conventional Boiler | Wall firing - front firing | 25 | 347 | 13.88 | subbituminous | 0.0051256 | 0.0085748 | [10 empty] | 4.4667e-05 | 0.00061997 |  |  | 4.4667e-05 | 0.00061997 | 0.00015405 | 0.0021382 |  |  |  |  | 0.00015405 | 0.0021382 | 0.0026377 | 0.036611 |  |  |  |  | 0.0026377 | 0.036611 |  |  | 0.34595 | 4.8018 |  |  |  |  | 0.34595 | 4.8018 | PM control | Fabric Filter, pulse | 1980-01-01
coal | 2828 | Cardinal | OH | CD-U3 | 3 | Conventional Boiler | Wall firing - opposed firing | 650 | 5275 | 8.1154 | bituminous | 0.058236 | 0.0056419 | [10 empty] | 0.00018633 | 0.0015122 |  |  | 0.00018633 | 0.0015122 | 0.034472 | 0.27975 |  |  |  |  | 0.034472 | 0.27975 | 0.0031369 | 0.025458 |  |  |  |  | 0.0031369 | 0.025458 | 1.4084 | 11.4296 | [6 empty] | 1.4084 | 11.4296 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-09-01 | NOx control | Selective Catalytic Reduction | 2003-01-01
coal | 492 | Martin Drake | CO | Unit 5 - Coal | 5 | Conventional Boiler | Wall firing - front firing | 55 | 570 | 10.3636 | subbituminous | [22 empty] | 0.00203 | 0.021038 | 0.00203 | 0.021038 |  |  |  |  | 0.00314 | 0.032542 | 0.00314 | 0.032542 | [10 empty] | PM control | Fabric Filter, reverse air | 1998-05-01
coal | 6017 | Newton | IL | 002 | 2 | Conventional Boiler | Tangential firing | 620 | 5500 | 8.871 | subbituminous | 0.0012994 | 0.006009 | [10 empty] | 8.01e-05 | 0.00071056 |  |  | 8.01e-05 | 0.00071056 | 0.00048706 | 0.0043207 |  |  |  |  | 0.00048706 | 0.0043207 | 0.0033769 | 0.029957 |  |  |  |  | 0.0033769 | 0.029957 | [10 empty] | Other control | Other (specify): Flue gas conditioning | 2001-04-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning
coal | 988 | Tanners Creek | IN | TC-4 | 4 | Conventional Boiler | Cyclone firing | 579.7 | 4990 | 8.6079 | subbituminous, bituminous | 0.026962 | 0.0044752 | [10 empty] | 0.00019333 | 0.0016642 |  |  | 0.00019333 | 0.0016642 | 0.017865 | 0.15378 |  |  |  |  | 0.017865 | 0.15378 | 0.0038116 | 0.032809 |  |  |  |  | 0.0038116 | 0.032809 | 1.3719 | 11.8091 | [6 empty] | 1.3719 | 11.8091 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-11-01
coal | 2837 | Eastlake | OH | Unit 1 | 1 | Conventional Boiler | Tangential firing | 144 | 1205 | 8.3681 | subbituminous, bituminous | 0.023937 | 0.0044064 | [10 empty] | 0.00097362 | 0.0081473 |  |  | 0.00097362 | 0.0081473 | 0.048399 | 0.40501 |  |  |  |  | 0.048399 | 0.40501 | 0.0039485 | 0.033042 |  |  |  |  | 0.0039485 | 0.033042 |  |  | 1.8619 | 15.5803 |  |  |  |  | 1.8619 | 15.5803 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
coal | 3115 | Titus | PA | TI-2 | 2 | Conventional Boiler | Tangential firing | 86.2 | 900 | 10.4408 | coal - bituminous | [22 empty] | 0.095667 | 0.99884 | 0.095667 | 0.99884 |  |  |  |  | 0.0043333 | 0.045244 | 0.0043333 | 0.045244 | [10 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-02-01
coal | 2837 | Eastlake | OH | Unit 3 | 3 | Conventional Boiler | Tangential firing | 144 | 1205 | 8.3681 | subbituminous, bituminous | 0.051324 | 0.0046979 | [10 empty] | 0.0011797 | 0.0098722 |  |  | 0.0011797 | 0.0098722 | 0.063698 | 0.53302 |  |  |  |  | 0.063698 | 0.53302 | 0.0044592 | 0.037315 |  |  |  |  | 0.0044592 | 0.037315 |  |  | 2.1209 | 17.7476 |  |  |  |  | 2.1209 | 17.7476 | NOx control | Selective Noncatalytic Reduction | 1999-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-01-01
coal | 1385 | Dale Station | KY | 03 | 3 | Conventional Boiler | Wall firing - front firing | 80 | 944 | 11.8 | bituminous |  | 0.0029345 | [10 empty] | 0.00053333 | 0.0062933 |  |  | 0.00053333 | 0.0062933 | 0.14399 | 1.6991 | 0.14403 | 1.6996 |  |  | 0.14399 | 1.6991 | 0.0045268 | 0.053416 | 0.0045333 | 0.053493 |  |  | 0.0045268 | 0.053416 | 1.4328 | 16.9066 | [6 empty] | 1.4328 | 16.9066 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning
coal | 1008 | R. Gallagher | IN | 2-2007 | 2 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | 9.7333 | coal - bituminous | [22 empty] | 0.257 | 2.5014 | 0.257 | 2.5014 |  |  |  |  | 0.0046061 | 0.044833 | 0.0046061 | 0.044833 | [6 empty] | 0.003236 | 0.031497 | 0.003236 | 0.031497 | PM control | Fabric Filter, shake and deflate | 2007-12-01
coal | 1010 | Wabash River | IN | 6 | 6 | Conventional Boiler | Tangential firing | 342 | 3059.0605 | 8.9446 | bituminous | 0.043129 | 0.0037291 | [10 empty] | 2.24e-05 | 0.00020036 |  |  | 2.24e-05 | 0.00020036 | 0.012675 | 0.11338 |  |  |  |  | 0.012675 | 0.11338 | 0.0046267 | 0.041384 |  |  |  |  | 0.0046267 | 0.041384 |  |  | 3.662 | 32.7552 |  |  |  |  | 3.662 | 32.7552 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-05-01
coal | 1010 | Wabash River | IN | 4 | 4 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | 10.2633 | bituminous | 0.043129 | 0.0037291 | [10 empty] | 2.24e-05 | 0.0002299 |  |  | 2.24e-05 | 0.0002299 | 0.012675 | 0.13009 |  |  |  |  | 0.012675 | 0.13009 | 0.0046267 | 0.047485 |  |  |  |  | 0.0046267 | 0.047485 |  |  | 3.662 | 37.5841 |  |  |  |  | 3.662 | 37.5841 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-10-01
coal | 1040 | Whitewater Valley | IN | 002 | 2 | Conventional Boiler | Tangential firing | 69 | 730 | 10.5797 | bituminous | 0.016841 | 0.0042452 | [10 empty] | 2.6233e-05 | 0.00027754 |  |  | 2.6233e-05 | 0.00027754 | 0.0072622 | 0.076832 |  |  |  |  | 0.0072622 | 0.076832 | 0.0046959 | 0.049681 |  |  |  |  | 0.0046959 | 0.049681 |  |  | 3.548 | 37.5371 |  |  |  |  | 3.548 | 37.5371 | NOx control | Selective Noncatalytic Reduction | 2003-09-01 | PM control | Electrostatic precipitator, unspecified | 1973-05-16 | PM control | Fabric Filter, unspecified | 2009-01-06
coal | 1218 | Fair Station | IA | U2 | 2 | Conventional Boiler | Wall firing - front firing | 44 | 465 | 10.5682 | bituminous | 0.16427 | 0.0041938 | [10 empty] | 0.00018267 | 0.0019305 |  |  | 0.00018267 | 0.0019305 | 0.17785 | 1.8795 |  |  |  |  | 0.17785 | 1.8795 | 0.0047332 | 0.050021 |  |  |  |  | 0.0047332 | 0.050021 | 2.0314 | 21.4679 | [6 empty] | 2.0314 | 21.4679 | Other control | Other (specify): Flue gas conditioning for opacity control | 2006-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-10-01
coal | 3942 | Albright Power Station | WV | Unit_1 | 1 | Conventional Boiler | Wall firing - unspecified | 81 | 786 | 9.7037 | bituminous | 0.012891 | 0.0034365 | [10 empty] | 0.00077233 | 0.0074945 |  |  | 0.00077233 | 0.0074945 | 0.020307 | 0.19705 |  |  |  |  | 0.020307 | 0.19705 | 0.0054918 | 0.053291 |  |  |  |  | 0.0054918 | 0.053291 |  |  | 2.3668 | 22.9665 |  |  |  |  | 2.3668 | 22.9665 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
coal | 2840 | Conesville | OH | CV-3 | 3 | Conventional Boiler | Wall firing - front firing | 165 | 1862 | 11.2848 | bituminous | 0.041145 | 0.0045128 | [10 empty] | 0.000762 | 0.0085991 |  |  | 0.000762 | 0.0085991 | 0.035774 | 0.4037 |  |  |  |  | 0.035774 | 0.4037 | 0.0058129 | 0.065598 |  |  |  |  | 0.0058129 | 0.065598 | 4.1253 | 46.5528 | [6 empty] | 4.1253 | 46.5528 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-01-01
coal | 47 | Colbert | AL | 3 | 3 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | 10.605 | other--subbituminous/bituminous blend | 0.026409 | 0.0072358 | [10 empty] | 0.00048 | 0.0050904 |  |  | 0.00048 | 0.0050904 | 0.013641 | 0.14466 |  |  |  |  | 0.013641 | 0.14466 | 0.0058475 | 0.062013 |  |  |  |  | 0.0058475 | 0.062013 |  |  | 0.60788 | 6.4465 |  |  |  |  | 0.60788 | 6.4465 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-05-01
coal | 642 | Scholz | FL | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 49 | 581.091 | 11.859 | bituminous | 0.09247 | 0.0051878 | [10 empty] | 4.2667e-05 | 0.00050598 |  |  | 4.2667e-05 | 0.00050598 | 0.10835 | 1.2849 |  |  |  |  | 0.10835 | 1.2849 | 0.0059504 | 0.070566 |  |  |  |  | 0.0059504 | 0.070566 | 1.4127 | 16.7534 |  |  |  |  | 1.3667 | 16.2073 | 1.3667 | 16.2073 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01
coal | 642 | Scholz | FL | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 49 | 644.742 | 13.158 | bituminous | 0.09247 | 0.0051878 | [10 empty] | 4.2667e-05 | 0.00056141 |  |  | 4.2667e-05 | 0.00056141 | 0.10835 | 1.4256 |  |  |  |  | 0.10835 | 1.4256 | 0.0059504 | 0.078296 |  |  |  |  | 0.0059504 | 0.078296 | 1.4127 | 18.5885 |  |  |  |  | 1.3667 | 17.9826 | 1.3667 | 17.9826 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2007-12-01
coal | 7210 | Cope | SC | COP001 | COP1 | Conventional Boiler | Tangential firing | 441 | 4059.1 | 9.2043 | bituminous | 0.066539 | 0.0056809 | [10 empty] | 0.00090521 | 0.0083319 |  |  | 0.00090521 | 0.0083319 |  |  | 0.011767 | 0.1083 |  |  | 0.011767 | 0.1083 |  |  | 0.0061967 | 0.057036 |  |  | 0.0061967 | 0.057036 | [10 empty] | NOx control | Selective Catalytic Reduction | 2009-01-01 | SO2 control | Dry FGD - Spray Dryer | 1993-04-01 | PM control | Fabric Filter, unspecified | 1993-04-01
coal | 3297 | Wateree | SC | WAT002 | WAT2 | Conventional Boiler | Wall firing - unspecified | 380 | 3305.1 | 8.6976 | [23 empty] | 0.0596 | 0.51838 | 0.0596 | 0.51838 |  |  |  |  | 0.00664 | 0.057752 | 0.00664 | 0.057752 | [10 empty] | NOx control | Selective Catalytic Reduction | 2004-04-01 | PM control | Fabric Filter, unspecified | 2001-07-01 | SO2 control | Wet FGD - Unspecified
coal | 628 | Crystal River Power Plant | FL | CryR_Cfg_1 | 1 | Conventional Boiler | Tangential firing | 400 | 3837 | 9.5925 | bituminous | 0.11387 | 0.0056012 | [10 empty] | 2.9133e-05 | 0.00027946 |  |  | 2.9133e-05 | 0.00027946 | 0.074352 | 0.71323 |  |  |  |  | 0.074352 | 0.71323 | 0.007471 | 0.071666 |  |  |  |  | 0.007471 | 0.071666 |  |  | 1.367 | 13.1131 |  |  |  |  | 1.367 | 13.1131 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
coal | 3935 | John E. Amos | WV | AM-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | [12 empty] | 0.00020833 | 0.0017916 |  |  | 0.00020833 | 0.0017916 | 0.075845 | 0.65225 |  |  |  |  | 0.075845 | 0.65225 | 0.007504 | 0.064533 |  |  |  |  | 0.007504 | 0.064533 | 1.2657 | 10.8847 | [6 empty] | 1.2657 | 10.8847 | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-04-01
coal | 3942 | Albright Power Station | WV | Unit_2 | 2 | Conventional Boiler | Wall firing - unspecified | 81 | 643 | 7.9383 | bituminous | 0.020284 | 0.0090344 | [10 empty] | 0.00016033 | 0.0012728 |  |  | 0.00016033 | 0.0012728 | 0.033133 | 0.26302 |  |  |  |  | 0.033133 | 0.26302 | 0.0076195 | 0.060485 |  |  |  |  | 0.0076195 | 0.060485 |  |  | 2.0144 | 15.9909 |  |  |  |  | 2.0144 | 15.9909 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
coal | 3152 | Sunbury Generation LP | PA | Boiler 3 | 3 | Conventional Boiler | Wall firing - front firing | 94 | 1100 | 11.7021 | coal - bituminous | [22 empty] | 0.067657 | 0.79173 | 0.067657 | 0.79173 |  |  |  |  | 0.0077597 | 0.090805 | 0.0077597 | 0.090805 | [10 empty] | Other control | Other (specify): SO3 injection | 1980-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-06-01
coal | 3131 | Shawville | PA | SHAW3-2 | 3 | Conventional Boiler | Tangential firing | 188 | 1794 | 9.5426 | bituminous | 0.05641 | 0.0029125 | [10 empty] | 8.28e-05 | 0.00079012 |  |  | 8.28e-05 | 0.00079012 | 0.089306 | 0.8522 |  |  |  |  | 0.089306 | 0.8522 | 0.0078141 | 0.074566 |  |  |  |  | 0.0078141 | 0.074566 | 3.1493 | 30.0524 | [6 empty] | 3.1493 | 30.0524 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1959-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
coal | 3131 | Shawville | PA | SHAW4-2 | 4 | Conventional Boiler | Tangential firing | 188 | 1794 | 9.5426 | bituminous | 0.05641 | 0.0029125 | [10 empty] | 8.28e-05 | 0.00079012 |  |  | 8.28e-05 | 0.00079012 | 0.089306 | 0.8522 |  |  |  |  | 0.089306 | 0.8522 | 0.0078141 | 0.074566 |  |  |  |  | 0.0078141 | 0.074566 | 3.1493 | 30.0524 | [6 empty] | 3.1493 | 30.0524 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
coal | 3297 | Wateree | SC | WAT001 | WAT1 | Conventional Boiler | Wall firing - unspecified | 383 | 3329.7 | 8.6937 | [23 empty] | 0.056 | 0.48685 | 0.056 | 0.48685 |  |  |  |  | 0.00807 | 0.070158 | 0.00807 | 0.070158 | [10 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Fabric Filter, unspecified | 2001-05-01 | SO2 control | Wet FGD - Unspecified
coal | 3948 | Mitchell | WV | MI-2 | 2 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | 0.075257 | 0.0065234 | [10 empty] | 0.000204 | 0.0017544 |  |  | 0.000204 | 0.0017544 | 0.01226 | 0.10544 |  |  |  |  | 0.01226 | 0.10544 | 0.0081736 | 0.070291 |  |  |  |  | 0.0081736 | 0.070291 | 0.075067 | 0.64556 | [6 empty] | 0.075067 | 0.64556 | NOx control | Selective Catalytic Reduction | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-08-01 | SO2 control | Wet FGD - Tray Type | 2007-01-01
coal | 492 | Martin Drake | CO | Unit 7 - Coal | 7 | Conventional Boiler | Wall firing - front firing | 141 | 1475 | 10.461 | subbituminous, bituminous | [22 empty] | 0.0014667 | 0.015343 | 0.0014667 | 0.015343 |  |  |  |  | 0.00875 | 0.091534 | 0.00875 | 0.091534 | [10 empty] | PM control | Fabric Filter, reverse air | 1993-11-01
coal | 54144 | Piney Creek Project | PA | BRBRI | BRBR1 | Fluidized bed firing | Fluidized bed firing | 36 | 450 | 12.5 | bituminous, synfuel | 0.057013 | 0.019094 | [10 empty] | 0.00025333 | 0.0031667 |  |  | 0.00025333 | 0.0031667 | 0.02688 | 0.336 |  |  |  |  | 0.02688 | 0.336 | 0.011998 | 0.14997 |  |  |  |  | 0.011998 | 0.14997 |  |  | 0.5784 | 7.23 |  |  | 0.66 | 8.25 | 0.5784 | 7.23 | NOx control | Selective Noncatalytic Reduction | 2002-08-01 | PM control | Fabric Filter, pulse | 1992-11-01
coal | 3152 | Sunbury Generation LP | PA | Boiler 4 | 4 | Conventional Boiler | Wall firing - front firing | 128 | 1360 | 10.625 | bituminous | 0.055138 | 0.005313 | [10 empty] | 0.00093333 | 0.0099167 |  |  | 0.00093333 | 0.0099167 |  |  | 0.051667 | 0.54896 |  |  | 0.051667 | 0.54896 |  |  | 0.014 | 0.14875 |  |  | 0.014 | 0.14875 | 3.0539 | 32.4473 | [6 empty] | 3.0539 | 32.4473 | Other control | Other (specify): SO3 injection | 1980-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-06-01
coal | 2732 | Riverbend | NC | 7 | 7 | Conventional Boiler | Tangential firing | 99.5 | 1059 | 10.6432 | bituminous | 0.067396 | 0.0061446 | [10 empty] | 5.5499e-06 | 5.9069e-05 |  |  | 5.5499e-06 | 5.9069e-05 | 0.14385 | 1.531 |  |  |  |  | 0.14385 | 1.531 | 0.014787 | 0.15739 |  |  |  |  | 0.014787 | 0.15739 |  |  | 2.8633 | 30.4745 |  |  |  |  | 2.8633 | 30.4745 | NOx control | Selective Noncatalytic Reduction | 2007-02-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1995-01-01
coal | 3152 | Sunbury Generation LP | PA | Boiler 2B | 2B | Conventional Boiler | Arch firing | 40 | 525 | 13.125 | coal - bituminous | [22 empty] | 0.027667 | 0.36313 | 0.027667 | 0.36313 |  |  |  |  | 0.015005 | 0.19694 | 0.015005 | 0.19694 | [10 empty] | PM control | Fabric Filter, reverse air | 1970-06-01
coal | 2716 | W.H. Weatherspoon Plant | NC | Wea_Cfg_1 | 1 | Conventional Boiler | Wall firing - front firing | 53 | 472 | 8.9057 | bituminous | 0.086032 | 0.004096 | [10 empty] | 4.1933e-05 | 0.00037344 |  |  | 4.1933e-05 | 0.00037344 | 0.19297 | 1.7185 |  |  |  |  | 0.19297 | 1.7185 | 0.01523 | 0.13563 |  |  |  |  | 0.01523 | 0.13563 |  |  | 3.2129 | 28.6132 |  |  |  |  | 3.2129 | 28.6132 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
coal | 2716 | W.H. Weatherspoon Plant | NC | Wea_Cfg_1 | 2 | Conventional Boiler | Wall firing - front firing | 53 | 472 | 8.9057 | bituminous | 0.086032 | 0.004096 | [10 empty] | 4.1933e-05 | 0.00037344 |  |  | 4.1933e-05 | 0.00037344 | 0.19297 | 1.7185 |  |  |  |  | 0.19297 | 1.7185 | 0.01523 | 0.13563 |  |  |  |  | 0.01523 | 0.13563 |  |  | 3.2129 | 28.6132 |  |  |  |  | 3.2129 | 28.6132 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
coal | 3948 | Mitchell | WV | MI-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | 0.077728 | 0.0066512 | [10 empty] | 0.00021933 | 0.0018862 |  |  | 0.00021933 | 0.0018862 | 0.013117 | 0.1128 |  |  |  |  | 0.013117 | 0.1128 | 0.01987 | 0.17088 |  |  |  |  | 0.01987 | 0.17088 | 0.0613 | 0.52717 | [6 empty] | 0.0613 | 0.52717 | NOx control | Selective Catalytic Reduction | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-02-01 | SO2 control | Wet FGD - Tray Type | 2007-01-01
coal | 1893 | Boswell Energy Center | MN | BEC3 | 3 | Conventional Boiler | Tangential firing | 371.3 | 4115 | 11.0827 | subbituminous | 0.0039194 | 0.0032475 | [16 empty] | 0.00051267 | 0.0056817 |  |  |  |  | 0.00051267 | 0.0056817 | 0.037945 | 0.42053 |  |  |  |  | 0.037945 | 0.42053 | 0.011667 | 0.1293 | [6 empty] | 0.011667 | 0.1293 | NOx control | Selective Catalytic Reduction |  | SO2 control | Wet FGD - Spray Type | 2009-01-01 | Other control | Activated carbon injection |  | PM control | Fabric Filter, unspecified | 2009-01-01
coal | 7253 | Richard Gorsuch | OH | UNIT3 | 3 | Conventional Boiler | Radiant | 53.3 | 553 | 10.3752 | bituminous | 0.059423 | 0.0059242 | [10 empty] | 9.3333e-05 | 0.00096836 |  |  | 9.3333e-05 | 0.00096836 | 0.007771 | 0.080626 |  |  |  |  | 0.007771 | 0.080626 | 0.043408 | 0.45037 |  |  |  |  | 0.043408 | 0.45037 |  |  | 2.6829 | 27.8359 |  |  |  |  | 2.6829 | 27.8359 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-06-01
coal | 963 | Dallman | IL | 31 | 31 | Conventional Boiler | Cyclone firing | 90 | 962.12 | 10.6902 | bituminous | 0.12999 | 0.0043066 | [10 empty] | 0.00020967 | 0.0022414 |  |  | 0.00020967 | 0.0022414 |  |  | 0.01259 | 0.13459 |  |  | 0.01259 | 0.13459 |  |  | 0.056089 | 0.5996 |  |  | 0.056089 | 0.5996 | 0.18217 | 1.9474 | [6 empty] | 0.18217 | 1.9474 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-06-01 | SO2 control | Wet FGD - Packed Type | 2001-08-01
coal | 963 | Dallman | IL | 32 | 32 | Conventional Boiler | Cyclone firing | 84 | 905.94 | 10.785 | bituminous | 0.12999 | 0.0043066 | [10 empty] | 0.00020967 | 0.0022613 |  |  | 0.00020967 | 0.0022613 |  |  | 0.01259 | 0.13578 |  |  | 0.01259 | 0.13578 |  |  | 0.056089 | 0.60492 |  |  | 0.056089 | 0.60492 | 0.18217 | 1.9647 | [6 empty] | 0.18217 | 1.9647 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Packed Type | 2001-08-01
coal | 1012 | F. B. Culley | IN | Config3 | 3 | Conventional Boiler | Wall firing - opposed firing | 287 | 2689 | 9.3693 | subbituminous | 0.083333 | 0.0065667 | [10 empty] | 0.00026133 | 0.0024485 |  |  | 0.00026133 | 0.0024485 | 0.10233 | 0.95878 |  |  |  |  | 0.10233 | 0.95878 | 0.068221 | 0.63918 |  |  |  |  | 0.068221 | 0.63918 | 0.080045 | 0.74997 | [6 empty] | 0.080045 | 0.74997 | NOx control | Selective Catalytic Reduction | 2004-01-01 | PM control | Fabric Filter, pulse | 2006-11-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 1012 | F. B. Culley | IN | Config2 | 2 | Conventional Boiler | Wall firing - opposed firing | 100 | 1031 | 10.31 | subbituminous | 0.083333 | 0.0065667 | [10 empty] | 0.00026133 | 0.0026943 |  |  | 0.00026133 | 0.0026943 | 0.10233 | 1.055 |  |  |  |  | 0.10233 | 1.055 | 0.068221 | 0.70336 |  |  |  |  | 0.068221 | 0.70336 | 0.080045 | 0.82527 | [6 empty] | 0.080045 | 0.82527 | PM control | Fabric Filter, pulse | 2006-11-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
coal | 8102 | General James M. Gavin | OH | GA-2 | 2 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11936 | 9.0424 | bituminous | 0.036174 | 0.0066351 | [10 empty] | 0.0002 | 0.0018085 |  |  | 0.0002 | 0.0018085 | 0.011177 | 0.10107 |  |  |  |  | 0.011177 | 0.10107 | 0.074512 | 0.67377 |  |  |  |  | 0.074512 | 0.67377 | 0.26869 | 2.4296 | [6 empty] | 0.26869 | 2.4296 | NOx control | Selective Catalytic Reduction | 2000-01-01 | Other control | Dry sorbent injection | 2001-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-03-01 | SO2 control | Wet FGD - Spray Type | 1995-03-01
coal | 8102 | General James M. Gavin | OH | GA-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11936 | 9.0424 | bituminous | 0.031068 | 0.0066543 | [10 empty] | 0.0002 | 0.0018085 |  |  | 0.0002 | 0.0018085 | 0.011537 | 0.10432 |  |  |  |  | 0.011537 | 0.10432 | 0.076914 | 0.69549 |  |  |  |  | 0.076914 | 0.69549 | 0.29073 | 2.6289 | [6 empty] | 0.29073 | 2.6289 | NOx control | Selective Catalytic Reduction | 2000-01-01 | Other control | Dry sorbent injection | 2001-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-04-01 | SO2 control | Wet FGD - Spray Type | 1994-12-01
coal | 2324 | Reid Gardner | NV | 3 | 3 | Conventional Boiler | Wall firing - front firing | 111 | 1237 | 11.1441 | coal - bituminous, other non-fossil fuel (specify) | [22 empty] | 0.00045233 | 0.0050409 | 0.00045233 | 0.0050409 | [14 empty] | 0.029267 | 0.32615 | 0.029267 | 0.32615 | PM control | Fabric Filter, pulse | 2009-02-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
coal | 2848 | O H Hutchings | OH | H-5 | H-5 | Conventional Boiler | Tangential firing | 63 | 641 | 10.1746 | coal - bituminous | [22 empty] | 0.009 | 0.091571 | 0.009 | 0.091571 | [14 empty] | 1.0933 | 11.1242 | 1.0933 | 11.1242 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
coal | 10343 | Foster Wheeler Mt Carmel Cogen | PA | SG-101 | SG-101 | Fluidized bed firing | Fluidized bed firing | 43 | 505 | 11.7442 | coal refuse (culm or gob) | [22 empty] | 0.017333 | 0.20357 | 0.017333 | 0.20357 | [10 empty] | 0.10864 | 1.2759 |  |  |  |  | 0.10864 | 1.2759 | PM control | Fabric Filter, reverse air | 1990-01-01
coal | 1218 | Fair Station | IA | U1 | 1 | Conventional Boiler | Wall firing - front firing | 24.5 | 330 | 13.4694 | coal - bituminous | [22 empty] | 0.033 | 0.44449 | 0.033 | 0.44449 | [14 empty] | 3.93 | 52.9347 | 3.93 | 52.9347 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
coal | 2384 | Deepwater | NJ | Coal-firing | 8 | Conventional Boiler | Wall firing - front firing | 87 | 820 | 9.4253 | [23 empty] | 0.10657 | 1.0045 | 0.10657 | 1.0045 | [18 empty] | Other control | Other (specify): Hydrated lime injection to control HCl | 2008-09-01 | NOx control | Selective Noncatalytic Reduction | 2008-09-01 | PM control | Fabric Filter, reverse air | 1981-01-01
coal | 2824 | Stanton | ND | u10 | 10 | Conventional Boiler | Tangential firing | 60 | 642 | 10.7 | coal - subbituminous | [40 empty] | 0.0076601 | 0.081963 | 0.0076601 | 0.081963 | SO2 control | Dry FGD - Spray Dryer | 2000-01-01 | PM control | Fabric Filter, reverse air | 2000-01-01
coal | 54238 | Port of Stockton District Energy Facility | CA | 1 | N64514 | Fluidized bed firing | Fluidized bed firing | 25 | 285 | 11.4 | coal - bituminous | [40 empty] | 0.008 | 0.0912 | 0.008 | 0.0912 | NOx control | Selective Noncatalytic Reduction | 1987-12-01 | PM control | Fabric Filter, shake and deflate | 1987-12-01
coal | 54238 | Port of Stockton District Energy Facility | CA | 1 | N64516 | Fluidized bed firing | Fluidized bed firing | 25 | 285 | 11.4 | coal - bituminous | [40 empty] | 0.008 | 0.0912 | 0.008 | 0.0912 | NOx control | Selective Noncatalytic Reduction | 1987-12-01 | PM control | Fabric Filter, shake and deflate | 1987-12-01
coal | 641 | Crist | FL | Unit 5 | 5 | Conventional Boiler | Tangential firing | 82 | 817.83 | 9.9735 | bituminous | [34 empty] | 0.025 | 0.24934 | [6 empty] | 0.025 | 0.24934 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
coal | 641 | Crist | FL | Unit 6 | 6 | Conventional Boiler | Wall firing - front firing | 320 | 3193.348 | 9.9792 | bituminous | [34 empty] | 0.025 | 0.24948 | [6 empty] | 0.025 | 0.24948 | NOx control | Selective Noncatalytic Reduction | 2005-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
coal | 641 | Crist | FL | Unit 7 | 7 | Conventional Boiler | Wall firing - front firing | 500 | 5279.792 | 10.5596 | bituminous | [34 empty] | 0.025 | 0.26399 | [6 empty] | 0.025 | 0.26399 | NOx control | Selective Catalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2004-04-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
coal | 641 | Crist | FL | Unit 4 | 4 | Conventional Boiler | Tangential firing | 82 | 868.842 | 10.5956 | bituminous | [34 empty] | 0.025 | 0.26489 | [6 empty] | 0.025 | 0.26489 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
coal | 10768 | Rio Bravo Jasmin | CA | Config 1 | S-1715-3-13 | Fluidized bed firing | Fluidized bed firing | 36 | 412.16 | 11.4489 | bituminous | [34 empty] | 0.023867 | 0.27325 |  |  |  |  | 0.0232 | 0.26561 | 0.0232 | 0.26561 | NOx control | Selective Noncatalytic Reduction | 1990-03-01 | PM control | Fabric Filter, reverse air | 1990-03-01
coal | 10769 | Rio Bravo Poso | CA | Config 1 | C-E CONTRACT 24687 | Fluidized bed firing | Fluidized bed firing | 36 | 407.93 | 11.3314 | bituminous | [34 empty] | 0.025033 | 0.28366 |  |  |  |  | 0.0245 | 0.27762 | 0.0245 | 0.27762 | NOx control | Selective Noncatalytic Reduction | 1990-03-01 | PM control | Fabric Filter, reverse air | 1990-03-01
coal | 10384 | Edgecombe Genco, LLC | NC | Gen 1 | 1A | Conventional Boiler | Stoker - overfeed | 30.5 | 375 | 12.2951 | bituminous | [34 empty] | 0.0278 | 0.3418 | [6 empty] | 0.0278 | 0.3418 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | PM control | Fabric Filter, reverse air | 1990-10-01 | PM control | Fabric Filter, pulse | 1990-10-01
coal | 10384 | Edgecombe Genco, LLC | NC | Gen 1 | 1B | Conventional Boiler | Stoker - overfeed | 30.5 | 375 | 12.2951 | bituminous | [34 empty] | 0.0278 | 0.3418 | [6 empty] | 0.0278 | 0.3418 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | PM control | Fabric Filter, reverse air | 1990-10-01 | PM control | Fabric Filter, pulse | 1990-10-01
coal | 10784 | Colstrip Energy LP | MT | Config1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 44 | 635 | 14.4318 | coal refuse (culm or gob) | [38 empty] | 0.031567 | 0.45556 |  |  | 0.031567 | 0.45556 | PM control | Fabric Filter, pulse | 1990-06-01 | Other control | Activated carbon injection | 2009-12-01
coal | 10002 | ACE Cogeneration Company | CA | Config 1 | 1 | Fluidized bed firing | Fluidized bed firing | 117 | 1052 | 8.9915 | bituminous | [34 empty] | 0.054567 | 0.49063 |  |  |  |  | 0.052 | 0.46756 | 0.052 | 0.46756 | NOx control | Selective Noncatalytic Reduction | 1991-01-01 | PM control | Fabric Filter, reverse air | 1991-01-01
coal | 113 | Cholla | AZ | 001 | 1 | Conventional Boiler | Tangential firing | 131 | 1270 | 9.6947 | [41 empty] | 0.05 | 0.48473 | 0.05 | 0.48473 | PM control | Fabric Filter, unspecified | 2007-01-01 | SO2 control | Wet FGD - Venturi Type | 1972-01-01
coal | 8223 | Springerville | AZ | 2 | 2 | Conventional Boiler | Tangential firing | 430 | 3830 | 8.907 | bituminous | [40 empty] | 0.056 | 0.49879 | 0.056 | 0.49879 | SO2 control | Dry FGD - Spray Dryer | 1990-06-01 | PM control | Fabric Filter, reverse air | 1990-06-01
coal | 7790 | Bonanza Power Plant | UT | 1-1 | 1-1 | Conventional Boiler | Wall firing - opposed firing | 483 | 4899 | 10.1429 | Bituminous | [40 empty] | 0.04943 | 0.50136 | 0.04943 | 0.50136 | PM control | Fabric Filter, reverse air | 1985-11-01 | SO2 control | Wet FGD - Spray Type | 1985-11-01
coal | 113 | Cholla | AZ | 002 | 2 | Conventional Boiler | Tangential firing | 305 | 2938 | 9.6328 | [41 empty] | 0.061 | 0.5876 | 0.061 | 0.5876 | PM control | PM scrubber - Venturi | 1978-01-01 | SO2 control | Wet FGD - Venturi Type | 1978-01-01
coal | 8 | Gorgas | AL | Unit 10 | 10 | Conventional Boiler | Tangential firing | 720 | 6523.794 | 9.0608 | coal - bituminous | [40 empty] | 0.065176 | 0.59055 | 0.065176 | 0.59055 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-10-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
coal | 8 | Gorgas | AL | Unit 8 | 8 | Conventional Boiler | Tangential firing | 175 | 1600.8973 | 9.148 | coal - bituminous | [40 empty] | 0.065176 | 0.59623 | 0.065176 | 0.59623 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
coal | 8 | Gorgas | AL | Unit 9 | 9 | Conventional Boiler | Tangential firing | 185 | 1738.6247 | 9.398 | coal - bituminous | [40 empty] | 0.065176 | 0.61252 | 0.065176 | 0.61252 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
coal | 2324 | Reid Gardner | NV | 4 | 4 | Conventional Boiler | Wall firing - front firing | 281 | 2956 | 10.5196 | [41 empty] | 0.0591 | 0.62171 | 0.0591 | 0.62171 | PM control | Fabric Filter, pulse | 1983-07-01 | SO2 control | Wet FGD - Venturi Type | 1983-07-01
coal | 8224 | North Valmy | NV | 2 | 2 | Conventional Boiler | Wall firing - front firing | 270.2 | 2881 | 10.6625 | [41 empty] | 0.058667 | 0.62553 | 0.058667 | 0.62553 | SO2 control | Dry FGD - Spray Dryer | 1985-05-01 | PM control | Fabric Filter, reverse air | 1985-05-01
coal | 1606 | Mount Tom | MA | 1 current | 1 | Conventional Boiler | Wall firing - front firing | 155 | 1480 | 9.5484 | coal - bituminous | [40 empty] | 0.066 | 0.63019 | 0.066 | 0.63019 | NOx control | Selective Catalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-09-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-12-01 | PM control | Fabric Filter, pulse | 2009-12-01
coal | 8223 | Springerville | AZ | 1 | 1 | Conventional Boiler | Tangential firing | 427 | 3830 | 8.9696 | coal - subbituminous | [40 empty] | 0.071 | 0.63684 | 0.071 | 0.63684 | SO2 control | Dry FGD - Spray Dryer | 1985-06-01 | PM control | Fabric Filter, reverse air | 1985-06-01
coal | 10384 | Edgecombe Genco, LLC | NC | Gen 2 | 2A | Conventional Boiler | Stoker - overfeed | 30.5 | 375 | 12.2951 | bituminous | 0.095137 | 0.0050961 | [32 empty] | 0.0568 | 0.69836 | [6 empty] | 0.0568 | 0.69836 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | PM control | Fabric Filter, reverse air | 1990-10-01 | PM control | Fabric Filter, reverse air | 1990-10-01
coal | 10384 | Edgecombe Genco, LLC | NC | Gen 2 | 2B | Conventional Boiler | Stoker - overfeed | 30.5 | 375 | 12.2951 | bituminous | 0.095137 | 0.0050961 | [32 empty] | 0.0568 | 0.69836 | [6 empty] | 0.0568 | 0.69836 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | SO2 control | Dry FGD - Spray Dryer | 1990-10-01 | PM control | Fabric Filter, reverse air | 1990-10-01 | PM control | Fabric Filter, reverse air | 1990-10-01
coal | 2324 | Reid Gardner | NV | 2 | 2 | Conventional Boiler | Wall firing - front firing | 111 | 1215 | 10.9459 | [41 empty] | 0.083 | 0.90851 | 0.083 | 0.90851 | PM control | Fabric Filter, pulse | 2009-04-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
coal | 160 | Apache Station | AZ | ST2 | 2 | Conventional Boiler | Turbo | 204 | 1932.521 | 9.4731 | coal - subbituminous | [40 empty] | 0.10257 | 0.97162 | 0.10257 | 0.97162 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1978-06-01
coal | 6041 | H L Spurlock Station | KY | Unit 01 | 1 | Conventional Boiler | Wall firing - opposed firing | 344 | 3641 | 10.5843 | bituminous | [34 empty] | 0.24907 | 2.6362 |  |  |  |  | 0.10867 | 1.1502 | 0.10867 | 1.1502 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2003-05-01 | NOx control | Selective Catalytic Reduction | 2003-05-01 | SO2 control | Wet FGD - Unspecified | 2009-04-01 | Other control | Wet electrostatic precipitator | 2009-04-01
coal | 160 | Apache Station | AZ | ST3 | 3 | Conventional Boiler | Turbo | 204 | 1932.521 | 9.4731 | coal - subbituminous | [40 empty] | 0.12491 | 1.1833 | 0.12491 | 1.1833 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1978-06-01
coal | 2832 | Miami Fort | OH | U8 | Unit 8 | Conventional Boiler | Wall firing - opposed firing | 550 | 5003 | 9.0964 | coal - bituminous | [40 empty] | 0.14467 | 1.3159 | 0.14467 | 1.3159 | NOx control | Selective Catalytic Reduction | 2001-01-01 | SO2 control | Wet FGD - Spray Type | 2007-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-02-01
coal | 127 | Oklaunion | TX | OKL-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 670 | 6800 | 10.1493 | subbituminous | [34 empty] | 0.1845 | 1.8725 | 0.13562 | 1.3764 |  |  |  |  | 0.13562 | 1.3764 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1986-01-01 | SO2 control | Wet FGD - Spray Type | 1986-12-01
coal | 6041 | H L Spurlock Station | KY | Unit 02 | 2 | Conventional Boiler | Tangential firing | 555 | 5600 | 10.0901 | bituminous | [34 empty] | 0.14053 | 1.418 | [6 empty] | 0.14053 | 1.418 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1981-02-01 | NOx control | Selective Catalytic Reduction | 2002-05-01 | SO2 control | Wet FGD - Unspecified | 2008-10-01 | Other control | Wet electrostatic precipitator | 2008-10-01
coal | 2832 | Miami Fort | OH | U7 | Unit 7 | Conventional Boiler | Wall firing - opposed firing | 550 | 4995 | 9.0818 | coal - bituminous | [40 empty] | 0.15767 | 1.4319 | 0.15767 | 1.4319 | NOx control | Selective Catalytic Reduction | 2007-01-01 | SO2 control | Wet FGD - Spray Type | 2007-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-05-01
coal | 645 | Big Bend | FL | BB03_SCR_iso | 3 | Conventional Boiler | Wall firing - opposed firing | 400 | 4115 | 10.2875 | coal - bituminous, petroleum coke | [40 empty] | 0.16233 | 1.67 | 0.16233 | 1.67 | NOx control | Selective Catalytic Reduction | 2008-07-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1976-05-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
coal | 207 | St Johns River Power Park | FL | PPUnit2Configuration | PPBoiler2 | Conventional Boiler | Wall firing - opposed firing | 660 | 6144 | 9.3091 | bituminous | [34 empty] | 0.207 | 1.927 | [6 empty] | 0.207 | 1.927 | NOx control | Selective Catalytic Reduction | 2009-03-01 | NOx control | Other (specify): Ammonia Injection for SO3 Mitigation | 2009-03-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1986-12-01 | SO2 control | Wet FGD - Spray/Tray Type | 1988-03-01 | SO2 control | Wet FGD - Spray Type | 1988-03-01
coal | 207 | St Johns River Power Park | FL | PPUnit1Configuration | PPBoiler1 | Conventional Boiler | Wall firing - opposed firing | 660 | 6144 | 9.3091 | bituminous | [34 empty] | 0.21052 | 1.9597 | [6 empty] | 0.21052 | 1.9597 | NOx control | Selective Catalytic Reduction | 2009-07-01 | NOx control | Other (specify): Ammonia Injection for SO3 Mitigation | 2009-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1988-03-01 | SO2 control | Wet FGD - Spray/Tray Type | 1986-12-01 | SO2 control | Wet FGD - Spray Type | 1986-12-01
coal | 10675 | AES Thames | CT | B | B | Fluidized bed firing | Fluidized bed firing | 104 | 1002 | 9.6346 | bituminous | [34 empty] | 0.25287 | 2.4363 |  |  |  |  | 0.29 | 2.794 | 0.25287 | 2.4363 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1990-03-01 | PM control | Fabric Filter, pulse | 1990-03-01
coal | 10675 | AES Thames | CT | A | A | Fluidized bed firing | Fluidized bed firing | 104 | 1002 | 9.6346 | bituminous | [34 empty] | 0.2576 | 2.4819 |  |  |  |  | 0.29 | 2.794 | 0.2576 | 2.4819 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1990-03-01 | PM control | Fabric Filter, pulse | 1990-03-01
coal | 645 | Big Bend | FL | BB04_SCR_iso | 4 | Conventional Boiler | Tangential firing | 465 | 4330 | 9.3118 | coal - bituminous, other fossil fuel (specify) | [40 empty] | 0.30395 | 2.8303 | 0.30395 | 2.8303 | NOx control | Selective Catalytic Reduction | 2007-06-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1985-02-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
coal | 3788 | Potomac River | VA | 5 | 5 | Conventional Boiler | Tangential firing | 108 | 961 | 8.8981 | coal - bituminous | [40 empty] | 0.32 | 2.8474 | 0.32 | 2.8474 | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1957-05-01
coal | 50611 | WPS Westwood Generation, LLC | PA | 001 | 031 | Fluidized bed firing | Fluidized bed firing | 36 | 615 | 17.0833 | coal refuse (culm or gob) | [34 empty] | 0.16833 | 2.8757 | [6 empty] | 0.16833 | 2.8757 | PM control | Fabric Filter, pulse | 1987-12-01
coal | 6177 | Coronado Generating Station | AZ | U2B | U2B | Conventional Boiler | Wall firing - unspecified | 456.6 | 4719 | 10.3351 | [41 empty] | 0.28 | 2.8938 | 0.28 | 2.8938 | PM control | Electrostatic precipitator, hot side, unspecified | 1980-10-01
coal | 6177 | Coronado Generating Station | AZ | U1B | U1B | Conventional Boiler | Wall firing - unspecified | 456.6 | 4719 | 10.3351 | [41 empty] | 0.29 | 2.9972 | 0.29 | 2.9972 | PM control | Electrostatic precipitator, hot side, unspecified | 1979-12-01
coal | 6085 | R.M. Schahfer | IN | R.M.0018 | 18 | Conventional Boiler | Tangential firing | 393 | 3967 | 10.0941 | bituminous | [36 empty] | 0.31636 | 3.1934 |  |  |  |  | 0.31636 | 3.1934 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1986-01-01 | SO2 control | Wet FGD - Spray Type | 1986-02-01
coal | 3136 | Keystone | PA | KEY-2-4 | 2 | Conventional Boiler | Tangential firing | 936 | 8695 | 9.2895 | coal - bituminous | [40 empty] | 0.39333 | 3.6539 | 0.39333 | 3.6539 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-04-01 | SO2 control | Wet FGD - Spray Type | 2009-11-01
coal | 50039 | Kline Township Cogen Facility | PA | 001 | 001 | Fluidized bed firing | Fluidized bed firing | 58 | 825 | 14.2241 | coal refuse (culm or gob) | [36 empty] | 0.25913 | 3.6858 |  |  |  |  | 0.25913 | 3.6858 | PM control | Fabric Filter, unspecified
coal | 3136 | Keystone | PA | KEY-1-4 | 1 | Conventional Boiler | Tangential firing | 936 | 8695 | 9.2895 | coal - bituminous | [40 empty] | 0.42017 | 3.9032 | 0.42017 | 3.9032 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-04-01 | SO2 control | Wet FGD - Spray Type | 2009-09-01
coal | 10113 | John B Rich Memorial Power Station | PA | CFB1 | CFB1 | Fluidized bed firing | Fluidized bed firing | 44 | 520 | 11.8182 | coal refuse (culm or gob) | [36 empty] | 0.34643 | 4.0942 |  |  |  |  | 0.34643 | 4.0942 | PM control | Fabric Filter, pulse
coal | 10113 | John B Rich Memorial Power Station | PA | CFB2 | CFB2 | Fluidized bed firing | Fluidized bed firing | 44 | 520 | 11.8182 | coal refuse (culm or gob) | [36 empty] | 0.34643 | 4.0942 |  |  |  |  | 0.34643 | 4.0942 | PM control | Fabric Filter, pulse
coal | 10641 | Cambria Cogen | PA | 001 | B1 | Fluidized bed firing | Fluidized bed firing | 49 | 560 | 11.4286 | coal refuse (culm or gob), other--natural gas | 0.07479 | 0.01679 | [34 empty] | 0.37533 | 4.2894 |  |  |  |  | 0.37533 | 4.2894 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
coal | 891 | Havana | IL | Boiler 9 | Boiler 9 | Conventional Boiler | Wall firing - unspecified | 481 | 5030 | 10.4574 | bituminous | 0.00092571 | 0.0058061 | [32 empty] | 0.43072 | 4.5042 | [6 empty] | 0.43072 | 4.5042 | PM control | Electrostatic precipitator, hot side, unspecified | 1978-04-01 | NOx control | Selective Catalytic Reduction | 2003-08-01 | Other control | Activated carbon injection | 2009-07-01 | SO2 control | Dry FGD - Spray Dryer |  | PM control | Fabric Filter, unspecified | 2009-06-01
coal | 884 | Will County | IL | WC4CONFIG | 4 | Conventional Boiler | Tangential firing | 542 | 5254.53 | 9.6947 | subbituminous | [34 empty] | 0.4775 | 4.6292 | [6 empty] | 0.4775 | 4.6292 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1963-06-01
coal | 10641 | Cambria Cogen | PA | 002 | B2 | Fluidized bed firing | Fluidized bed firing | 49 | 560 | 11.4286 | coal refuse (culm or gob), other--natural gas | 0.11888 | 0.018212 | [34 empty] | 0.44678 | 5.106 |  |  |  |  | 0.44678 | 5.106 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
coal | 2963 | Northeastern | OK | NE-3 | 3313 | Conventional Boiler | Tangential firing | 490 | 4775 | 9.7449 | subbituminous | [34 empty] | 0.52496 | 5.1157 | [6 empty] | 0.52496 | 5.1157 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
coal | 2824 | Stanton | ND | u1 | 1 | Conventional Boiler | Wall firing - front firing | 132 | 1800 | 13.6364 | subbituminous | [40 empty] | 0.37624 | 5.1306 | 0.37624 | 5.1306 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-01-01
coal | 4078 | Weston | WI | W3 | 3 | Conventional Boiler | Tangential firing | 365.6 | 3423.48 | 9.364 | subbituminous | [34 empty] | 0.56487 | 5.2894 | [6 empty] | 0.56487 | 5.2894 | PM control | Fabric Filter, pulse | 2001-05-01 | Other control | Activated carbon injection
coal | 6166 | Rockport | IN | RP-2 | MB2 | Conventional Boiler | Wall firing - opposed firing | 1320 | 12374 | 9.3742 | subbituminous | [34 empty] | 0.57263 | 5.368 | [6 empty] | 0.57263 | 5.368 | Other control | Activated carbon injection | 2009-09-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1989-12-01
coal | 6073 | Victor J. Daniel Jr | MS | Unit 1 | 1 | Conventional Boiler | Tangential firing | 537 | 5206.306 | 9.6952 | coal - subbituminous, coal - bituminous | [40 empty] | 0.608 | 5.8947 | 0.608 | 5.8947 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01
coal | 2049 | Jack Watson | MS | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 250 | 2226.86 | 8.9074 | coal - bituminous | [40 empty] | 0.779 | 6.9389 | 0.779 | 6.9389 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-07-01
coal | 8224 | North Valmy | NV | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 243.5 | 2560 | 10.5133 | [41 empty] | 0.67 | 7.0439 | 0.67 | 7.0439 | PM control | Fabric Filter, reverse air | 1981-12-01
coal | 6073 | Victor J. Daniel Jr | MS | Unit 2 | 2 | Conventional Boiler | Tangential firing | 536 | 5166.728 | 9.6394 | coal - subbituminous, coal - bituminous | [40 empty] | 0.74 | 7.1332 | 0.74 | 7.1332 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01
coal | 2049 | Jack Watson | MS | Unit 5 | 5 | Conventional Boiler | Wall firing - front firing | 500 | 4752.86 | 9.5057 | coal - bituminous | [40 empty] | 0.8786 | 8.3517 | 0.8786 | 8.3517 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1973-05-01
coal | 2480 | Danskammer Generating Station | NY | 3 | 3 | Conventional Boiler | Tangential firing | 144.9 | 1365 | 9.4203 | bituminous | [36 empty] | 0.96577 | 9.0979 |  |  |  |  | 0.96577 | 9.0979 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1987-09-01
coal | 2480 | Danskammer Generating Station | NY | 4 | 4 | Conventional Boiler | Tangential firing | 242.3 | 2535 | 10.4622 | bituminous | [36 empty] | 0.94266 | 9.8624 |  |  |  |  | 0.94266 | 9.8624 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1987-09-01
coal | 663 | Deerhaven Generating Station | FL | 001 | B-2 | Conventional Boiler | Wall firing - unspecified | 235 | 2428 | 10.3319 | [41 empty] | 1.04 | 10.7452 | 1.04 | 10.7452 | PM control | Electrostatic precipitator, hot side, unspecified | 1987-10-01 | NOx control | Selective Catalytic Reduction | 2009-05-01 | SO2 control | Dry FGD - Unspecified | 2009-05-01
coal | 2848 | O H Hutchings | OH | H-1 | H-1 | Conventional Boiler | Tangential firing | 53 | 607 | 11.4528 | coal - bituminous | [40 empty] | 1.05 | 12.0255 | 1.05 | 12.0255 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
coal | 2848 | O H Hutchings | OH | H-3 | H-3 | Conventional Boiler | Tangential firing | 62.5 | 716 | 11.456 | coal - bituminous | [40 empty] | 1.0767 | 12.3343 | 1.0767 | 12.3343 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
coal | 2848 | O H Hutchings | OH | H-2 | H-2 | Conventional Boiler | Tangential firing | 53 | 574 | 10.8302 | coal - bituminous | [40 empty] | 1.1633 | 12.5991 | 1.1633 | 12.5991 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
coal | 2848 | O H Hutchings | OH | H-6 | H-6 | Conventional Boiler | Tangential firing | 60.5 | 646 | 10.6777 | coal - bituminous | [40 empty] | 1.23 | 13.1336 | 1.23 | 13.1336 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
coal | 2848 | O H Hutchings | OH | H-4 | H-4 | Conventional Boiler | Tangential firing | 64 | 696 | 10.875 | coal - bituminous | [40 empty] | 1.23 | 13.3763 | 1.23 | 13.3763 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
coal | 6648 | Sandow No 4 | TX | 4 | 4 | Conventional Boiler | Tangential firing | 568 | 7810 | 13.75 | coal - lignite | [40 empty] | 1.008 | 13.8605 | 1.008 | 13.8605 | NOx control | Selective Catalytic Reduction |  | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-05-01 | SO2 control | Wet FGD - Spray Type | 1981-05-01
coal | 3947 | Kammer | WV | K-1 | 1 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | 9.0779 | bituminous | [34 empty] | 2.0177 | 18.3168 | [6 empty] | 2.0177 | 18.3168 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-08-01
coal | 3947 | Kammer | WV | K-3 | 3 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | 9.0779 | bituminous | [34 empty] | 2.0177 | 18.3168 | [6 empty] | 2.0177 | 18.3168 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-04-01
coal | 2364 | Merrimack Station | NH | mk2 | 2 | Conventional Boiler | Cyclone firing | 337 | 3017 | 8.9525 | bituminous | [34 empty] | 2.1748 | 19.4699 | [6 empty] | 2.1748 | 19.4699 | NOx control | Selective Catalytic Reduction | 1995-05-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1999-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-05-01
coal | 1217 | Earl F Wisdom | IA | 1 | 1 | Conventional Boiler | Wall firing - front firing | 40 | 477 | 11.925 | coal - bituminous | [40 empty] | 2.1 | 25.0425 | 2.1 | 25.0425 | PM control | Multiple cyclone | 1960-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-07-01
Note on AS129: stboone: suspect data removed and Part III data subsituted,

## HF_Avg_MMBtu
Emissions (lb/MMBtu)
| Seward | Seward | Logan Generating Plant | Chambers Cogeneration LP | Red Hills Generating Facility | Red Hills Generating Facility | Chambers Cogeneration LP | Sandow Station | Duck Creek | Laramie River Station | H L Spurlock Station | TS Power Plant | Walter Scott Jr. Energy Center | Roxboro Steam Electric Plant | Hammond | Hammond | Hammond | Hammond | Sandow Station | Hatfield's Ferry Power Station | HOLCOMB | Hardin Generator Project | Bowen | Rawhide | Weston | Cross | Spruance Genco, LLC | Spruance Genco, LLC | Cross | Bowen | Navajo Generating Station | J K Spruce | Navajo Generating Station | Asheville Steam Electric Plant | Cedar Bay Generating Company L.P. | INDIANTOWN COGENERATION L.P. | Cedar Bay Generating Company L.P. | Morgantown Energy Facility | Morgantown Energy Facility | Cedar Bay Generating Company L.P. | Gibson | AES Warrior Run Cogeneration Facility | H L Spurlock Station | Elm Road Generating Station | Bowen | Navajo Generating Station | BL England | Pleasant Prairie | Roanoke Valley II | AES Hawaii | Hayden | Birchwood Power Facility | Springerville | Conesville | Roanoke Valley I | Harrison Power Station | Wansley | Dallman | Valmont | Hayden | Mitchell Power Station | Hawthorn | Pleasant Prairie | John E. Amos | AES Hawaii | Cardinal | Cholla | Ghent | Stanton Energy Center | John E. Amos | Cardinal | Cholla | AES Cayuga, LLC | Conemaugh | Big Bend | Big Bend | Wansley | Spruance Genco, LLC | Spruance Genco, LLC | Oak Grove | Conemaugh | Marion Generating Station | AES Puerto Rico Cogeneration Facility | Elrama Power Plant | Elrama Power Plant | Elrama Power Plant | Elrama Power Plant | Springerville | Ebensburg Power Company | AES Puerto Rico Cogeneration Facility | AES Cayuga, LLC | Hamilton | San Juan | San Juan | Sunnyside Cogen Associates | AES Petersburg | Bailly | Bailly | Harding Street | R D Green | Mecklenburg Power Station | Mecklenburg Power Station | Cross | Harrison Power Station | Yates | Cherokee | Harrison Power Station | Asheville Steam Electric Plant | Welsh | Cumberland | Colstrip | Walter Scott Jr. Energy Center | Cumberland | Hopewell | Hopewell | Ghent | Nearman Creek | Cherokee | Southampton Power Station | Southampton Power Station | Nebraska City | W H Zimmer | Ghent | AES Petersburg | Lamar Plant | Clover | Marshall | Marshall | East Bend Station | Marshall
ORIS/Facility/Unit | 3130 | 3130 | 10043 | 10566 | 55076 | 55076 | 10566 | 52071 | 6016 | 6204 | 6041 | 56224 | 1082 | 2712 | 708 | 708 | 708 | 708 | 52071 | 3179 | 108 | 55749 | 703 | 6761 | 4078 | 130 | 54081 | 54081 | 130 | 703 | 4941 | 7097 | 4941 | 2706 | 10672 | 50976 | 10672 | 10743 | 10743 | 10672 | 6113 | 10678 | 6041 | 56068 | 703 | 4941 | 2378 | 6170 | 54755 | 10673 | 525 | 54304 | 8223 | 2840 | 54035 | 3944 | 6052 | 963 | 477 | 525 | 3181 | 2079 | 6170 | 3935 | 10673 | 2828 | 113 | 1356 | 564 | 3935 | 2828 | 113 | 2535 | 3118 | 645 | 645 | 6052 | 54081 | 54081 | 6180 | 3118 | 976 | 68029 | 3098 | 3098 | 3098 | 3098 | 8223 | 10603 | 68029 | 2535 | 2917 | 2451 | 2451 | 50951 | 994 | 995 | 995 | 990 | 6639 | 52007 | 52007 | 130 | 3944 | 728 | 469 | 3944 | 2706 | 6139 | 3399 | 6076 | 1082 | 3399 | 10771 | 10771 | 1356 | 6064 | 469 | 10774 | 10774 | 6096 | 6019 | 1356 | 994 | 508 | 7213 | 2727 | 2727 | 6018 | 2727
Test Averages | 1 | 2 | B01 | Boil 1 | AA-002 | AA-001 | Boil 2 | 5B | 1 | 3 | 4 | BLR100 | 4 | 2 | 2 | 3 | 1 | 4 | 5A | 1 | SGU1 | PC1 | 2 | 101 | 4 | 4 | 3A | 3B | 3 | 3 | 1 | BLR1 | 2 | 1 | CBC | AABO1 | CBA | CFB1 | CFB2 | CBB | 4 | BLR1 | 3 | 1 | 4 | 3 | 2 | 1 | BLR2 | BLR A | 2 | 1A | 3 | 4 | BLR1 | 1 | 2 | 34 | 5 | 1 | 33 | 5A | 2 | 3 | BLR B | 2 | 3 | 1 | 2 | 2 | 1 | 4 | 2 | 2 | 1 | 2 | 1 | 1A | 1B | 1 | 1 | 123 | BLR2 | 4 | 3 | 1 | 2 | 4 | 31 | BLR1 | 1 | 9 | Unit 3 | Unit 4 | 1 | 2 | 7 | 8 | 70 | G2 | BLR1 | BLR2 | 1 | 3 | Y1BR | 4 | 2 | 2 | 1 | 2 | 3 | 3 | 1 | 10771-01 | 10771-02 | 3 | N1 | 3 | 1 | 2 | NC2 | 1 | 4 | 1 | 001 | Unit 1 | U4 | U3 | 2 | U1
1 | 5.6867e-06 | 5.6867e-06 | 6.737e-06 | 7.3682e-06 | 8.7975e-06 | 8.7975e-06 | 9.2489e-06 | 9.5233e-06 | 9.74e-06 | 1.1327e-05 | 1.3333e-05 | 1.5011e-05 | 1.5307e-05 | 2.117e-05 | 2.1654e-05 | 2.1654e-05 | 2.1654e-05 | 2.1654e-05 | 2.241e-05 | 2.47e-05 | 2.8e-05 | 2.8873e-05 | 2.9983e-05 | 3e-05 | 3.1e-05 | 3.26e-05 | 3.532e-05 | 3.532e-05 | 4.1533e-05 | 4.4955e-05 | 4.9105e-05 | 4.9757e-05 | 5e-05 | 5.01e-05 | 5.0206e-05 | 5.0377e-05 | 5.2e-05 | 5.2633e-05 | 5.2633e-05 | 5.4333e-05 | 5.6145e-05 | 5.623e-05 | 5.6667e-05 | 5.7206e-05 | 5.7474e-05 | 5.7895e-05 | 5.9506e-05 | 5.9544e-05 | 6.0043e-05 | 6.2111e-05 | 6.2331e-05 | 6.3333e-05 | 6.4e-05 | 6.5255e-05 | 6.5791e-05 | 6.5821e-05 | 6.6759e-05 | 6.7e-05 | 7.246e-05 | 7.315e-05 | 7.3553e-05 | 7.3847e-05 | 7.6263e-05 | 7.7926e-05 | 7.8954e-05 | 8.1572e-05 | 8.2224e-05 | 8.39e-05 | 8.4724e-05 | 8.4782e-05 | 8.6175e-05 | 8.7302e-05 | 8.7624e-05 | 8.913e-05 | 8.9805e-05 | 9.1702e-05 | 9.181e-05 | 9.3168e-05 | 9.3168e-05 | 9.3473e-05 | 9.451e-05 | 9.7766e-05 | 9.8457e-05 | 9.9974e-05 | 9.9974e-05 | 9.9974e-05 | 9.9974e-05 | 0.0001 | 0.0001 | 0.00010252 | 0.00010627 | 0.00010963 | 0.0001111 | 0.00011285 | 0.00011316 | 0.00011555 | 0.00011799 | 0.00011799 | 0.00011806 | 0.00011813 | 0.0001202 | 0.0001202 | 0.00012186 | 0.00012657 | 0.00012767 | 0.00012964 | 0.00012983 | 0.00013533 | 0.00013661 | 0.00013823 | 0.00014115 | 0.000142 | 0.00014362 | 0.00014608 | 0.00014608 | 0.00014621 | 0.00014667 | 0.00014827 | 0.00014995 | 0.00014995 | 0.00015207 | 0.00015864 | 0.0001689 | 0.00016914 | 0.0001694 | 0.00017153 | 0.00017169 | 0.00017206 | 0.00017505 | 0.00017508
2 | 0.00020526 | 0.00020526 | 6.9115e-06 | 1.836e-05 | 0.00015 | 0.00015 |  | 4.4525e-05 | 0.00045197 |  | 4.8516e-05 | 6.5139e-05 | 2.9e-05 | [5 empty] | 9.4701e-05 | 7.7176e-05 |  | 5e-05 |  | 3e-05 |  | 0.00010289 |  |  | 6.7011e-05 |  | 5e-05 | 0.00015333 | 5.2386e-05 | 6.2577e-05 | 5.0333e-05 | 9.4655e-05 | 5.4742e-05 | 0.00010482 | 0.00010482 | 5.5154e-05 | 0.00015811 |  | 5.7403e-05 |  |  | 6e-05 | 0.0001 | [5 empty] | 0.00020733 |  |  |  |  | 6.9e-05 | [15 empty] | 0.00046667 | [5 empty] | 0.00014 | 0.00017 | [6 empty] | 0.000252 | [12 empty] | 0.00012247 | 0.00012247
3 |  |  | 8.3606e-06 | [7 empty] | 6.6663e-05 | 0.00021433 | 0.000108 | [10 empty] | 4.6491e-05 | [10 empty] | 7e-05 |  | 6e-05 |  |  | 5.9333e-05 | [6 empty] | 0.00018472 | [10 empty] | 9.4e-05
4 |  |  | 1.4471e-05 | [7 empty] | 0.0001 | [12 empty] | 6.75e-05 | [22 empty] | 0.00018848
5 |  |  | 2.3254e-05 | [20 empty] | 7.9544e-05
6 |  |  | 9.1535e-05 | [20 empty] | 0.00015
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 2 | 2 | 6 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 6 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 3 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 2 | 1 | 1 | 2 | 4 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Outlier Emission Averages Removed:
Total number of values used to calculate mean on row 65 |  | 130 |  | = n for existing sources in Term 1 on row 79
n =Total # test runs = |  | 187 |  | = n for new sources in Term 1 | ; = number of data points in s^2 calculation; also, this number minus 1 is the value used to calculate the t-statistic | [10 empty] | UPL Pooled Variance=
|  | 186 |  | (this value is used to determine the t-statistic on row 95)
This step is for QC only:
means | 5.6867e-06 | 5.6867e-06 | 6.737e-06 | 7.3682e-06 | 8.7975e-06 | 8.7975e-06 | 9.2489e-06 | 9.5233e-06 | 9.74e-06 | 1.1327e-05 | 1.3333e-05 | 1.5011e-05 | 1.5307e-05 | 2.117e-05 | 2.1654e-05 | 2.1654e-05 | 2.1654e-05 | 2.1654e-05 | 2.241e-05 | 2.47e-05 | 2.8e-05 | 2.8873e-05 | 2.9983e-05 | 3e-05 | 3.1e-05 | 3.26e-05 | 3.532e-05 | 3.532e-05 | 4.1533e-05 | 4.4955e-05 | 4.9105e-05 | 4.9757e-05 | 5e-05 | 5.01e-05 | 5.0206e-05 | 5.0377e-05 | 5.2e-05 | 5.2633e-05 | 5.2633e-05 | 5.4333e-05 | 5.6145e-05 | 5.623e-05 | 5.6667e-05 | 5.7206e-05 | 5.7474e-05 | 5.7895e-05 | 5.9506e-05 | 5.9544e-05 | 6.0043e-05 | 6.2111e-05 | 6.2331e-05 | 6.3333e-05 | 6.4e-05 | 6.5255e-05 | 6.5791e-05 | 6.5821e-05 | 6.6759e-05 | 6.7e-05 | 7.246e-05 | 7.315e-05 | 7.3553e-05 | 7.3847e-05 | 7.6263e-05 | 7.7926e-05 | 7.8954e-05 | 8.1572e-05 | 8.2224e-05 | 8.39e-05 | 8.4724e-05 | 8.4782e-05 | 8.6175e-05 | 8.7302e-05 | 8.7624e-05 | 8.913e-05 | 8.9805e-05 | 9.1702e-05 | 9.181e-05 | 9.3168e-05 | 9.3168e-05 | 9.3473e-05 | 9.451e-05 | 9.7766e-05 | 9.8457e-05 | 9.9974e-05 | 9.9974e-05 | 9.9974e-05 | 9.9974e-05 | 0.0001 | 0.0001 | 0.00010252 | 0.00010627 | 0.00010963 | 0.0001111 | 0.00011285 | 0.00011316 | 0.00011555 | 0.00011799 | 0.00011799 | 0.00011806 | 0.00011813 | 0.0001202 | 0.0001202 | 0.00012186 | 0.00012657 | 0.00012767 | 0.00012964 | 0.00012983 | 0.00013533 | 0.00013661 | 0.00013823 | 0.00014115 | 0.000142 | 0.00014362 | 0.00014608 | 0.00014608 | 0.00014621 | 0.00014667 | 0.00014827 | 0.00014995 | 0.00014995 | 0.00015207 | 0.00015864 | 0.0001689 | 0.00016914 | 0.0001694 | 0.00017153 | 0.00017169 | 0.00017206 | 0.00017505 | 0.00017508
8.1873e-05
UPL Mean = | [6 empty] | Distribution of Normal Tests | Distribution of Log Tests
[6 empty] | Skewness = | 0.20301 | #DIV/0!
[6 empty] | SE Skewness | 0.21483 | #DIV/0!
Pooled Variance = |  | 4.0821e-09 |  |  |  | Skewness Test | normal | #DIV/0!
[6 empty] | Kurtosis = | -0.88646 | #DIV/0!
[6 empty] | SE Kurtosis | 0.42967 | #DIV/0!
[6 empty] | Kurtosis Test | normal | #DIV/0!
[6 empty] | Number of test runs = | 130 | 0 | Result: | normal
m= number future runs = |  | 1
Term1 |  | 1.0077
Term2 |  | 4.1135e-09
Squared root Term2 |  | 6.4136e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 2.3466 |  | (the t-statistic should be calculated with the one less data point than the data set used for calculation of s^2.)
UPL POOLED VARIANCE = |  | 0.00023237 | lb/MMBtu
HF | 3xRDL, 4dscm sample volume | 0.0004 | lb/MMBtu
| Floor Value | 0.0004 | lb/MMBtu
Tukey's Exploratory Data Analysis Model
5.0025e-05 | 25th Percentile
0.00011799 | 75th Percentile
6.7963e-05 | IQR
Gross Outlier Test
Far Outlier Test (low)
Far Outlier Test (high)
Near Outlier Test (low)
Near Outlier Test (high)
Note on A113: Evaluates multiple test averages for a source and flags if max test average is >100x larger than Min test avg.
Note on A114: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A115: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A116: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.
Note on A117: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.

## HF_New_MMBtu
Emissions (lb/MMBtu)
Seward
ORIS/Facility/Unit | 3130
Runs | 1
1 | 5.48e-06 | BDL
2 | 5.75e-06 | BDL
3 | 5.83e-06 | BDL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3
2
This step is for QC only:
means | 5.6867e-06
5.6867e-06
UPL Mean =
Pooled Variance = |  | 3.3633e-14
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 2.2422e-14
Squared root Term2 |  | 1.4974e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 6.7295e-06 | lb/MMBtu
HF | 3xRDL, 4dscm sample volume | 0.0004 | lb/MMBtu
| Floor Value | 0.0004 | lb/MMBtu

## HF_Avg_MW
Emissions (lb/MW)
| Logan Generating Plant | Seward | Seward | Chambers Cogeneration LP | Red Hills Generating Facility | Red Hills Generating Facility | Chambers Cogeneration LP | Sandow Station | Duck Creek | Laramie River Station | H L Spurlock Station | TS Power Plant | Walter Scott Jr. Energy Center | Roxboro Steam Electric Plant | Hammond | Hammond | Hammond | Hammond | Sandow Station | Hatfield's Ferry Power Station | HOLCOMB | Rawhide | Weston | Bowen | Hardin Generator Project | Cross | Bowen | Cross | Navajo Generating Station | Navajo Generating Station | Spruance Genco, LLC | Spruance Genco, LLC | Asheville Steam Electric Plant | H L Spurlock Station | INDIANTOWN COGENERATION L.P. | Navajo Generating Station | Gibson | J K Spruce | Bowen | Harrison Power Station | Elm Road Generating Station | Dallman | BL England | AES Warrior Run Cogeneration Facility | Cedar Bay Generating Company L.P. | Pleasant Prairie | Hayden | Springerville | Cedar Bay Generating Company L.P. | Roanoke Valley I | Conesville | Wansley | AES Hawaii | Cedar Bay Generating Company L.P. | Mitchell Power Station | Birchwood Power Facility | Roanoke Valley II | Valmont | Lamar Plant | Cardinal | Hayden | John E. Amos | John E. Amos | AES Hawaii | Cardinal | AES Cayuga, LLC | Pleasant Prairie | Stanton Energy Center | Cholla | Hawthorn | Morgantown Energy Facility | Morgantown Energy Facility | Wansley | Conemaugh | Cholla | Big Bend | Big Bend | Conemaugh | Springerville | AES Cayuga, LLC | AES Puerto Rico Cogeneration Facility | AES Puerto Rico Cogeneration Facility | Ghent | Marion Generating Station | Oak Grove | Elrama Power Plant | Elrama Power Plant | Harding Street | Harrison Power Station | AES Petersburg | Bailly | Bailly | Harrison Power Station | San Juan | San Juan | Cherokee | Spruance Genco, LLC | Spruance Genco, LLC | Elrama Power Plant | Elrama Power Plant | Asheville Steam Electric Plant | Welsh | Cross | Yates | Sunnyside Cogen Associates | Colstrip | R D Green | Nearman Creek | W H Zimmer | Walter Scott Jr. Energy Center | Ebensburg Power Company | Mecklenburg Power Station | Mecklenburg Power Station | AES Petersburg | Marshall | Marshall | Cumberland | Nebraska City | Cumberland | Hamilton | Marshall | Marshall | Ghent | Cherokee | Eddystone Generating Station | East Bend Station | Urquhart | Hopewell | Hopewell | Mountaineer
ORIS/Facility/Unit | 10043 | 3130 | 3130 | 10566 | 55076 | 55076 | 10566 | 52071 | 6016 | 6204 | 6041 | 56224 | 1082 | 2712 | 708 | 708 | 708 | 708 | 52071 | 3179 | 108 | 6761 | 4078 | 703 | 55749 | 130 | 703 | 130 | 4941 | 4941 | 54081 | 54081 | 2706 | 6041 | 50976 | 4941 | 6113 | 7097 | 703 | 3944 | 56068 | 963 | 2378 | 10678 | 10672 | 6170 | 525 | 8223 | 10672 | 54035 | 2840 | 6052 | 10673 | 10672 | 3181 | 54304 | 54755 | 477 | 508 | 2828 | 525 | 3935 | 3935 | 10673 | 2828 | 2535 | 6170 | 564 | 113 | 2079 | 10743 | 10743 | 6052 | 3118 | 113 | 645 | 645 | 3118 | 8223 | 2535 | 68029 | 68029 | 1356 | 976 | 6180 | 3098 | 3098 | 990 | 3944 | 994 | 995 | 995 | 3944 | 2451 | 2451 | 469 | 54081 | 54081 | 3098 | 3098 | 2706 | 6139 | 130 | 728 | 50951 | 6076 | 6639 | 6064 | 6019 | 1082 | 10603 | 52007 | 52007 | 994 | 2727 | 2727 | 3399 | 6096 | 3399 | 2917 | 2727 | 2727 | 1356 | 469 | 3161 | 6018 | 3295 | 10771 | 10771 | 6264
Test Averages | B01 | 1 | 2 | Boil 1 | AA-002 | AA-001 | Boil 2 | 5B | 1 | 3 | 4 | BLR100 | 4 | 2 | 2 | 3 | 1 | 4 | 5A | 1 | SGU1 | 101 | 4 | 2 | PC1 | 4 | 3 | 3 | 1 | 2 | 3A | 3B | 1 | 3 | AABO1 | 3 | 4 | BLR1 | 4 | 1 | 1 | 34 | 2 | BLR1 | CBC | 1 | 2 | 3 | CBA | BLR1 | 4 | 2 | BLR A | CBB | 33 | 1A | BLR2 | 5 | 4 | 2 | 1 | 3 | 2 | BLR B | 1 | 2 | 2 | 2 | 3 | 5A | CFB1 | CFB2 | 1 | 2 | 4 | 1 | 2 | 1 | 4 | 1 | BLR2 | BLR1 | 1 | 123 | 1 | 4 | 3 | 70 | 3 | 2 | 7 | 8 | 2 | Unit 4 | Unit 3 | 4 | 1A | 1B | 1 | 2 | 2 | 1 | 1 | Y1BR | 1 | 3 | G2 | N1 | 1 | 3 | 31 | BLR1 | BLR2 | 1 | Unit 4 | Unit 3 | 2 | NC2 | 1 | 9 | Unit 1 | Unit 2 | 3 | 3 | 2 | 2 | URQ003 | 1 & 2 | 1 & 2 | Mt-1
1 | 5.898e-05 | 6.0269e-05 | 6.0269e-05 | 7.1717e-05 | 8.3833e-05 | 8.4491e-05 | 9.0023e-05 | 9.9837e-05 | 0.00010957 | 0.00012255 | 0.00012444 | 0.000131 | 0.00013821 | 0.00020757 | 0.00021429 | 0.00021492 | 0.00021819 | 0.00022731 | 0.00023493 | 0.00023863 | 0.0002452 | 0.00027541 | 0.00027914 | 0.00028928 | 0.00031639 | 0.00035458 | 0.00039437 | 0.00040257 | 0.00045053 | 0.00045874 | 0.0004615 | 0.0004615 | 0.00046324 | 0.00047222 | 0.00047753 | 0.00053118 | 0.00053215 | 0.0005457 | 0.0005475 | 0.00054888 | 0.00055051 | 0.0005622 | 0.00056909 | 0.00056982 | 0.0005801 | 0.00058626 | 0.00059313 | 0.00059733 | 0.00060083 | 0.00061453 | 0.00061726 | 0.00062073 | 0.00062503 | 0.00062779 | 0.00065231 | 0.00065616 | 0.00067248 | 0.00068209 | 0.00069298 | 0.00069944 | 0.00071086 | 0.00071548 | 0.0007291 | 0.00073447 | 0.00073891 | 0.00075628 | 0.00076488 | 0.00077591 | 0.00078962 | 0.00082053 | 0.0008258 | 0.0008258 | 0.00084283 | 0.00085559 | 0.00087672 | 0.00088425 | 0.00089376 | 0.00090724 | 0.00093333 | 0.00094731 | 0.00095036 | 0.00098963 | 0.0010142 | 0.0010184 | 0.0010263 | 0.0010381 | 0.0010421 | 0.0010513 | 0.0010747 | 0.0010761 | 0.0010981 | 0.0011309 | 0.0011336 | 0.0011718 | 0.001176 | 0.0011915 | 0.0012174 | 0.0012174 | 0.0012537 | 0.0012537 | 0.0012618 | 0.0012623 | 0.0012989 | 0.0013062 | 0.0013202 | 0.0013279 | 0.0013477 | 0.0013863 | 0.001426 | 0.0014293 | 0.001431 | 0.0014503 | 0.0014503 | 0.0014592 | 0.0014789 | 0.0015002 | 0.0015025 | 0.0015431 | 0.0015611 | 0.0015795 | 0.0016012 | 0.0016034 | 0.0016342 | 0.0016867 | 0.0016912 | 0.0016983 | 0.0018145 | 0.0018367 | 0.0018367 | 0.0018437
2 | 6.0508e-05 | 0.0021754 | 0.0021754 | 0.00017871 | 0.0014294 | 0.0014406 |  | 0.00046677 | 0.0050846 |  | 0.00045281 | 0.00056849 | 0.00026185 | [11 empty] | 0.00099279 | 0.0007456 |  | 0.00027541 |  |  | 0.0005479 | 0.0011191 |  | 0.00064953 | 0.00045874 | 0.00048064 |  |  | 0.00057862 | 0.00047836 | 0.00089726 | 0.00055049 | 0.0014986 | 0.0016816 |  |  |  | 0.00057898 | 0.00095637 |  | 0.00058157 |  |  | 0.0019351 | 0.0006325 |  |  |  |  | 0.00063727 | [16 empty] | 0.0016447 | 0.0016447 |  | 0.0044797 |  |  |  | 0.0016319 | 0.002352 | [5 empty] | 0.0015371 | [26 empty] | 0.0014777 | 0.0014777
3 | 7.3194e-05 | [9 empty] | 0.00062219 | 0.0018705 | 0.00097518 | [14 empty] | 0.0004268 | [19 empty] | 0.00078876 | 0.0017666 |  | 0.0008088 |  |  |  | 0.00069326 |  |  |  |  | 0.00068556
4 | 0.00012669 | [9 empty] | 0.00093333 | [16 empty] | 0.00061967 | [20 empty] | 0.0018025
5 | 0.00020358 | [26 empty] | 0.00073024
6 | 0.00080136 | [26 empty] | 0.001377
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 6 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 6 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 3 | 4 | 1 | 3 | 1 | 1 | 2 | 3 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Outlier Emission Averages Removed:
Total number of values used to calculate mean on row 65 |  | 130 |  | = n for existing sources in Term 1 on row 79
n =Total # test runs = |  | 187 |  | = n for new sources in Term 1 | ; = number of data points in s^2 calculation; also, this number minus 1 is the value used to calculate the t-statistic | [10 empty] | UPL Pooled Variance=
|  | 186 |  | (this value is used to determine the t-statistic on row 95)
This step is for QC only:
means | 5.898e-05 | 6.0269e-05 | 6.0269e-05 | 7.1717e-05 | 8.3833e-05 | 8.4491e-05 | 9.0023e-05 | 9.9837e-05 | 0.00010957 | 0.00012255 | 0.00012444 | 0.000131 | 0.00013821 | 0.00020757 | 0.00021429 | 0.00021492 | 0.00021819 | 0.00022731 | 0.00023493 | 0.00023863 | 0.0002452 | 0.00027541 | 0.00027914 | 0.00028928 | 0.00031639 | 0.00035458 | 0.00039437 | 0.00040257 | 0.00045053 | 0.00045874 | 0.0004615 | 0.0004615 | 0.00046324 | 0.00047222 | 0.00047753 | 0.00053118 | 0.00053215 | 0.0005457 | 0.0005475 | 0.00054888 | 0.00055051 | 0.0005622 | 0.00056909 | 0.00056982 | 0.0005801 | 0.00058626 | 0.00059313 | 0.00059733 | 0.00060083 | 0.00061453 | 0.00061726 | 0.00062073 | 0.00062503 | 0.00062779 | 0.00065231 | 0.00065616 | 0.00067248 | 0.00068209 | 0.00069298 | 0.00069944 | 0.00071086 | 0.00071548 | 0.0007291 | 0.00073447 | 0.00073891 | 0.00075628 | 0.00076488 | 0.00077591 | 0.00078962 | 0.00082053 | 0.0008258 | 0.0008258 | 0.00084283 | 0.00085559 | 0.00087672 | 0.00088425 | 0.00089376 | 0.00090724 | 0.00093333 | 0.00094731 | 0.00095036 | 0.00098963 | 0.0010142 | 0.0010184 | 0.0010263 | 0.0010381 | 0.0010421 | 0.0010513 | 0.0010747 | 0.0010761 | 0.0010981 | 0.0011309 | 0.0011336 | 0.0011718 | 0.001176 | 0.0011915 | 0.0012174 | 0.0012174 | 0.0012537 | 0.0012537 | 0.0012618 | 0.0012623 | 0.0012989 | 0.0013062 | 0.0013202 | 0.0013279 | 0.0013477 | 0.0013863 | 0.001426 | 0.0014293 | 0.001431 | 0.0014503 | 0.0014503 | 0.0014592 | 0.0014789 | 0.0015002 | 0.0015025 | 0.0015431 | 0.0015611 | 0.0015795 | 0.0016012 | 0.0016034 | 0.0016342 | 0.0016867 | 0.0016912 | 0.0016983 | 0.0018145 | 0.0018367 | 0.0018367 | 0.0018437
0.0008284
UPL Mean = | [6 empty] | Distribution of Normal Tests | Distribution of Log Tests
[6 empty] | Skewness = | 0.26226 | #DIV/0!
[6 empty] | SE Skewness | 0.21483 | #DIV/0!
Pooled Variance = |  | 4.3858e-07 |  |  |  | Skewness Test | normal | #DIV/0!
[6 empty] | Kurtosis = | -0.90443 | #DIV/0!
[6 empty] | SE Kurtosis | 0.42967 | #DIV/0!
[6 empty] | Kurtosis Test | normal | #DIV/0!
[6 empty] | Number of test runs = | 130 | 0 | Result: | normal
m= number future runs = |  | 1
Term1 |  | 1.0077
Term2 |  | 4.4196e-07
Squared root Term2 |  | 0.0006648
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 2.3466 |  | (the t-statistic should be calculated with the one less data point than the data set used for calculation of s^2.)
UPL POOLED VARIANCE = |  | 0.0023884 | lb/MW
HF | 3xRDL, 4dscm sample volume | 0.0004 | lb/MW
| Floor Value | 0.0023884 | lb/MW
Tukey's Exploratory Data Analysis Model
0.00046549 | 25th Percentile
0.0012174 | 75th Percentile
0.00075187 | IQR
Gross Outlier Test
Far Outlier Test (low)
Far Outlier Test (high)
Near Outlier Test (low)
Near Outlier Test (high)
IF(COUNT(Q5:Q39)>1,IF(MAX(Q5:Q39)>100*MIN(Q5:Q39),"Gross Outlier",""),"")
3.165
[16 empty] | 0.00021492 | 0.021492
1.4594e-08
14726.7227
Note on A113: Evaluates multiple test averages for a source and flags if max test average is >100x larger than Min test avg.
Note on A114: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A115: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/3 of the 25th percentile value.
Note on A116: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.
Note on A117: Uses Tukey's method for evaluating outliers across multiple sources. Flags the minimum test average if it is less than 1/1.5 of the 25th percentile value.

## HF_New_MW
Emissions (lb/MW)
Logan Generating Plant
ORIS/Facility/Unit | 10043
Runs | B01
1 | 5.647e-05 | BDL
2 | 6.3999e-05 | BDL
3 | 5.647e-05 | BDL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3
2
This step is for QC only:
means | 5.898e-05
5.898e-05
UPL Mean =
Pooled Variance = |  | 1.8897e-11
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.2598e-11
Squared root Term2 |  | 3.5494e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 8.37e-05 | lb/MW
HF | 3xRDL, 4dscm sample volume | 0.0004 | lb/MW
| Floor Value | 0.0004 | lb/MW

## SO2_Avg_coal_MMBtu
Emissions (lb/MMBtu)
| R. Gallagher | Stanton | Port of Stockton District Energy Facility | Port of Stockton District Energy Facility | Coffeen | AES Puerto Rico Cogeneration Facility | Elm Road Generating Station | AES Puerto Rico Cogeneration Facility | Sandow Station | Boswell Energy Center | Duck Creek | TransAlta Centralia Generation | Spruance Genco, LLC | Spruance Genco, LLC | Rio Bravo Jasmin | TransAlta Centralia Generation | Spruance Genco, LLC | Spruance Genco, LLC | Rio Bravo Poso | Crist | Crist | Crist | Crist | Edgecombe Genco, LLC | Edgecombe Genco, LLC | Reid Gardner | Hammond | Hammond | Hammond | Hammond | Mountaineer | Hatfield's Ferry Power Station | Colstrip Energy LP | Sandow Station | San Juan | Asheville Steam Electric Plant | Walter Scott Jr. Energy Center | TS Power Plant | Roxboro Steam Electric Plant | Spruance Genco, LLC | Spruance Genco, LLC | Clover | Asheville Steam Electric Plant | John E. Amos | Colstrip | Hopewell | Hopewell | AES Petersburg | Wygen 2 | Belews Creek Steam Station | Bonanza Power Plant | Cholla | Weston | ACE Cogeneration Company | John E. Amos | Bowen | Oak Grove | Reid Gardner | Springerville | Edgecombe Genco, LLC | Edgecombe Genco, LLC | Southampton Power Station | Southampton Power Station | North Valmy | San Juan | Reid Gardner | East Bend Station | Cholla | Mitchell | Gorgas | Gorgas | Gorgas | Crystal River Power Plant | San Juan | Mount Tom | Springerville | Harrison Power Station | Springerville | Bowen | Cross | Springerville | Mitchell | Rawhide | Clover | F. B. Culley | F. B. Culley | R D Green | Big Bend | Marshall | Marshall | Reid Gardner | San Juan | Ghent | Logan Generating Plant | Neil Simpson II | Nebraska City | Yates | PANTHER CREEK ENERGY FACILITY | PANTHER CREEK ENERGY FACILITY | Marshall | Hardin Generator Project | G G Allen | G G Allen | H L Spurlock Station | AES Petersburg | Mt. Storm | Ghent | Cholla | Apache Station | Spruance Genco, LLC | Spruance Genco, LLC | Foster Wheeler Mt Carmel Cogen | H L Spurlock Station | Cherokee | Valmont | Cholla | Cherokee | Bailly | Bailly | Dallman | Hayden | G G Allen | G G Allen | G G Allen | Hayden | Northampton Generating Company, L.P. | Apache Station | Red Hills Generating Facility | Red Hills Generating Facility | Hawthorn
ORIS/Facility/Unit | 1008 | 2824 | 54238 | 54238 | 861 | 68029 | 56068 | 68029 | 52071 | 1893 | 6016 | 3845 | 54081 | 54081 | 10768 | 3845 | 54081 | 54081 | 10769 | 641 | 641 | 641 | 641 | 10384 | 10384 | 2324 | 708 | 708 | 708 | 708 | 6264 | 3179 | 10784 | 52071 | 2451 | 2706 | 1082 | 56224 | 2712 | 54081 | 54081 | 7213 | 2706 | 3935 | 6076 | 10771 | 10771 | 994 | 56319 | 8042 | 7790 | 113 | 4078 | 10002 | 3935 | 703 | 6180 | 2324 | 8223 | 10384 | 10384 | 10774 | 10774 | 8224 | 2451 | 2324 | 6018 | 113 | 3948 | 8 | 8 | 8 | 628 | 2451 | 1606 | 8223 | 3944 | 8223 | 703 | 130 | 8223 | 3948 | 6761 | 7213 | 1012 | 1012 | 6639 | 645 | 2727 | 2727 | 2324 | 2451 | 1356 | 10043 | 7504 | 6096 | 728 | 50776 | 50776 | 2727 | 55749 | 2718 | 2718 | 6041 | 994 | 3954 | 1356 | 113 | 160 | 54081 | 54081 | 10343 | 6041 | 469 | 477 | 113 | 469 | 995 | 995 | 963 | 525 | 2718 | 2718 | 2718 | 525 | 50888 | 160 | 55076 | 55076 | 2079
Test Averages | 2 | u10 | 1 | 1 | 1 | Unit_2 | ERGS-B1 | Unit_1 | 5A | BEC3 | 1 | BW21CONFIG | GEN3 | GEN3 | Config 1 | BW22CONFIG | GEN2 | GEN2 | Config 1 | Unit 5 | Unit 6 | Unit 7 | Unit 4 | Gen 1 | Gen 1 | 3 | Unit 2 | Unit 3 | Unit 1 | Unit 4 | Mt-1 | 1 | Config1 | 5B | Unit 3 | Ash_Cfg_1d | 4 | TSPower | Rox_Cfg_2c | GEN4 | GEN4 | Unit 1 | Ash_Cfg_2 | AM-2 | Unit3 | 1 & 2 | 1 & 2 | 1s | WYG2Cfg | 2008-01-01 | 2011-01-01 | 1 | W4 | Config 1 | AM-3 | Unit 4 | OG1 | 1 | 2 | Gen 2 | Gen 2 | Unit 1 & 2 | Unit 1 & 2 | 2 | Unit 4 | 4 | 2 | 2 | MI-1 | Unit 10 | Unit 8 | Unit 9 | CryR_Cfg_5c | Unit 1 | 1 current | 4 | Boiler2 | 1 | Unit 3 | C3 | 3 | MI-2 | Rawhide101 | Unit 2 | Config3 | Config2 | 2 | BB01_pre-SCR | U12007 | U22007 | 2 | Unit 2 | GH1 | Unit1 | NS2Cfg | NC2 | Y1BR | BG1 | BG2 | U4 | PC1 | 2009-03-01 | 2009-04-01 | Unit 04 | 2ss | Unit 3 | GH4 | 4 | ST2 | GEN1 | GEN1 | SG-101 | Unit 01 | Unit 3 | Unit 5 | 3 | Unit 4 | 7 | 8 | 34 | Unit 1 | 2009-02-01 | 2009-05-01 | 2009-01-01 | Unit 2 | GEN1 | ST3 | 2 | 1 | 5A
1 | 0.003236 | 0.0076601 | 0.008 | 0.008 | 0.0084667 | 0.00871 | 0.009 | 0.009 | 0.011155 | 0.011667 | 0.0133 | 0.0213 | 0.0227 | 0.0227 | 0.0232 | 0.023333 | 0.0241 | 0.0241 | 0.0245 | 0.025 | 0.025 | 0.025 | 0.025 | 0.0278 | 0.0278 | 0.029267 | 0.029367 | 0.029367 | 0.029367 | 0.029367 | 0.0314 | 0.031525 | 0.031567 | 0.032 | 0.035548 | 0.038 | 0.041 | 0.041667 | 0.042 | 0.0423 | 0.0423 | 0.043842 | 0.044414 | 0.045067 | 0.045224 | 0.046315 | 0.046315 | 0.047471 | 0.048 | 0.04836 | 0.04943 | 0.05 | 0.05 | 0.052 | 0.052143 | 0.053933 | 0.054 | 0.055 | 0.056 | 0.0568 | 0.0568 | 0.05739 | 0.05739 | 0.058667 | 0.058871 | 0.0591 | 0.060856 | 0.061 | 0.0613 | 0.065176 | 0.065176 | 0.065176 | 0.065224 | 0.065474 | 0.066 | 0.069233 | 0.070078 | 0.071 | 0.071933 | 0.0743 | 0.074367 | 0.075067 | 0.078533 | 0.079175 | 0.080045 | 0.080045 | 0.080267 | 0.082901 | 0.082924 | 0.082924 | 0.083 | 0.083286 | 0.084433 | 0.090996 | 0.0921 | 0.092367 | 0.0937 | 0.093701 | 0.093701 | 0.094491 | 0.095333 | 0.097062 | 0.097062 | 0.097767 | 0.098233 | 0.098267 | 0.0991 | 0.1 | 0.10257 | 0.10313 | 0.10313 | 0.10864 | 0.10867 | 0.11097 | 0.11116 | 0.113 | 0.11387 | 0.11433 | 0.11433 | 0.118 | 0.11897 | 0.11925 | 0.11925 | 0.11925 | 0.12141 | 0.12354 | 0.12491 | 0.12496 | 0.12496 | 0.12535
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Total Number of sources = |  | 130
n =Total # test runs = |  | 130
129
This step is for QC only:
means | 0.003236 | 0.0076601 | 0.008 | 0.008 | 0.0084667 | 0.00871 | 0.009 | 0.009 | 0.011155 | 0.011667 | 0.0133 | 0.0213 | 0.0227 | 0.0227 | 0.0232 | 0.023333 | 0.0241 | 0.0241 | 0.0245 | 0.025 | 0.025 | 0.025 | 0.025 | 0.0278 | 0.0278 | 0.029267 | 0.029367 | 0.029367 | 0.029367 | 0.029367 | 0.0314 | 0.031525 | 0.031567 | 0.032 | 0.035548 | 0.038 | 0.041 | 0.041667 | 0.042 | 0.0423 | 0.0423 | 0.043842 | 0.044414 | 0.045067 | 0.045224 | 0.046315 | 0.046315 | 0.047471 | 0.048 | 0.04836 | 0.04943 | 0.05 | 0.05 | 0.052 | 0.052143 | 0.053933 | 0.054 | 0.055 | 0.056 | 0.0568 | 0.0568 | 0.05739 | 0.05739 | 0.058667 | 0.058871 | 0.0591 | 0.060856 | 0.061 | 0.0613 | 0.065176 | 0.065176 | 0.065176 | 0.065224 | 0.065474 | 0.066 | 0.069233 | 0.070078 | 0.071 | 0.071933 | 0.0743 | 0.074367 | 0.075067 | 0.078533 | 0.079175 | 0.080045 | 0.080045 | 0.080267 | 0.082901 | 0.082924 | 0.082924 | 0.083 | 0.083286 | 0.084433 | 0.090996 | 0.0921 | 0.092367 | 0.0937 | 0.093701 | 0.093701 | 0.094491 | 0.095333 | 0.097062 | 0.097062 | 0.097767 | 0.098233 | 0.098267 | 0.0991 | 0.1 | 0.10257 | 0.10313 | 0.10313 | 0.10864 | 0.10867 | 0.11097 | 0.11116 | 0.113 | 0.11387 | 0.11433 | 0.11433 | 0.118 | 0.11897 | 0.11925 | 0.11925 | 0.11925 | 0.12141 | 0.12354 | 0.12491 | 0.12496 | 0.12496 | 0.12535
[7 empty] | Distribution of Normal Tests | Distribution of Log Tests
0.063421
UPL Mean = | [5 empty] | Skewness = | 0.15143 | #DIV/0!
[6 empty] | SE Skewness | 0.21483 | #DIV/0!
[6 empty] | Skewness Test | normal | #DIV/0!
[6 empty] | Kurtosis = | -1.0753 | #DIV/0!
Pooled Variance = |  | 0.0011843 |  |  |  | SE Kurtosis | 0.42967 | #DIV/0!
[6 empty] | Kurtosis Test | normal | #DIV/0!
[6 empty] | Number of test runs = | 130 | 0 | REsult: | normal
m= number future runs = |  | 1
Term1 |  | 1.0077
Term2 |  | 0.0011934
Squared root Term2 |  | 0.034545
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 2.3556
UPL POOLED VARIANCE = |  | 0.1448

## SO2_New_coal_MMBtu
Emissions (lb/MMBtu)
Port of Stockton District Energy Facility
ORIS/Facility/Unit | 54238
Runs | 1
1 | 0.003 | ADL
2 | 0.009 | ADL
3 | 0.012 | ADL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 | 0.00989
0.00932
0.00779
2
This step is for QC only:
means | 0.008
0.008
Mean =
Pooled Variance = |  | 2.1e-05
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.4e-05
Squared root Term2 |  | 0.0037417
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.034059

## SO2_Avg_coal_MW
Emissions (lb/MW)
| R. Gallagher | Coffeen | Stanton | AES Puerto Rico Cogeneration Facility | Elm Road Generating Station | AES Puerto Rico Cogeneration Facility | Port of Stockton District Energy Facility | Port of Stockton District Energy Facility | Sandow Station | Boswell Energy Center | Duck Creek | Crist | Crist | Crist | Crist | Rio Bravo Jasmin | TransAlta Centralia Generation | Rio Bravo Poso | Mountaineer | Hammond | Hammond | Hammond | Spruance Genco, LLC | Spruance Genco, LLC | Hatfield's Ferry Power Station | Hammond | Spruance Genco, LLC | Spruance Genco, LLC | TransAlta Centralia Generation | Reid Gardner | Sandow Station | Edgecombe Genco, LLC | Edgecombe Genco, LLC | Asheville Steam Electric Plant | TS Power Plant | Walter Scott Jr. Energy Center | San Juan | John E. Amos | AES Petersburg | Roxboro Steam Electric Plant | Asheville Steam Electric Plant | Colstrip | Belews Creek Steam Station | Weston | Colstrip Energy LP | ACE Cogeneration Company | John E. Amos | Cholla | Springerville | Clover | Bonanza Power Plant | Bowen | Mitchell | Spruance Genco, LLC | Spruance Genco, LLC | Hopewell | Hopewell | Cholla | East Bend Station | Gorgas | Oak Grove | Gorgas | Reid Gardner | San Juan | Harrison Power Station | Gorgas | Reid Gardner | North Valmy | Mount Tom | Bowen | Crystal River Power Plant | Springerville | Mitchell | Springerville | Wygen 2 | San Juan | Springerville | Edgecombe Genco, LLC | Edgecombe Genco, LLC | Cross | Rawhide | F. B. Culley | Southampton Power Station | Southampton Power Station | Marshall | Marshall | G G Allen | G G Allen | Logan Generating Plant | Marshall | Big Bend | F. B. Culley | San Juan | Reid Gardner | H L Spurlock Station | AES Petersburg | R D Green | Clover | Nebraska City | Yates | Apache Station | Dallman | Cholla | G G Allen | Ghent | Mt. Storm | Hardin Generator Project | Valmont | Cherokee | Bailly | Cholla | Bailly | Ghent | G G Allen | Marshall | H L Spurlock Station | Neil Simpson II | Hayden | Hayden | Northampton Generating Company, L.P. | Cardinal | G G Allen | Apache Station | Red Hills Generating Facility | Red Hills Generating Facility | INDIANTOWN COGENERATION L.P. | PANTHER CREEK ENERGY FACILITY | PANTHER CREEK ENERGY FACILITY | Cherokee | Foster Wheeler Mt Carmel Cogen
ORIS/Facility/Unit | 1008 | 861 | 2824 | 68029 | 56068 | 68029 | 54238 | 54238 | 52071 | 1893 | 6016 | 641 | 641 | 641 | 641 | 10768 | 3845 | 10769 | 6264 | 708 | 708 | 708 | 54081 | 54081 | 3179 | 708 | 54081 | 54081 | 3845 | 2324 | 52071 | 10384 | 10384 | 2706 | 56224 | 1082 | 2451 | 3935 | 994 | 2712 | 2706 | 6076 | 8042 | 4078 | 10784 | 10002 | 3935 | 113 | 8223 | 7213 | 7790 | 703 | 3948 | 54081 | 54081 | 10771 | 10771 | 113 | 6018 | 8 | 6180 | 8 | 2324 | 2451 | 3944 | 8 | 2324 | 8224 | 1606 | 703 | 628 | 8223 | 3948 | 8223 | 56319 | 2451 | 8223 | 10384 | 10384 | 130 | 6761 | 1012 | 10774 | 10774 | 2727 | 2727 | 2718 | 2718 | 10043 | 2727 | 645 | 1012 | 2451 | 2324 | 6041 | 994 | 6639 | 7213 | 6096 | 728 | 160 | 963 | 113 | 2718 | 1356 | 3954 | 55749 | 477 | 469 | 995 | 113 | 995 | 1356 | 2718 | 2727 | 6041 | 7504 | 525 | 525 | 50888 | 2828 | 2718 | 160 | 55076 | 55076 | 50976 | 50776 | 50776 | 469 | 10343
Test Averages | 2 | 1 | u10 | Unit_2 | ERGS-B1 | Unit_1 | 1 | 1 | 5A | BEC3 | 1 | Unit 5 | Unit 6 | Unit 7 | Unit 4 | Config 1 | BW21CONFIG | Config 1 | Mt-1 | Unit 2 | Unit 3 | Unit 1 | GEN3 | GEN3 | 1 | Unit 4 | GEN2 | GEN2 | BW22CONFIG | 3 | 5B | Gen 1 | Gen 1 | Ash_Cfg_1d | TSPower | 4 | Unit 3 | AM-2 | 1s | Rox_Cfg_2c | Ash_Cfg_2 | Unit3 | 2008-01-01 | W4 | Config1 | Config 1 | AM-3 | 1 | 2 | Unit 1 | 2011-01-01 | Unit 4 | MI-1 | GEN4 | GEN4 | 1 & 2 | 1 & 2 | 2 | 2 | Unit 10 | OG1 | Unit 8 | 1 | Unit 4 | Boiler2 | Unit 9 | 4 | 2 | 1 current | Unit 3 | CryR_Cfg_5c | 1 | MI-2 | 4 | WYG2Cfg | Unit 1 | 3 | Gen 2 | Gen 2 | C3 | Rawhide101 | Config3 | Unit 1 & 2 | Unit 1 & 2 | U12007 | U22007 | 2009-03-01 | 2009-04-01 | Unit1 | U4 | BB01_pre-SCR | Config2 | Unit 2 | 2 | Unit 04 | 2ss | 2 | Unit 2 | NC2 | Y1BR | ST2 | 34 | 4 | 2009-02-01 | GH1 | Unit 3 | PC1 | Unit 5 | Unit 4 | 7 | 3 | 8 | GH4 | 2009-05-01 | U3 | Unit 01 | NS2Cfg | Unit 2 | Unit 1 | GEN1 | CD-U2 | 2009-01-01 | ST3 | 2 | 1 | 1 | BG1 | BG2 | Unit 3 | SG-101
1 | 0.031497 | 0.077188 | 0.081963 | 0.084074 | 0.08661 | 0.086873 | 0.0912 | 0.0912 | 0.11695 | 0.1293 | 0.14963 | 0.24934 | 0.24948 | 0.26399 | 0.26489 | 0.26561 | 0.27351 | 0.27762 | 0.2845 | 0.29061 | 0.29147 | 0.2959 | 0.2966 | 0.2966 | 0.30456 | 0.30827 | 0.3149 | 0.3149 | 0.31864 | 0.32615 | 0.33547 | 0.3418 | 0.3418 | 0.35136 | 0.36364 | 0.37021 | 0.37626 | 0.38756 | 0.40955 | 0.41182 | 0.41409 | 0.42544 | 0.44045 | 0.45022 | 0.45556 | 0.46756 | 0.47875 | 0.48473 | 0.49879 | 0.50077 | 0.50136 | 0.51377 | 0.52717 | 0.5527 | 0.5527 | 0.58234 | 0.58234 | 0.5876 | 0.59039 | 0.59055 | 0.59288 | 0.59623 | 0.60203 | 0.61133 | 0.61187 | 0.61252 | 0.62171 | 0.62553 | 0.63019 | 0.63104 | 0.63124 | 0.63684 | 0.64556 | 0.64618 | 0.65 | 0.65598 | 0.69409 | 0.69836 | 0.69836 | 0.72018 | 0.72096 | 0.74997 | 0.75029 | 0.75029 | 0.75838 | 0.75941 | 0.76822 | 0.77701 | 0.79664 | 0.81395 | 0.81627 | 0.82527 | 0.83016 | 0.90851 | 0.91249 | 0.91478 | 0.91571 | 0.91963 | 0.93724 | 0.95867 | 0.97162 | 0.99014 | 1.0042 | 1.0166 | 1.0207 | 1.0397 | 1.0447 | 1.0464 | 1.0465 | 1.064 | 1.0852 | 1.0958 | 1.1263 | 1.1306 | 1.1367 | 1.1502 | 1.1513 | 1.1553 | 1.1561 | 1.17 | 1.1738 | 1.1762 | 1.1833 | 1.1908 | 1.2002 | 1.2007 | 1.209 | 1.209 | 1.2624 | 1.2759
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Total Number of sources = |  | 130
n =Total # test runs = |  | 130
129
This step is for QC only:
means | 0.031497 | 0.077188 | 0.081963 | 0.084074 | 0.08661 | 0.086873 | 0.0912 | 0.0912 | 0.11695 | 0.1293 | 0.14963 | 0.24934 | 0.24948 | 0.26399 | 0.26489 | 0.26561 | 0.27351 | 0.27762 | 0.2845 | 0.29061 | 0.29147 | 0.2959 | 0.2966 | 0.2966 | 0.30456 | 0.30827 | 0.3149 | 0.3149 | 0.31864 | 0.32615 | 0.33547 | 0.3418 | 0.3418 | 0.35136 | 0.36364 | 0.37021 | 0.37626 | 0.38756 | 0.40955 | 0.41182 | 0.41409 | 0.42544 | 0.44045 | 0.45022 | 0.45556 | 0.46756 | 0.47875 | 0.48473 | 0.49879 | 0.50077 | 0.50136 | 0.51377 | 0.52717 | 0.5527 | 0.5527 | 0.58234 | 0.58234 | 0.5876 | 0.59039 | 0.59055 | 0.59288 | 0.59623 | 0.60203 | 0.61133 | 0.61187 | 0.61252 | 0.62171 | 0.62553 | 0.63019 | 0.63104 | 0.63124 | 0.63684 | 0.64556 | 0.64618 | 0.65 | 0.65598 | 0.69409 | 0.69836 | 0.69836 | 0.72018 | 0.72096 | 0.74997 | 0.75029 | 0.75029 | 0.75838 | 0.75941 | 0.76822 | 0.77701 | 0.79664 | 0.81395 | 0.81627 | 0.82527 | 0.83016 | 0.90851 | 0.91249 | 0.91478 | 0.91571 | 0.91963 | 0.93724 | 0.95867 | 0.97162 | 0.99014 | 1.0042 | 1.0166 | 1.0207 | 1.0397 | 1.0447 | 1.0464 | 1.0465 | 1.064 | 1.0852 | 1.0958 | 1.1263 | 1.1306 | 1.1367 | 1.1502 | 1.1513 | 1.1553 | 1.1561 | 1.17 | 1.1738 | 1.1762 | 1.1833 | 1.1908 | 1.2002 | 1.2007 | 1.209 | 1.209 | 1.2624 | 1.2759
[7 empty] | Distribution of Normal Tests | Distribution of Log Tests
0.64215
UPL Mean = | [5 empty] | Skewness = | 0.17057 | #DIV/0!
[6 empty] | SE Skewness | 0.21483 | #DIV/0!
[6 empty] | Skewness Test | normal | #DIV/0!
[6 empty] | Kurtosis = | -1.0373 | #DIV/0!
Pooled Variance = |  | 0.11502 |  |  |  | SE Kurtosis | 0.42967 | #DIV/0!
[6 empty] | Kurtosis Test | normal | #DIV/0!
[6 empty] | Number of test runs = | 130 | 0 | REsult: | normal
m= number future runs = |  | 1
Term1 |  | 1.0077
Term2 |  | 0.1159
Squared root Term2 |  | 0.34044
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 2.3556
UPL POOLED VARIANCE = |  | 1.4441

## SO2_New_coal_MW
Emissions (lb/MW)
Port of Stockton District Energy Facility
ORIS/Facility/Unit | 54238
Runs | 1
1 | 0.0342 | ADL
2 | 0.1026 | ADL
3 | 0.1368 | ADL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3
2
This step is for QC only:
means | 0.0912
0.0912
Mean =
Pooled Variance = |  | 0.0027292
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 0.0018194
Squared root Term2 |  | 0.042655
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.38827