## Pb_Min_Tests
Key | primary_fuel | Pb_Min_lb_per_MWh_Rank | Reason_for_Removal | ORIS code | Plant Name | State | Unit Number | boiler_id | Unit Type | boiler_type | MWe_capacity | max_heat_input | Unit_heat_rate | Fuel types | fuel | Lead_Fuel_lb/MMBtu | Lead - ERT | Lead MW - ERT | Lead - Part II | Lead MW - Part II | Lead - min | Lead MW - min | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
4078_4 | coal | 1 |  | 4078 | Weston | WI | W4 | 4 | Conventional Boiler | Wall firing - opposed firing | 574.5 | 5173.07 | 9.0045 | subbituminous | subbituminous | 0.00024541 | 9.9562e-08 | 8.965e-07 | 1.5467e-06 | 1.3927e-05 | 9.9562e-08 | 8.965e-07 | NOx control | Selective Catalytic Reduction | 2008-07-01 | Other control | Activated carbon injection | 2008-07-01 | SO2 control | Dry FGD - Spray Dryer | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-07-01
2324_1 | coal | 2 |  | 2324 | Reid Gardner | NV | 1 | 1 | Conventional Boiler | Wall firing - front firing | 111 | 1215 | 10.9459 | bituminous | bituminous | 0.00022501 | 9.0551e-08 | 9.9116e-07 |  |  | 9.0551e-08 | 9.9116e-07 | PM control | Fabric Filter, pulse | 2008-12-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
963_34 | coal | 3 |  | 963 | Dallman | IL | 34 | 34 | Conventional Boiler | Wall firing - opposed firing | 229.4 | 1924.9 | 8.391 | bituminous | bituminous | 0.00031503 | 2.3e-07 | 1.9299e-06 | 1.36e-07 | 1.1412e-06 | 1.36e-07 | 1.1412e-06 | NOx control | Selective Catalytic Reduction | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01 | SO2 control | Wet FGD - Packed Type | 2009-05-01 | Other control | Wet electrostatic precipitator | 2009-05-01
6761_101 | coal | 4 |  | 6761 | Rawhide | CO | Rawhide101 | 101 | Conventional Boiler | Tangential firing | 305 | 2800 | 9.1803 | subbituminous | subbituminous | 0.00023104 | 1.3236e-07 | 1.2151e-06 |  |  | 1.3236e-07 | 1.2151e-06 | SO2 control | Dry FGD - Spray Dryer | 1984-04-01 | PM control | Fabric Filter, reverse air | 1984-04-01
602_2 | coal | 5 |  | 602 | Brandon Shores | MD | 002 | 2 | Conventional Boiler | Wall firing - unspecified | 690 | 6700 | 9.7101 | bituminous | bituminous | 0.00041984 | 1.4171e-07 | 1.376e-06 |  |  | 1.4171e-07 | 1.376e-06 | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, hot side, unspecified |  | Other control | Activated carbon injection |  | Other control | Other (specify): lime injection |  | PM control | Fabric Filter, unspecified |  | SO2 control | Wet FGD - Unspecified
10043_B01 | coal | 6 |  | 10043 | Logan Generating Plant | NJ | Unit1 | B01 | Conventional Boiler | Wall firing - opposed firing | 241.7 | 2116 | 8.7547 | bituminous | bituminous | 0.00051281 | 1.8499e-07 | 1.6195e-06 | 4.41e-05 | 0.00038608 | 1.8499e-07 | 1.6195e-06 | NOx control | Selective Catalytic Reduction | 1994-09-01 | SO2 control | Dry FGD - Spray Dryer | 1994-09-01 | PM control | Fabric Filter, reverse air | 1994-09-01
891_Boiler 9 | coal | 7 |  | 891 | Havana | IL | Boiler 9 | Boiler 9 | Conventional Boiler | Wall firing - unspecified | 481 | 5030 | 10.4574 | bituminous | bituminous | 0.00023539 | 1.5555e-07 | 1.6266e-06 |  |  | 1.5555e-07 | 1.6266e-06 | PM control | Electrostatic precipitator, hot side, unspecified | 1978-04-01 | NOx control | Selective Catalytic Reduction | 2003-08-01 | Other control | Activated carbon injection | 2009-07-01 | SO2 control | Dry FGD - Spray Dryer |  | PM control | Fabric Filter, unspecified | 2009-06-01
3845_BD21 | coal | 8 |  | 3845 | TransAlta Centralia Generation | WA | BW21CONFIG | BD21 | Conventional Boiler | Tangential firing | 603 | 7743 | 12.8408 | subbituminous | subbituminous | 0.00036646 | 1.2896e-07 | 1.6559e-06 |  |  | 1.2896e-07 | 1.6559e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-01-01 | SO2 control | Wet FGD - Spray Type | 2002-06-01
2408_E1 | coal | 9 |  | 2408 | PSEG Mercer Generating Station | NJ | MERU1E1PT1OS1-Coal | E1 | Conventional Boiler | Wall firing - unspecified | 343 | 3100 | 9.0379 | bituminous | bituminous | 0.00095074 | 1.8879e-07 | 1.7063e-06 | 5.3333e-07 | 4.8202e-06 | 1.8879e-07 | 1.7063e-06 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1994-05-01 | NOx control | Selective Catalytic Reduction | 2004-06-01 | Other control | Activated carbon injection | 2007-01-01 | PM control | Fabric Filter, pulse | 2008-12-01
10673_BLR B | coal | 10 |  | 10673 | AES Hawaii | HI | 002 | BLR B | Fluidized bed firing | Fluidized bed firing | 101.5 | 944.2 | 9.3025 | bituminous | bituminous | 0.00035153 | 1.8823e-07 | 1.751e-06 |  |  | 1.8823e-07 | 1.751e-06 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
1082_4 | coal | 11 |  | 1082 | Walter Scott Jr. Energy Center | IA | 4 | 4 | Conventional Boiler | Wall firing - unspecified | 850 | 7675 | 9.0294 | subbituminous | subbituminous | 0.00026202 | 1.4205e-06 | 1.2826e-05 | 2e-07 | 1.8059e-06 | 2e-07 | 1.8059e-06 | NOx control | Selective Catalytic Reduction | 2007-02-01 | Other control | Activated carbon injection | 2007-02-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-02-01 | PM control | Fabric Filter, pulse | 2007-02-01
113_4 | coal | 12 |  | 113 | Cholla | AZ | 004 | 4 | Conventional Boiler | Tangential firing | 425 | 4268 | 10.0424 | bituminous | bituminous | 0.00060327 | 1.8284e-07 | 1.8362e-06 |  |  | 1.8284e-07 | 1.8362e-06 | PM control | Fabric Filter, unspecified | 2008-01-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
10566_Boil 2 | coal | 13 |  | 10566 | Chambers Cogeneration LP | NJ | Boil 2 | Boil 2 | Conventional Boiler | Wall firing - front firing | 142.5 | 1387 | 9.7333 | bituminous | bituminous | 0.00028614 | 1.9971e-07 | 1.9439e-06 |  |  | 1.9971e-07 | 1.9439e-06 | NOx control | Selective Catalytic Reduction | 1994-03-01 | SO2 control | Dry FGD - Spray Dryer | 1994-03-01 | PM control | Fabric Filter, reverse air | 1994-03-01
2706_1 | coal | 14 |  | 2706 | Asheville Steam Electric Plant | NC | Ash_Cfg_1d | 1 | Conventional Boiler | Wall firing - front firing | 207 | 1914 | 9.2464 | bituminous | bituminous | 0.00035847 | 4.0292e-06 | 3.7256e-05 | 2.1842e-07 | 2.0196e-06 | 2.1842e-07 | 2.0196e-06 | NOx control | Selective Catalytic Reduction | 2007-06-14 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2005-11-17 | SO2 control | Wet FGD - Spray/Tray Type | 2005-11-17
2706_2 | coal | 15 |  | 2706 | Asheville Steam Electric Plant | NC | Ash_Cfg_2 | 2 | Conventional Boiler | Wall firing - front firing | 204 | 1902 | 9.3235 | bituminous | bituminous | 0.00034046 | 2.1983e-07 | 2.0496e-06 | 4.31e-07 | 4.0184e-06 | 2.1983e-07 | 2.0496e-06 | NOx control | Selective Catalytic Reduction | 2006-06-14 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Spray/Tray Type | 2006-05-15
7210_COP1 | coal | 16 |  | 7210 | Cope | SC | COP001 | COP1 | Conventional Boiler | Tangential firing | 441 | 4059.1 | 9.2043 | bituminous | bituminous | 0.0005352 | 2.3286e-07 | 2.1433e-06 |  |  | 2.3286e-07 | 2.1433e-06 | NOx control | Selective Catalytic Reduction | 2009-01-01 | SO2 control | Dry FGD - Spray Dryer | 1993-04-01 | PM control | Fabric Filter, unspecified | 1993-04-01
6021_C2 | coal | 17 |  | 6021 | Craig | CO | C2 | C2 | Conventional Boiler | Wall firing - opposed firing | 456 | 4269 | 9.3618 | subbituminous | subbituminous | 0.00027366 | 2.3491e-07 | 2.1992e-06 |  |  | 2.3491e-07 | 2.1992e-06 | PM control | Fabric Filter, pulse | 2004-05-01 | SO2 control | Wet FGD - Spray Type | 1979-11-01
50888_BLR1 | coal | 18 |  | 50888 | Northampton Generating Company, L.P. | PA | GEN1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 121 | 1146 | 9.4711 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0078647 | 2.4467e-07 | 2.3172e-06 | 1.055e-06 | 9.9918e-06 | 2.4467e-07 | 2.3172e-06 | NOx control | Selective Noncatalytic Reduction | 1995-08-01 | PM control | Fabric Filter, pulse | 1995-08-01
10671_2a | coal | 19 |  | 10671 | AES Shady Point,LLC | OK | Unit 2 | 2a | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | bituminous, subbituminous | 0.00044619 | 1.7942e-07 | 2.4904e-06 |  |  | 1.7942e-07 | 2.4904e-06 | PM control | Fabric Filter, pulse | 1991-01-01
10671_2b | coal | 20 |  | 10671 | AES Shady Point,LLC | OK | Unit 2 | 2b | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | bituminous, subbituminous | 0.00044619 | 1.7942e-07 | 2.4904e-06 |  |  | 1.7942e-07 | 2.4904e-06 | PM control | Fabric Filter, pulse | 1991-01-01
10671_1b | coal | 21 |  | 10671 | AES Shady Point,LLC | OK | Unit 1 | 1b | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | bituminous, subbituminous | 0.00044619 | 1.7942e-07 | 2.4904e-06 |  |  | 1.7942e-07 | 2.4904e-06 | PM control | Fabric Filter, pulse | 1991-01-01
10671_1A | coal | 22 |  | 10671 | AES Shady Point,LLC | OK | Unit 1 | 1A | Fluidized bed firing | Fluidized bed firing | 80 | 1110.435 | 13.8804 | bituminous, subbituminous | bituminous, subbituminous | 0.00044619 | 1.7942e-07 | 2.4904e-06 |  |  | 1.7942e-07 | 2.4904e-06 | PM control | Fabric Filter, pulse | 1991-01-01
6041_4 | coal | 23 |  | 6041 | H L Spurlock Station | KY | Unit 04 | 4 | Fluidized bed firing | Fluidized bed firing | 300 | 2800 | 9.3333 | bituminous | bituminous | 0.00050351 | 3.3251e-06 | 3.1034e-05 | 2.67e-07 | 2.492e-06 | 2.67e-07 | 2.492e-06 | NOx control | Selective Noncatalytic Reduction | 2009-04-01 | SO2 control | Dry FGD - Unspecified | 2009-04-01 | PM control | Fabric Filter, pulse | 2009-04-01
10675_B | coal | 24 |  | 10675 | AES Thames | CT | B | B | Fluidized bed firing | Fluidized bed firing | 104 | 1002 | 9.6346 | bituminous | bituminous |  |  |  | 2.7067e-07 | 2.6078e-06 | 2.7067e-07 | 2.6078e-06 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1990-03-01 | PM control | Fabric Filter, pulse | 1990-03-01
10673_BLR A | coal | 25 |  | 10673 | AES Hawaii | HI | 001 | BLR A | Fluidized bed firing | Fluidized bed firing | 101.5 | 1021.4 | 10.0631 | bituminous | bituminous | 0.00043954 | 2.5955e-07 | 2.6119e-06 |  |  | 2.5955e-07 | 2.6119e-06 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
6077_2 | coal | 26 |  | 6077 | Gerald Gentleman | NE | U2 | 2 | Conventional Boiler | Wall firing - opposed firing | 750 | 7538 | 10.0507 | bituminous | bituminous | 0.00016589 | 2.6402e-07 | 2.6536e-06 |  |  | 2.6402e-07 | 2.6536e-06 | PM control | Fabric Filter, reverse air | 2001-05-01
56068_1 | coal | 27 |  | 56068 | Elm Road Generating Station | WI | ERGS-B1 | 1 | Conventional Boiler | Wall firing - unspecified | 677 | 6515 | 9.6233 | bituminous | bituminous | 0.00032042 | 2.7919e-07 | 2.6867e-06 |  |  | 2.7919e-07 | 2.6867e-06 | NOx control | Selective Catalytic Reduction | 2009-10-01 | PM control | Fabric Filter, pulse | 2009-10-01 | SO2 control | Wet FGD - Spray Type | 2009-10-01 | Other control | Wet electrostatic precipitator | 2009-10-01
10566_Boil 1 | coal | 28 |  | 10566 | Chambers Cogeneration LP | NJ | Boil 1 | Boil 1 | Conventional Boiler | Wall firing - front firing | 142.5 | 1387 | 9.7333 | bituminous | bituminous | 0.00028525 | 2.7617e-07 | 2.688e-06 |  |  | 2.7617e-07 | 2.688e-06 | NOx control | Selective Catalytic Reduction | 1994-03-01 | SO2 control | Dry FGD - Spray Dryer | 1994-03-01 | PM control | Fabric Filter, reverse air | 1994-03-01
6639_G2 | coal | 29 |  | 6639 | R D Green | KY | 2 | G2 | Conventional Boiler | Wall firing - opposed firing | 239 | 2726.6 | 11.4084 | bituminous, Petroleum coke | bituminous, Petroleum coke | 0.00034843 | 2.3581e-07 | 2.6902e-06 |  |  | 2.3581e-07 | 2.6902e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-01-01 | SO2 control | Wet FGD - Spray Type | 1981-01-01
641_5 | coal | 30 |  | 641 | Crist | FL | Unit 5 | 5 | Conventional Boiler | Tangential firing | 82 | 817.83 | 9.9735 | bituminous | bituminous | 0.0018702 | 2.7154e-07 | 2.7082e-06 |  |  | 2.7154e-07 | 2.7082e-06 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
641_6 | coal | 31 |  | 641 | Crist | FL | Unit 6 | 6 | Conventional Boiler | Wall firing - front firing | 320 | 3193.348 | 9.9792 | bituminous | bituminous | 0.0018702 | 2.7154e-07 | 2.7097e-06 |  |  | 2.7154e-07 | 2.7097e-06 | NOx control | Selective Noncatalytic Reduction | 2005-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
2408_E2 | coal | 32 |  | 2408 | PSEG Mercer Generating Station | NJ | MERU2E2PT2OS1-Coal | E2 | Conventional Boiler | Wall firing - unspecified | 343 | 3100 | 9.0379 | bituminous | bituminous | 0.00064474 | 3.0277e-07 | 2.7364e-06 | 5.3333e-07 | 4.8202e-06 | 3.0277e-07 | 2.7364e-06 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1991-08-01 | NOx control | Selective Catalytic Reduction | 2004-06-01 | Other control | Activated carbon injection | 2007-01-01 | PM control | Fabric Filter, pulse | 2008-12-01
8223_4 | coal | 33 |  | 8223 | Springerville | AZ | 4 | 4 | Conventional Boiler | Wall firing - opposed firing | 450 | 4200 | 9.3333 | bituminous | bituminous | 0.00016811 | 3.5303e-07 | 3.295e-06 | 3e-07 | 2.8e-06 | 3e-07 | 2.8e-06 | NOx control | Selective Catalytic Reduction | 2009-12-01 | SO2 control | Dry FGD - Spray Dryer | 2009-12-01 | PM control | Fabric Filter, pulse | 2009-12-01
641_7 | coal | 34 |  | 641 | Crist | FL | Unit 7 | 7 | Conventional Boiler | Wall firing - front firing | 500 | 5279.792 | 10.5596 | bituminous | bituminous | 0.0018702 | 2.7154e-07 | 2.8673e-06 |  |  | 2.7154e-07 | 2.8673e-06 | NOx control | Selective Catalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2004-04-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
641_4 | coal | 35 |  | 641 | Crist | FL | Unit 4 | 4 | Conventional Boiler | Tangential firing | 82 | 868.842 | 10.5956 | bituminous | bituminous | 0.0018702 | 2.7154e-07 | 2.8771e-06 |  |  | 2.7154e-07 | 2.8771e-06 | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 2009-12-01
6139_1 | coal | 36 |  | 6139 | Welsh | TX | WE-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | 9.2401 | subbituminous | subbituminous | 8.0792e-05 | 3.119e-07 | 2.882e-06 |  |  | 3.119e-07 | 2.882e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-03-01
10672_CBC | coal | 37 |  | 10672 | Cedar Bay Generating Company L.P. | FL | CBC1 | CBC | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | 11.5543 | bituminous | bituminous | 0.00056431 | 9.3139e-07 | 1.0762e-05 | 2.5177e-07 | 2.9091e-06 | 2.5177e-07 | 2.9091e-06 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
8223_3 | coal | 38 |  | 8223 | Springerville | AZ | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 450 | 4200 | 9.3333 | subbituminous | subbituminous | 0.00016612 | 3.8553e-07 | 3.5983e-06 | 3.15e-07 | 2.94e-06 | 3.15e-07 | 2.94e-06 | NOx control | Selective Catalytic Reduction | 2006-08-01 | SO2 control | Dry FGD - Spray Dryer | 2006-08-01 | PM control | Fabric Filter, pulse | 2006-08-01
6016_1 | coal | 39 |  | 6016 | Duck Creek | IL | 001 | 1 | Conventional Boiler | Wall firing - unspecified | 400 | 4500 | 11.25 | subbituminous | subbituminous | 0.00030292 | 2.7008e-07 | 3.0384e-06 | 4.8e-07 | 5.4e-06 | 2.7008e-07 | 3.0384e-06 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2009-03-01 | SO2 control | Wet FGD - Venturi Type | 2009-03-01
6137_1 | coal | 40 |  | 6137 | A. B. Brown Generating Station | IN | 1Config | 1 | Conventional Boiler | Wall firing - opposed firing | 265 | 2518 | 9.5019 | subbituminous | subbituminous | 0.0016798 | 3.2147e-07 | 3.0545e-06 |  |  | 3.2147e-07 | 3.0545e-06 | NOx control | Selective Catalytic Reduction | 2005-04-01 | PM control | Fabric Filter, pulse | 2004-11-01 | SO2 control | Wet FGD - Spray Type | 1979-04-01
2277_1 | coal | 41 |  | 2277 | Sheldon Station | NE | U1 | 1 | Conventional Boiler | Cyclone firing | 128 | 1374 | 10.7344 | subbituminous | subbituminous | 0.00016735 | 2.9119e-07 | 3.1257e-06 |  |  | 2.9119e-07 | 3.1257e-06 | PM control | Fabric Filter, pulse | 1999-12-01
564_2 | coal | 42 |  | 564 | Stanton Energy Center | FL | 2 coal | 2 | Conventional Boiler | Wall firing - opposed firing | 468 | 4286 | 9.1581 | coal - bituminous | bituminous |  | 3.4737e-07 | 3.1813e-06 |  |  | 3.4737e-07 | 3.1813e-06 | NOx control | Selective Catalytic Reduction | 1996-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1996-06-01 | SO2 control | Wet FGD - Spray Type | 1996-06-01
2554_4 | coal | 43 |  | 2554 | Dunkirk Generating Plant | NY | 4 | 4 | Conventional Boiler | Tangential firing | 195 | 1836 | 9.4154 | subbituminous | subbituminous | 0.00026521 | 3.3841e-07 | 3.1863e-06 |  |  | 3.3841e-07 | 3.1863e-06 | NOx control | Selective Noncatalytic Reduction |  | Other control | Dry sorbent injection |  | PM control | Fabric Filter, unspecified | 2009-05-01
7213_2 | coal | 44 |  | 7213 | Clover | VA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 434 | 5041 | 11.6152 | bituminous | bituminous | 0.00084832 | 2.8178e-07 | 3.273e-06 |  |  | 2.8178e-07 | 3.273e-06 | NOx control | Selective Noncatalytic Reduction | 2003-03-01 | PM control | Fabric Filter, reverse air | 2003-05-01 | SO2 control | Wet FGD - Spray Type | 2003-05-01
3845_BD22 | coal | 45 |  | 3845 | TransAlta Centralia Generation | WA | BW22CONFIG | BD22 | Conventional Boiler | Tangential firing | 567 | 7743 | 13.6561 | subbituminous | subbituminous | 0.00034732 | 2.4106e-07 | 3.292e-06 |  |  | 2.4106e-07 | 3.292e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1971-12-01 | SO2 control | Wet FGD - Spray Type | 2001-10-01
55479_3 | coal | 46 |  | 55479 | Wygen 1 | WY | WYG1Cfg | 3 | Conventional Boiler | Wall firing - front firing | 91 | 1053 | 11.5714 | subbituminous | subbituminous | 0.00019616 | 2.9383e-07 | 3.4e-06 |  |  | 2.9383e-07 | 3.4e-06 | NOx control | Selective Catalytic Reduction | 2003-04-01 | SO2 control | Dry FGD - Spray Dryer | 2003-04-01 | PM control | Fabric Filter, pulse | 2003-04-01
2554_1 | coal | 47 |  | 2554 | Dunkirk Generating Plant | NY | 1 | 1 | Conventional Boiler | Tangential firing | 85 | 922.2 | 10.8494 | subbituminous | subbituminous | 0.00023752 | 3.1348e-07 | 3.4011e-06 |  |  | 3.1348e-07 | 3.4011e-06 | NOx control | Selective Noncatalytic Reduction |  | Other control | Dry sorbent injection |  | PM control | Fabric Filter, unspecified | 2009-12-01
2451_Unit 3 | coal | 48 |  | 2451 | San Juan | NM | Unit 3 | Unit 3 | Conventional Boiler | Wall firing - opposed firing | 544 | 5758 | 10.5846 | subbituminous | subbituminous | 0.00097422 | 3.2299e-07 | 3.4187e-06 |  |  | 3.2299e-07 | 3.4187e-06 | Other control | Activated carbon injection | 2008-04-01 | PM control | Fabric Filter, pulse | 2008-03-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
2277_2 | coal | 49 |  | 2277 | Sheldon Station | NE | U2 | 2 | Conventional Boiler | Cyclone firing | 141 | 1514 | 10.7376 | subbituminous | subbituminous | 0.00016726 | 3.2129e-07 | 3.4499e-06 |  |  | 3.2129e-07 | 3.4499e-06 | PM control | Fabric Filter, pulse | 2000-02-01
7097_BLR1 | coal | 50 |  | 7097 | J K Spruce | TX | 1 | BLR1 | Conventional Boiler | Tangential firing | 580 | 6361 | 10.9672 | bituminous | bituminous | 0.00025513 | 3.1761e-07 | 3.4833e-06 | 1.6433e-06 | 1.8023e-05 | 3.1761e-07 | 3.4833e-06 | PM control | Fabric Filter, reverse air | 1992-07-01 | SO2 control | Wet FGD - Spray Type | 1992-12-01
10678_BLR1 | coal | 51 |  | 10678 | AES Warrior Run Cogeneration Facility | MD | BLR1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 202 | 2047 | 10.1337 | bituminous | bituminous | 0.00074099 | 3.4524e-07 | 3.4985e-06 |  |  | 3.4524e-07 | 3.4985e-06 | NOx control | Selective Noncatalytic Reduction | 2000-02-01 | PM control | Fabric Filter, pulse | 2000-02-01
56319_0001 | coal | 52 |  | 56319 | Wygen 2 | WY | WYG2Cfg | 0001 | Conventional Boiler | Wall firing - front firing | 96 | 1300 | 13.5417 | subbituminous | subbituminous | 0.00019593 | 2.6068e-07 | 3.53e-06 |  |  | 2.6068e-07 | 3.53e-06 | NOx control | Selective Catalytic Reduction | 2008-01-01 | SO2 control | Dry FGD - Spray Dryer | 2008-01-01 | PM control | Fabric Filter, pulse | 2008-01-01
568_BHB3 | coal | 53 |  | 568 | Bridgeport Station | CT | BHSEMU3OS2-Coal | BHB3 | Conventional Boiler | Tangential firing | 403 | 4100 | 10.1737 | subbituminous | subbituminous | 8.6855e-05 | 3.4743e-07 | 3.5347e-06 |  |  | 3.4743e-07 | 3.5347e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-08-01 | Other control | Activated carbon injection | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-01-01
6002_4 | coal | 54 |  | 6002 | James H. Miller Jr. | AL | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 723 | 6976.5291 | 9.6494 | subbituminous | subbituminous | 0.00020118 | 3.7468e-07 | 3.6154e-06 |  |  | 3.7468e-07 | 3.6154e-06 | NOx control | Selective Catalytic Reduction | 2003-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-03-01 | SO2 control | Wet FGD - Spray Type
10675_A | coal | 55 |  | 10675 | AES Thames | CT | A | A | Fluidized bed firing | Fluidized bed firing | 104 | 1002 | 9.6346 | bituminous | bituminous |  |  |  | 3.8033e-07 | 3.6644e-06 | 3.8033e-07 | 3.6644e-06 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1990-03-01 | PM control | Fabric Filter, pulse | 1990-03-01
50951_1 | coal | 56 |  | 50951 | Sunnyside Cogen Associates | UT | Config 1 | 1 | Fluidized bed firing | Fluidized bed firing | 60 | 700 | 11.6667 | bituminous | bituminous | 0.0020283 | 3.1721e-07 | 3.7007e-06 |  |  | 3.1721e-07 | 3.7007e-06 | NOx control | Other (specify): Anhydrous ammonia injection | 1993-01-01 | SO2 control | Dry FGD - Sorbent Injection | 1993-01-01 | PM control | Fabric Filter, pulse | 1993-01-01
6113_1 | coal | 57 |  | 6113 | Gibson | IN | 1-2007-FGDIN | 1 | Conventional Boiler | Wall firing - opposed firing | 661 | 6368 | 9.6339 | bituminous | bituminous | 0.0010772 | 3.9105e-07 | 3.7673e-06 |  |  | 3.9105e-07 | 3.7673e-06 | NOx control | Selective Catalytic Reduction | 2005-04-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-01-01 | SO2 control | Wet FGD - Tray Type | 2007-10-01
2451_Unit 2 | coal | 58 |  | 2451 | San Juan | NM | Unit 2 | Unit 2 | Conventional Boiler | Wall firing - front firing | 370 | 3688 | 9.9676 | subbituminous | subbituminous | 0.00098577 | 3.7876e-07 | 3.7753e-06 |  |  | 3.7876e-07 | 3.7753e-06 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, pulse | 2009-04-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
10672_CBA | coal | 59 |  | 10672 | Cedar Bay Generating Company L.P. | FL | CBA1 | CBA | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | 11.5543 | bituminous | bituminous | 0.00059382 | 3.2951e-07 | 3.8072e-06 | 4.2366e-07 | 4.8951e-06 | 3.2951e-07 | 3.8072e-06 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
10672_CBB | coal | 60 |  | 10672 | Cedar Bay Generating Company L.P. | FL | CBB1 | CBB | Fluidized bed firing | Fluidized bed firing | 92 | 1063 | 11.5543 | bituminous | bituminous | 0.00057297 | 3.3319e-07 | 3.8498e-06 | 5.3484e-07 | 6.1798e-06 | 3.3319e-07 | 3.8498e-06 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1994-01-01 | NOx control | Selective Noncatalytic Reduction | 1994-01-01 | PM control | Fabric Filter, pulse | 1994-01-01
130_3 | coal | 61 |  | 130 | Cross | SC | C3 | 3 | Conventional Boiler | Tangential firing | 625 | 6058 | 9.6928 | bituminous | bituminous | 0.00036377 | 3.9976e-07 | 3.8748e-06 | 2.2333e-06 | 2.1647e-05 | 3.9976e-07 | 3.8748e-06 | NOx control | Selective Catalytic Reduction | 2006-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2006-08-01 | SO2 control | Wet FGD - Spray Type | 2006-08-01
7504_2 | coal | 62 |  | 7504 | Neil Simpson II | WY | NS2Cfg | 2 | Conventional Boiler | Wall firing - front firing | 88 | 1100 | 12.5 | subbituminous | subbituminous | 0.00030371 | 3.2935e-07 | 4.1169e-06 |  |  | 3.2935e-07 | 4.1169e-06 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1995-09-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-09-01
7213_1 | coal | 63 |  | 7213 | Clover | VA | Unit 1 | 1 | Conventional Boiler | Tangential firing | 431 | 4923 | 11.4223 | bituminous | bituminous | 0.00073062 | 3.6458e-07 | 4.1644e-06 |  |  | 3.6458e-07 | 4.1644e-06 | PM control | Fabric Filter, reverse air | 2003-05-01 | SO2 control | Wet FGD - Spray Type | 2003-05-01
2718_ES-3 | coal | 64 |  | 2718 | G G Allen | NC | 3-2009 | ES-3 | Conventional Boiler | Tangential firing | 281.5 | 2228 | 7.9147 | bituminous | bituminous | 0.0010162 | 5.2983e-07 | 4.1935e-06 |  |  | 5.2983e-07 | 4.1935e-06 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2002-06-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
2718_ES-4 | coal | 65 |  | 2718 | G G Allen | NC | 4-2009 | ES-4 | Conventional Boiler | Tangential firing | 297.3 | 2380 | 8.0054 | bituminous | bituminous | 0.0010162 | 5.2983e-07 | 4.2415e-06 |  |  | 5.2983e-07 | 4.2415e-06 | NOx control | Selective Noncatalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1999-02-01 | SO2 control | Wet FGD - Spray Type | 2009-04-01
4072_8 | coal | 66 |  | 4072 | Pulliam | WI | 8 | 8 | Conventional Boiler | Wall firing - rear firing | 137.9 | 1510 | 10.95 | subbituminous | subbituminous | 0.00022885 | 3.9747e-07 | 4.3522e-06 |  |  | 3.9747e-07 | 4.3522e-06 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1964-12-01
6181_1 | coal | 67 |  | 6181 | J T Deely | TX | 1 | 1 | Conventional Boiler | Tangential firing | 450 | 4251 | 9.4467 | subbituminous | subbituminous | 0.0002177 | 4.6153e-07 | 4.3599e-06 |  |  | 4.6153e-07 | 4.3599e-06 | PM control | Fabric Filter, reverse air | 2007-05-01
6181_2 | coal | 68 |  | 6181 | J T Deely | TX | 2 | 2 | Conventional Boiler | Tangential firing | 450 | 4251 | 9.4467 | subbituminous | subbituminous | 0.0002177 | 4.6153e-07 | 4.3599e-06 |  |  | 4.6153e-07 | 4.3599e-06 | PM control | Fabric Filter, reverse air | 2006-04-01
56224_BLR100 | coal | 69 |  | 56224 | TS Power Plant | NV | TSPower | BLR100 | Conventional Boiler | Wall firing - opposed firing | 242 | 2112 | 8.7273 | subbituminous | subbituminous | 0.00021282 | 8.4269e-07 | 7.3544e-06 | 5.0883e-07 | 4.4407e-06 | 5.0883e-07 | 4.4407e-06 | NOx control | Selective Catalytic Reduction | 2008-03-01 | Other control | Activated carbon injection | 2008-03-01 | SO2 control | Dry FGD - Spray Dryer | 2008-03-01 | PM control | Fabric Filter, pulse | 2008-01-01
2712_1 | coal | 70 |  | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_1b | 1 | Conventional Boiler | Wall firing - opposed firing | 385 | 3755 | 9.7532 | bituminous | bituminous | 0.00041724 | 4.5783e-07 | 4.4654e-06 | 9.8733e-07 | 9.6297e-06 | 4.5783e-07 | 4.4654e-06 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01 | SO2 control | Wet FGD - Spray/Tray Type | 2008-12-01
50976_AABO1 | coal | 71 |  | 50976 | INDIANTOWN COGENERATION L.P. | FL | 001 | AABO1 | Conventional Boiler | Wall firing - opposed firing | 361 | 3422 | 9.4792 | bituminous | bituminous | 0.00067127 | 3.5017e-06 | 3.3193e-05 | 4.9e-07 | 4.6448e-06 | 4.9e-07 | 4.6448e-06 | NOx control | Selective Catalytic Reduction | 1995-12-01 | SO2 control | Dry FGD - Spray Dryer | 1995-12-01 | PM control | Fabric Filter, pulse | 1995-12-01
1393_6 | coal | 72 |  | 1393 | RS Nelson | LA | 001 | 6 | Conventional Boiler | Tangential firing | 580 | 5761 | 9.9328 | bituminous | bituminous | 0.00019648 | 4.7787e-07 | 4.7466e-06 |  |  | 4.7787e-07 | 4.7466e-06 | PM control | Electrostatic precipitator, unspecified | 1982-05-01
3149_2 | coal | 73 |  | 3149 | PPL Montour | PA | U2 | 2 | Conventional Boiler | Tangential firing | 792 | 7239 | 9.1402 | bituminous | bituminous | 0.00028266 | 5.2017e-07 | 4.7545e-06 |  |  | 5.2017e-07 | 4.7545e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-05-01 | NOx control | Selective Catalytic Reduction | 2000-05-01 | SO2 control | Wet FGD - Tray Type | 2008-03-01
2107_2 | coal | 74 |  | 2107 | Sioux | MO | 002 | 2 | Conventional Boiler | Cyclone firing | 524 | 4920 | 9.3893 | subbituminous, bituminous | subbituminous, bituminous | 0.00025988 | 5.1346e-07 | 4.8211e-06 |  |  | 5.1346e-07 | 4.8211e-06 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1997-12-01 | SO2 control | Wet FGD - Unspecified
3179_1 | coal | 75 |  | 3179 | Hatfield's Ferry Power Station | PA | 001 | 1 | Conventional Boiler | Wall firing - opposed firing | 590 | 5700 | 9.661 | bituminous | bituminous | 0.00026556 | 5.1104e-07 | 4.9372e-06 | 7.6e-06 | 7.3424e-05 | 5.1104e-07 | 4.9372e-06 | PM control | Electrostatic precipitator, cold side, unspecified | 1969-01-01 | SO2 control | Wet FGD - Spray Type | 2009-06-01
2712_2 | coal | 76 |  | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_2c | 2 | Conventional Boiler | Tangential firing | 703 | 6893 | 9.8051 | bituminous | bituminous | 0.00055013 | 5.1169e-07 | 5.0172e-06 | 5.4013e-07 | 5.2961e-06 | 5.1169e-07 | 5.0172e-06 | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-05-01 | SO2 control | Wet FGD - Spray/Tray Type | 2007-04-20
6077_1 | coal | 77 |  | 6077 | Gerald Gentleman | NE | U1 | 1 | Conventional Boiler | Wall firing - opposed firing | 715 | 7538 | 10.5427 | bituminous | bituminous | 0.00016569 | 4.7643e-07 | 5.0228e-06 |  |  | 4.7643e-07 | 5.0228e-06 | PM control | Fabric Filter, reverse air | 2000-12-01
2837_3 | coal | 78 |  | 2837 | Eastlake | OH | Unit 3 | 3 | Conventional Boiler | Tangential firing | 144 | 1205 | 8.3681 | subbituminous, bituminous | subbituminous, bituminous | 0.00022356 | 6.3901e-07 | 5.3473e-06 |  |  | 6.3901e-07 | 5.3473e-06 | NOx control | Selective Noncatalytic Reduction | 1999-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-01-01
3140_2 | coal | 79 |  | 3140 | PPL Brunner Island | PA | U2 | 2 | Conventional Boiler | Tangential firing | 393 | 3790 | 9.6438 | bituminous | bituminous | 0.00039967 | 5.568e-07 | 5.3696e-06 |  |  | 5.568e-07 | 5.3696e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2009-10-01 | SO2 control | Wet FGD - Tray Type | 2009-11-01
6113_2 | coal | 80 |  | 6113 | Gibson | IN | 2-2007-FGDIN | 2 | Conventional Boiler | Wall firing - opposed firing | 661 | 6444 | 9.7489 | bituminous | bituminous | 0.0011439 | 5.6046e-07 | 5.4639e-06 |  |  | 5.6046e-07 | 5.4639e-06 | NOx control | Selective Catalytic Reduction | 2001-12-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-01-01 | SO2 control | Wet FGD - Tray Type | 2007-05-01
3140_1 | coal | 81 |  | 3140 | PPL Brunner Island | PA | U1 | 1 | Conventional Boiler | Tangential firing | 330 | 3345 | 10.1364 | bituminous | bituminous | 0.00039967 | 5.568e-07 | 5.6439e-06 |  |  | 5.568e-07 | 5.6439e-06 | PM control | Fabric Filter, pulse | 1965-01-01 | SO2 control | Wet FGD - Tray Type | 2009-11-01
2828_3 | coal | 82 |  | 2828 | Cardinal | OH | CD-U3 | 3 | Conventional Boiler | Wall firing - opposed firing | 650 | 5275 | 8.1154 | bituminous | bituminous | 0.00079645 | 7.0213e-07 | 5.6981e-06 |  |  | 7.0213e-07 | 5.6981e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-09-01 | NOx control | Selective Catalytic Reduction | 2003-01-01
6017_2 | coal | 83 |  | 6017 | Newton | IL | 002 | 2 | Conventional Boiler | Tangential firing | 620 | 5500 | 8.871 | subbituminous | subbituminous | 0.00022532 | 6.6673e-07 | 5.9146e-06 |  |  | 6.6673e-07 | 5.9146e-06 | Other control | Other (specify): Flue gas conditioning | 2001-04-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning
1626_1 | coal | 84 |  | 1626 | Salem Harbor | MA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 81.419 | 981 | 12.0488 | bituminous | bituminous | 0.00037879 | 4.9694e-07 | 5.9876e-06 |  |  | 4.9694e-07 | 5.9876e-06 | NOx control | Selective Noncatalytic Reduction | 1993-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-07-01
54304_1A | coal | 85 |  | 54304 | Birchwood Power Facility | VA | 1A | 1A | Conventional Boiler | Tangential firing | 222 | 2300 | 10.3604 | bituminous | bituminous | 0.00063632 | 5.7816e-07 | 5.9899e-06 |  |  | 5.7816e-07 | 5.9899e-06 | NOx control | Selective Catalytic Reduction | 1996-10-01 | SO2 control | Dry FGD - Spray Dryer | 1996-10-01 | PM control | Fabric Filter, reverse air | 1996-10-01
3403_2 | coal | 86 |  | 3403 | Gallatin | TN | 2 | 2 | Conventional Boiler | Tangential firing | 300 | 2750 | 9.1667 | subbituminous | subbituminous | 0.00018394 | 6.5947e-07 | 6.0451e-06 |  |  | 6.5947e-07 | 6.0451e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-09-01
2727_Unit 4 | coal | 87 |  | 2727 | Marshall | NC | U4 | Unit 4 | Conventional Boiler | Tangential firing | 700 | 6029.8 | 8.614 | bituminous | bituminous |  |  |  | 7.0461e-07 | 6.0695e-06 | 7.0461e-07 | 6.0695e-06 | NOx control | Selective Noncatalytic Reduction | 2006-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2006-05-01 | SO2 control | Wet FGD - Spray Type | 2006-10-01
2451_Unit 4 | coal | 88 |  | 2451 | San Juan | NM | Unit 4 | Unit 4 | Conventional Boiler | Wall firing - opposed firing | 544 | 5649 | 10.3842 | subbituminous | subbituminous | 0.00038709 | 5.8652e-07 | 6.0905e-06 |  |  | 5.8652e-07 | 6.0905e-06 | Other control | Activated carbon injection | 2008-04-01 | PM control | Fabric Filter, pulse | 2007-10-01 | SO2 control | Wet FGD - Spray Type | 1998-04-01
4078_3 | coal | 89 |  | 4078 | Weston | WI | W3 | 3 | Conventional Boiler | Tangential firing | 365.6 | 3423.48 | 9.364 | subbituminous | subbituminous | 0.0002585 | 6.5152e-07 | 6.1008e-06 |  |  | 6.5152e-07 | 6.1008e-06 | PM control | Fabric Filter, pulse | 2001-05-01 | Other control | Activated carbon injection
3149_1 | coal | 90 |  | 3149 | PPL Montour | PA | U1 | 1 | Conventional Boiler | Tangential firing | 797 | 7239 | 9.0828 | bituminous | bituminous | 0.00030298 | 6.7769e-07 | 6.1554e-06 |  |  | 6.7769e-07 | 6.1554e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2001-05-01 | NOx control | Selective Catalytic Reduction | 2001-05-01 | SO2 control | Wet FGD - Tray Type | 2008-05-01
6250_1A | coal | 91 |  | 6250 | Mayo Electric Generating Facility | NC | May_Cfg_1b | 1A | Conventional Boiler | Wall firing - opposed firing | 396 | 3743 | 9.452 | coal - bituminous | bituminous |  |  |  | 6.78e-07 | 6.4085e-06 | 6.78e-07 | 6.4085e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | NOx control | Selective Catalytic Reduction | 2004-04-19 | NOx control | Selective Catalytic Reduction | 2004-04-19 | SO2 control | Wet FGD - Spray/Tray Type | 2009-04-09
6250_1B | coal | 92 |  | 6250 | Mayo Electric Generating Facility | NC | May_Cfg_1b | 1B | Conventional Boiler | Wall firing - opposed firing | 396 | 3743 | 9.452 | coal - bituminous | bituminous |  |  |  | 6.78e-07 | 6.4085e-06 | 6.78e-07 | 6.4085e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1983-10-01 | NOx control | Selective Catalytic Reduction | 2004-04-19 | NOx control | Selective Catalytic Reduction | 2004-04-19 | SO2 control | Wet FGD - Spray/Tray Type | 2009-04-09
708_2 | coal | 93 |  | 708 | Hammond | GA | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 115 | 1138.032 | 9.8959 | bituminous | bituminous | 0.00072481 | 6.4907e-07 | 6.4232e-06 |  |  | 6.4907e-07 | 6.4232e-06 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-04-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
708_3 | coal | 94 |  | 708 | Hammond | GA | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 115 | 1141.392 | 9.9251 | bituminous | bituminous | 0.00072481 | 6.4907e-07 | 6.4421e-06 |  |  | 6.4907e-07 | 6.4421e-06 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
470_2 | coal | 95 |  | 470 | Comanche | CO | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 365 | 3482 | 9.5397 | subbituminous | subbituminous | 0.00022223 | 6.8083e-07 | 6.4949e-06 |  |  | 6.8083e-07 | 6.4949e-06 | Other control | Activated carbon injection |  | SO2 control | Dry FGD - Spray Dryer | 2008-07-01 | PM control | Fabric Filter, reverse air | 1991-12-01
708_1 | coal | 96 |  | 708 | Hammond | GA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 115 | 1158.752 | 10.0761 | bituminous | bituminous | 0.00072481 | 6.4907e-07 | 6.5401e-06 |  |  | 6.4907e-07 | 6.5401e-06 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-02-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
68029_BLR1 | coal | 97 |  | 68029 | AES Puerto Rico Cogeneration Facility | PR | Unit_1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 255 | 2461.4 | 9.6525 | bituminous | bituminous | 0.00018802 | 6.7876e-07 | 6.5518e-06 |  |  | 6.7876e-07 | 6.5518e-06 | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Spray Dryer |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
708_4 | coal | 98 |  | 708 | Hammond | GA | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 520 | 5458.53 | 10.4972 | bituminous | bituminous | 0.00072481 | 6.4907e-07 | 6.8134e-06 |  |  | 6.4907e-07 | 6.8134e-06 | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-12-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
10641_B1 | coal | 99 |  | 10641 | Cambria Cogen | PA | 001 | B1 | Fluidized bed firing | Fluidized bed firing | 49 | 560 | 11.4286 | coal refuse (culm or gob), other--natural gas | coal refuse (culm or gob), other--natural gas | 0.0034428 | 6.0585e-07 | 6.924e-06 |  |  | 6.0585e-07 | 6.924e-06 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
54081_2A | coal | 100 |  | 54081 | Spruance Genco, LLC | VA | GEN2 | 2A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00068749 | 5.3829e-07 | 7.0334e-06 |  |  | 5.3829e-07 | 7.0334e-06 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_2B | coal | 101 |  | 54081 | Spruance Genco, LLC | VA | GEN2 | 2B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00068749 | 5.3829e-07 | 7.0334e-06 |  |  | 5.3829e-07 | 7.0334e-06 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
1554_2 | coal | 102 |  | 1554 | Herbert A. Wagner | MD | 002 | 2 | Conventional Boiler | Wall firing - unspecified | 145 | 1488 | 10.2621 | bituminous | bituminous | 0.0033169 | 7.3207e-07 | 7.5126e-06 |  |  | 7.3207e-07 | 7.5126e-06 | NOx control | Selective Noncatalytic Reduction |  | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, unspecified
10849_BLR1 | coal | 103 |  | 10849 | Silver Bay Power | MN | GEN1 | BLR1 | Conventional Boiler | Wall firing - front firing | 45 | 371.9119 | 8.2647 | subbituminous | subbituminous | 0.00020085 | 9.211e-07 | 7.6126e-06 |  |  | 9.211e-07 | 7.6126e-06 | PM control | Fabric Filter, reverse air | 1980-01-01
6065_1 | coal | 104 |  | 6065 | Iatan | MO | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 726 | 7800 | 10.7438 | coal - subbituminous | subbituminous |  |  |  | 7.2e-07 | 7.7355e-06 | 7.2e-07 | 7.7355e-06 | NOx control | Selective Catalytic Reduction | 2009-02-01 | Other control | Activated carbon injection | 2009-10-01 | PM control | Fabric Filter, pulse | 2009-02-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
54144_BRBR1 | coal | 105 |  | 54144 | Piney Creek Project | PA | BRBRI | BRBR1 | Fluidized bed firing | Fluidized bed firing | 36 | 450 | 12.5 | bituminous, synfuel | bituminous, synfuel | 0.0031271 | 1.4284e-06 | 1.7855e-05 | 6.2054e-07 | 7.7568e-06 | 6.2054e-07 | 7.7568e-06 | NOx control | Selective Noncatalytic Reduction | 2002-08-01 | PM control | Fabric Filter, pulse | 1992-11-01
60_1 | coal | 106 |  | 60 | Whelan Energy Center Unit 1 (WEC1) | NE | 1 | 1 | Conventional Boiler | Tangential firing | 83.6 | 845.1 | 10.1089 | subbituminous | subbituminous | 0.0002525 | 7.7806e-07 | 7.8653e-06 |  |  | 7.7806e-07 | 7.8653e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
6021_C1 | coal | 107 |  | 6021 | Craig | CO | C1 | C1 | Conventional Boiler | Wall firing - opposed firing | 456 | 4028 | 8.8333 | subbituminous | subbituminous | 0.00034001 | 9.2528e-07 | 8.1733e-06 |  |  | 9.2528e-07 | 8.1733e-06 | PM control | Fabric Filter, pulse | 2003-11-01 | SO2 control | Wet FGD - Spray Type | 1980-07-01
3287_MCM2 | coal | 108 |  | 3287 | McMeekin | SC | MCM002 | MCM2 | Conventional Boiler | Tangential firing | 132 | 1101.3 | 8.3432 | bituminous | bituminous | 0.00056883 | 1.0192e-06 | 8.5032e-06 |  |  | 1.0192e-06 | 8.5032e-06 | PM control | Fabric Filter, unspecified | 1992-11-01
130_4 | coal | 109 |  | 130 | Cross | SC | C4 | 4 | Conventional Boiler | Tangential firing | 625 | 6798 | 10.8768 | bituminous | bituminous | 0.00030425 | 7.8335e-07 | 8.5204e-06 | 2.0667e-06 | 2.2479e-05 | 7.8335e-07 | 8.5204e-06 | NOx control | Selective Catalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2008-05-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
2712_3A | coal | 110 |  | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_3b | 3A | Conventional Boiler | Wall firing - rear firing | 370.5 | 3460 | 9.3387 | coal - bituminous | bituminous |  |  |  | 9.39e-07 | 8.7691e-06 | 9.39e-07 | 8.7691e-06 | NOx control | Selective Catalytic Reduction | 2003-04-22 | NOx control | Selective Catalytic Reduction | 2003-04-22 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-11-01 | SO2 control | Wet FGD - Spray/Tray Type | 2008-05-08
2712_3B | coal | 111 |  | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_3b | 3B | Conventional Boiler | Wall firing - rear firing | 370.5 | 3460 | 9.3387 | coal - bituminous | bituminous |  |  |  | 9.39e-07 | 8.7691e-06 | 9.39e-07 | 8.7691e-06 | NOx control | Selective Catalytic Reduction | 2003-04-22 | NOx control | Selective Catalytic Reduction | 2003-04-22 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-11-01 | SO2 control | Wet FGD - Spray/Tray Type | 2008-05-08
2712_4B | coal | 112 |  | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_4c | 4B | Conventional Boiler | Wall firing - opposed firing | 372.5 | 3469 | 9.3128 | coal - bituminous | bituminous |  |  |  | 9.5933e-07 | 8.934e-06 | 9.5933e-07 | 8.934e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | NOx control | Selective Catalytic Reduction | 2001-07-12 | NOx control | Selective Catalytic Reduction | 2001-07-12 | Other control | Dry sorbent injection | 2008-07-07 | SO2 control | Wet FGD - Spray/Tray Type | 2007-11-27
2712_4A | coal | 113 |  | 2712 | Roxboro Steam Electric Plant | NC | Rox_Cfg_4c | 4A | Conventional Boiler | Wall firing - opposed firing | 372.5 | 3469 | 9.3128 | coal - bituminous | bituminous |  |  |  | 9.5933e-07 | 8.934e-06 | 9.5933e-07 | 8.934e-06 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-09-01 | NOx control | Selective Catalytic Reduction | 2001-07-12 | NOx control | Selective Catalytic Reduction | 2001-07-12 | Other control | Dry sorbent injection | 2008-07-07 | SO2 control | Wet FGD - Spray/Tray Type | 2007-11-27
10774_2 | coal | 114 |  | 10774 | Southampton Power Station | VA | Unit 1 & 2 | 2 | Conventional Boiler | Stoker - spreader | 34 | 447 | 13.1471 | bituminous | bituminous | 0.00065339 | 6.9037e-07 | 9.0255e-06 |  |  | 6.9037e-07 | 9.0255e-06 | PM control | Multiple cyclone | 1992-03-01 | PM control | Multiple cyclone | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01
10774_1 | coal | 115 |  | 10774 | Southampton Power Station | VA | Unit 1 & 2 | 1 | Conventional Boiler | Stoker - spreader | 34 | 442 | 13 | bituminous | bituminous | 0.00065339 | 6.9037e-07 | 9.0255e-06 |  |  | 6.9037e-07 | 9.0255e-06 | PM control | Multiple cyclone | 1992-03-01 | PM control | Multiple cyclone | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | SO2 control | Dry FGD - Spray Dryer | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01 | PM control | Fabric Filter, pulse | 1992-03-01
525_1 | coal | 116 |  | 525 | Hayden | CO | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 202 | 1963 | 9.7178 | bituminous | bituminous | 0.00042431 | 9.5925e-07 | 9.3218e-06 |  |  | 9.5925e-07 | 9.3218e-06 | SO2 control | Dry FGD - Spray Dryer | 1998-12-01 | PM control | Fabric Filter, reverse air | 1998-12-01
6019_1 | coal | 117 |  | 6019 | W H Zimmer | OH | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1408 | 12656 | 8.9886 | bituminous, bituminous, bituminous | bituminous, bituminous, bituminous | 0.00035863 | 1.0471e-06 | 9.4123e-06 |  |  | 1.0471e-06 | 9.4123e-06 | Other control | Other (specify): Magnesium Hydroxide Injection |  | NOx control | Selective Catalytic Reduction | 2004-01-01 | Other control | Dry sorbent injection | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-03-01 | SO2 control | Wet FGD - Spray Type | 2004-06-01
6018_2 | coal | 118 |  | 6018 | East Bend Station | KY | 2 | 2 | Conventional Boiler | Wall firing - front firing | 650.7246 | 6313 | 9.7015 | bituminous | bituminous | 0.00050717 | 9.8002e-07 | 9.5077e-06 |  |  | 9.8002e-07 | 9.5077e-06 | Other control | Dry sorbent injection | 2005-01-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1981-01-01 | NOx control | Selective Catalytic Reduction | 2002-01-01 | SO2 control | Wet FGD - Spray Type | 1981-01-01
113_3 | coal | 119 |  | 113 | Cholla | AZ | 003 | 3 | Conventional Boiler | Tangential firing | 305 | 2929 | 9.6033 | bituminous | bituminous | 0.0007542 | 1.0104e-06 | 9.7028e-06 |  |  | 1.0104e-06 | 9.7028e-06 | PM control | Fabric Filter, unspecified | 2009-01-01 | SO2 control | Wet FGD - Unspecified | 2009-01-01
2837_1 | coal | 120 |  | 2837 | Eastlake | OH | Unit 1 | 1 | Conventional Boiler | Tangential firing | 144 | 1205 | 8.3681 | subbituminous, bituminous | subbituminous, bituminous | 0.00015393 | 1.1756e-06 | 9.8376e-06 |  |  | 1.1756e-06 | 9.8376e-06 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
6096_NC2 | coal | 121 |  | 6096 | Nebraska City | NE | NC2 | NC2 | Conventional Boiler | Wall firing - front firing | 682 | 6920.254 | 10.147 | bituminous | bituminous | 0.00016821 | 9.7181e-07 | 9.8609e-06 |  |  | 9.7181e-07 | 9.8609e-06 | NOx control | Selective Catalytic Reduction | 2009-05-01 | Other control | Activated carbon injection | 2009-05-01 | SO2 control | Dry FGD - Spray Dryer | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01
1374_1374-2 | coal | 122 |  | 1374 | Elmer Smith Station | KY | Unit001 | 1374-2 | Conventional Boiler | Tangential firing | 291.5 | 2317 | 7.9485 | bituminous, petroleum coke | bituminous, petroleum coke | 0.00069991 | 1.1955e-06 | 9.9164e-06 |  |  | 1.1955e-06 | 9.9164e-06 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
1374_1374 | coal | 123 |  | 1374 | Elmer Smith Station | KY | Unit001 | 1374 | Conventional Boiler | Cyclone firing | 153 | 1370 | 8.9542 | bituminous, petroleum coke | bituminous, petroleum coke | 0.00069991 | 1.1955e-06 | 9.9164e-06 |  |  | 1.1955e-06 | 9.9164e-06 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-12-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
525_2 | coal | 124 |  | 525 | Hayden | CO | Unit 2 | 2 | Conventional Boiler | Tangential firing | 285 | 2712 | 9.5158 | bituminous | bituminous | 0.00043787 | 1.065e-06 | 1.0134e-05 |  |  | 1.065e-06 | 1.0134e-05 | SO2 control | Dry FGD - Spray Dryer | 1999-06-01 | PM control | Fabric Filter, reverse air | 1999-06-01
68029_BLR2 | coal | 125 |  | 68029 | AES Puerto Rico Cogeneration Facility | PR | Unit_2 | BLR2 | Fluidized bed firing | Fluidized bed firing | 255 | 2461.4 | 9.6525 | bituminous | bituminous | 0.0002049 | 1.057e-06 | 1.0203e-05 |  |  | 1.057e-06 | 1.0203e-05 | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Spray Dryer |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
54081_1A | coal | 126 |  | 54081 | Spruance Genco, LLC | VA | GEN1 | 1A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00050125 | 7.8881e-07 | 1.0307e-05 |  |  | 7.8881e-07 | 1.0307e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_1B | coal | 127 |  | 54081 | Spruance Genco, LLC | VA | GEN1 | 1B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00050125 | 7.8881e-07 | 1.0307e-05 |  |  | 7.8881e-07 | 1.0307e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
2451_Unit 1 | coal | 128 |  | 2451 | San Juan | NM | Unit 1 | Unit 1 | Conventional Boiler | Wall firing - front firing | 370 | 3707 | 10.0189 | subbituminous | subbituminous | 0.00088884 | 1.0505e-06 | 1.0524e-05 |  |  | 1.0505e-06 | 1.0524e-05 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, pulse | 2008-10-01 | SO2 control | Wet FGD - Spray Type | 1998-05-01
1167_8 | coal | 129 |  | 1167 | Muscatine #1 | IA | 8 | 8 | Conventional Boiler | Cyclone firing | 75 | 823 | 10.9733 | subbituminous | subbituminous | 0.00017432 | 9.6746e-07 | 1.0616e-05 |  |  | 9.6746e-07 | 1.0616e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1999-03-01
10641_B2 | coal | 130 |  | 10641 | Cambria Cogen | PA | 002 | B2 | Fluidized bed firing | Fluidized bed firing | 49 | 560 | 11.4286 | coal refuse (culm or gob), other--natural gas | coal refuse (culm or gob), other--natural gas | 0.0031798 | 9.4512e-07 | 1.0801e-05 |  |  | 9.4512e-07 | 1.0801e-05 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
3138_3 | coal | 131 |  | 3138 | New Castle Plant | PA | NC3-2 | 3 | Conventional Boiler | Wall firing - front firing | 98 | 1025 | 10.4592 | coal - bituminous | bituminous |  |  |  | 1.0528e-06 | 1.1011e-05 | 1.0528e-06 | 1.1011e-05 | NOx control | Selective Noncatalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
1047_4 | coal | 132 |  | 1047 | Lansing | IA | Unit 4 | 4 | Conventional Boiler | Turbo | 264.2 | 2626 | 9.9394 | coal - subbituminous | subbituminous |  |  |  | 1.11e-06 | 1.1033e-05 | 1.11e-06 | 1.1033e-05 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-04-01
492_5 | coal | 133 |  | 492 | Martin Drake | CO | Unit 5 - Coal | 5 | Conventional Boiler | Wall firing - front firing | 55 | 570 | 10.3636 | subbituminous | subbituminous | 0.00035939 | 1.069e-06 | 1.1078e-05 |  |  | 1.069e-06 | 1.1078e-05 | PM control | Fabric Filter, reverse air | 1998-05-01
3287_MCM1 | coal | 134 |  | 3287 | McMeekin | SC | MCM001 | MCM1 | Conventional Boiler | Tangential firing | 135 | 1143.5 | 8.4704 | bituminous | bituminous | 0.00063398 | 1.3181e-06 | 1.1165e-05 |  |  | 1.3181e-06 | 1.1165e-05 | PM control | Fabric Filter, unspecified | 1993-04-01
54755_BLR2 | coal | 135 |  | 54755 | Roanoke Valley II | NC | Boiler 2 | BLR2 | Conventional Boiler | Wall firing - front firing | 50 | 560 | 11.2 | bituminous | bituminous | 0.00095849 | 1.0049e-06 | 1.1255e-05 |  |  | 1.0049e-06 | 1.1255e-05 | NOx control | Selective Noncatalytic Reduction | 1995-06-01 | SO2 control | Dry FGD - Spray Dryer | 1995-06-01 | PM control | Fabric Filter, pulse | 1995-06-01
55749_PC1 | coal | 136 |  | 55749 | Hardin Generator Project | MT | PC1 | PC1 | Conventional Boiler | Wall firing - unspecified | 119 | 1304 | 10.958 | bituminous | bituminous | 0.00037981 | 1.0484e-06 | 1.1488e-05 |  |  | 1.0484e-06 | 1.1488e-05 | NOx control | Selective Catalytic Reduction | 2006-04-01 | Other control | Activated carbon injection |  | SO2 control | Dry FGD - Spray Dryer | 2006-04-01 | PM control | Fabric Filter, pulse | 2006-04-01
2716_1 | coal | 137 |  | 2716 | W.H. Weatherspoon Plant | NC | Wea_Cfg_1 | 1 | Conventional Boiler | Wall firing - front firing | 53 | 472 | 8.9057 | bituminous | bituminous | 0.00075047 | 1.3095e-06 | 1.1662e-05 |  |  | 1.3095e-06 | 1.1662e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
2716_2 | coal | 138 |  | 2716 | W.H. Weatherspoon Plant | NC | Wea_Cfg_1 | 2 | Conventional Boiler | Wall firing - front firing | 53 | 472 | 8.9057 | bituminous | bituminous | 0.00075047 | 1.3095e-06 | 1.1662e-05 |  |  | 1.3095e-06 | 1.1662e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
130_1 | coal | 139 |  | 130 | Cross | SC | C1 | 1 | Conventional Boiler | Wall firing - opposed firing | 610 | 6502 | 10.659 | bituminous | bituminous | 0.00031307 | 1.1159e-06 | 1.1895e-05 |  |  | 1.1159e-06 | 1.1895e-05 | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-05-01 | SO2 control | Wet FGD - Spray Type | 1995-05-01
988_4 | coal | 140 |  | 988 | Tanners Creek | IN | TC-4 | 4 | Conventional Boiler | Cyclone firing | 579.7 | 4990 | 8.6079 | subbituminous, bituminous | subbituminous, bituminous | 0.00026937 | 1.4723e-06 | 1.2673e-05 |  |  | 1.4723e-06 | 1.2673e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-11-01
3775_1 | coal | 141 |  | 3775 | Clinch River | VA | CR-1 | 1 | Conventional Boiler | Vertical firing | 230 | 2100.9 | 9.1343 | bituminous | bituminous | 0.00064868 | 1.4003e-06 | 1.2791e-05 |  |  | 1.4003e-06 | 1.2791e-05 | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1975-02-01
50974_#2 CFB Boiler | coal | 142 |  | 50974 | Scrubgrass Generating Company L.P. | PA | Gen 1 | #2 CFB Boiler | Fluidized bed firing | Fluidized bed firing | 48.5 | 600 | 12.3711 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0082039 | 6.4563e-06 | 8.32e-05 | 1e-06 | 1.2887e-05 | 1e-06 | 1.2887e-05 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01
50974_#1 CFB boiler | coal | 143 |  | 50974 | Scrubgrass Generating Company L.P. | PA | Gen 1 | #1 CFB boiler | Fluidized bed firing | Fluidized bed firing | 48.5 | 650 | 13.4021 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0082039 | 6.4563e-06 | 8.32e-05 | 1e-06 | 1.2887e-05 | 1e-06 | 1.2887e-05 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | NOx control | Selective Noncatalytic Reduction | 1999-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | PM control | Fabric Filter, pulse | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1993-06-01
6113_4 | coal | 144 |  | 6113 | Gibson | IN | 4 | 4 | Conventional Boiler | Wall firing - opposed firing | 661 | 6265 | 9.4781 | bituminous | bituminous |  |  |  | 1.3776e-06 | 1.3057e-05 | 1.3776e-06 | 1.3057e-05 | NOx control | Selective Catalytic Reduction | 2003-04-01 | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01 | SO2 control | Wet FGD - Tray Type | 1994-12-01
1008_2 | coal | 145 |  | 1008 | R. Gallagher | IN | 2-2007 | 2 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | 9.7333 | coal - bituminous | bituminous |  |  |  | 1.3928e-06 | 1.3556e-05 | 1.3928e-06 | 1.3556e-05 | PM control | Fabric Filter, shake and deflate | 2007-12-01
3118_2 | coal | 146 |  | 3118 | Conemaugh | PA | CON-2 | 2 | Conventional Boiler | Tangential firing | 936 | 8985 | 9.5994 | bituminous | bituminous |  |  |  | 1.4863e-06 | 1.4268e-05 | 1.4863e-06 | 1.4268e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Spray Type | 1995-11-01
527_1 | coal | 147 |  | 527 | Nucla | CO | 001 | 1 | Fluidized bed firing | Fluidized bed firing | 110 | 1032 | 9.3818 | bituminous | bituminous | 0.0010538 | 1.5908e-06 | 1.4925e-05 |  |  | 1.5908e-06 | 1.4925e-05 | NOx control | Selective Noncatalytic Reduction | 2006-07-01 | PM control | Fabric Filter, shake and deflate | 1987-06-01
2378_2 | coal | 148 |  | 2378 | BL England | NJ | 2 Coal w or w/o TDF | 2 | Conventional Boiler | Cyclone firing | 167.3 | 1600 | 9.5637 | bituminous | bituminous |  |  |  | 1.5833e-06 | 1.5142e-05 | 1.5833e-06 | 1.5142e-05 | NOx control | Selective Noncatalytic Reduction | 1998-06-01 | Other control | Activated carbon injection | 2007-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
981_3 | coal | 149 |  | 981 | State Line | IN | Unit 3 | 3 | Conventional Boiler | Tangential firing | 216 | 2380 | 11.0185 | bituminous | bituminous | 0.00042017 | 1.4339e-06 | 1.5799e-05 |  |  | 1.4339e-06 | 1.5799e-05 | PM control | Fabric Filter, pulse | 1999-01-01
54081_4B | coal | 150 |  | 54081 | Spruance Genco, LLC | VA | GEN4 | 4B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00060532 | 1.2123e-06 | 1.5841e-05 | 2.452e-06 | 3.2038e-05 | 1.2123e-06 | 1.5841e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_4A | coal | 151 |  | 54081 | Spruance Genco, LLC | VA | GEN4 | 4A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00060532 | 1.2123e-06 | 1.5841e-05 | 2.452e-06 | 3.2038e-05 | 1.2123e-06 | 1.5841e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
1710_Unit 2 | coal | 152 |  | 1710 | Consumers Energy - J.H. Campbell | MI | JHC2-Conf | Unit 2 | Conventional Boiler | Wall firing - front firing | 374 | 3392 | 9.0695 | subbituminous, bituminous | subbituminous, bituminous | 0.00041608 | 1.8067e-06 | 1.6386e-05 |  |  | 1.8067e-06 | 1.6386e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-12-01
1710_Unit 1 | coal | 153 |  | 1710 | Consumers Energy - J.H. Campbell | MI | JHC1-Conf | Unit 1 | Conventional Boiler | Tangential firing | 274 | 2561 | 9.3467 | subbituminous | subbituminous | 0.0001662 | 1.8067e-06 | 1.6887e-05 |  |  | 1.8067e-06 | 1.6887e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2001-07-01
3138_5 | coal | 154 |  | 3138 | New Castle Plant | PA | NC5-2 | 5 | Conventional Boiler | Wall firing - front firing | 143.3 | 1441 | 10.0558 | coal - bituminous | bituminous |  |  |  | 1.76e-06 | 1.7698e-05 | 1.76e-06 | 1.7698e-05 | NOx control | Selective Noncatalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
642_1 | coal | 155 |  | 642 | Scholz | FL | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 49 | 581.091 | 11.859 | bituminous | bituminous | 0.000838 | 1.5356e-06 | 1.8211e-05 |  |  | 1.5356e-06 | 1.8211e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01
887_1 | coal | 156 |  | 887 | Joppa Steam | IL | 1 | 1 | Conventional Boiler | Tangential firing | 183.3 | 1800 | 9.82 | subbituminous | subbituminous | 0.00021179 | 1.8556e-06 | 1.8222e-05 |  |  | 1.8556e-06 | 1.8222e-05 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-01-01
4042_3 | coal | 157 |  | 4042 | Valley | WI | VAPP-B3 | 3 | Conventional Boiler | Wall firing - front firing | 72 | 868 | 12.0556 | bituminous | bituminous | 0.00038002 | 1.6039e-06 | 1.9335e-05 |  |  | 1.6039e-06 | 1.9335e-05 | PM control | Fabric Filter, pulse | 1995-06-01
642_2 | coal | 158 |  | 642 | Scholz | FL | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 49 | 644.742 | 13.158 | bituminous | bituminous | 0.000838 | 1.5356e-06 | 2.0206e-05 |  |  | 1.5356e-06 | 2.0206e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2007-12-01
10075_2 | coal | 159 |  | 10075 | Taconite Harbor Energy Center | MN | THEC2 | 2 | Conventional Boiler | Tangential firing | 79.2 | 913 | 11.5278 | bituminous | bituminous | 0.00016376 | 1.7913e-06 | 2.0649e-05 |  |  | 1.7913e-06 | 2.0649e-05 | NOx control |  | 2007-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2007-01-01
2094_3 | coal | 160 |  | 2094 | Sibley | MO | 3 | 3 | Conventional Boiler | Cyclone firing | 419 | 4094.1 | 9.7711 | subbituminous, bituminous | subbituminous, bituminous | 0.00029355 | 2.1273e-06 | 2.0787e-05 |  |  | 2.1273e-06 | 2.0787e-05 | NOx control | Selective Catalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-04-01
3280_CAN3 | coal | 161 |  | 3280 | Canadys Steam | SC | CAN003 | CAN3 | Conventional Boiler | Wall firing - unspecified | 185 | 1824.5 | 9.8622 | bituminous | bituminous | 0.00062453 | 2.1183e-06 | 2.0891e-05 |  |  | 2.1183e-06 | 2.0891e-05 | PM control | Fabric Filter, unspecified | 1998-07-01
10075_1 | coal | 162 |  | 10075 | Taconite Harbor Energy Center | MN | THEC1 | 1 | Conventional Boiler | Tangential firing | 83 | 847 | 10.2048 | bituminous | bituminous | 0.00018783 | 2.0594e-06 | 2.1016e-05 |  |  | 2.0594e-06 | 2.1016e-05 | NOx control | Selective Noncatalytic Reduction | 2008-01-01 | Other control | Dry sorbent injection | 2008-01-01 | PM control | Electrostatic precipitator, cold side, unspecified | 2008-01-01
4041_7 | coal | 163 |  | 4041 | South Oak Creek | WI | OCPP-B7 | 7 | Conventional Boiler | Tangential firing | 320 | 2856 | 8.925 | subbituminous | subbituminous | 0.00017461 | 2.4227e-06 | 2.1622e-05 |  |  | 2.4227e-06 | 2.1622e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1992-07-01
884_4 | coal | 164 |  | 884 | Will County | IL | WC4CONFIG | 4 | Conventional Boiler | Tangential firing | 542 | 5254.53 | 9.6947 | subbituminous | subbituminous | 0.00025739 | 2.2532e-06 | 2.1844e-05 |  |  | 2.2532e-06 | 2.1844e-05 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1963-06-01
6664_101 | coal | 165 |  | 6664 | Louisa | IA | 101 | 101 | Conventional Boiler | Wall firing - unspecified | 805 | 8624 | 10.713 | subbituminous | subbituminous | 0.00024431 | 2.0583e-06 | 2.2051e-05 | 1.06e-05 | 0.00011356 | 2.0583e-06 | 2.2051e-05 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-12-01 | PM control | Fabric Filter, pulse | 2007-12-01
47_4 | coal | 166 |  | 47 | Colbert | AL | 4 | 4 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | 10.605 | subbituminous, bituminous | subbituminous, bituminous | 0.00026332 | 2.1675e-06 | 2.2987e-05 |  |  | 2.1675e-06 | 2.2987e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-01-01
2094_1 | coal | 167 |  | 2094 | Sibley | MO | 1 | 1 | Conventional Boiler | Cyclone firing | 55 | 609.6 | 11.0836 | subbituminous, bituminous | subbituminous, bituminous | 0.00029355 | 2.1273e-06 | 2.3579e-05 |  |  | 2.1273e-06 | 2.3579e-05 | NOx control | Selective Noncatalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-01-01
2079_5A | coal | 168 |  | 2079 | Hawthorn | MO | 5A | 5A | Conventional Boiler | Wall firing - opposed firing | 594 | 6600 | 11.1111 | subbituminous, bituminous | subbituminous, bituminous | 0.00019194 | 2.1791e-06 | 2.4212e-05 |  |  | 2.1791e-06 | 2.4212e-05 | NOx control | Selective Catalytic Reduction | 2001-05-01 | SO2 control | Dry FGD - Spray Dryer | 2001-05-01 | PM control | Fabric Filter, pulse | 2001-05-01
3942_2 | coal | 169 |  | 3942 | Albright Power Station | WV | Unit_2 | 2 | Conventional Boiler | Wall firing - unspecified | 81 | 643 | 7.9383 | bituminous | bituminous | 0.00092612 | 3.0663e-06 | 2.4341e-05 |  |  | 3.0663e-06 | 2.4341e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
54081_3B | coal | 170 |  | 54081 | Spruance Genco, LLC | VA | GEN3 | 3B | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00052263 | 1.992e-06 | 2.6028e-05 |  |  | 1.992e-06 | 2.6028e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
54081_3A | coal | 171 |  | 54081 | Spruance Genco, LLC | VA | GEN3 | 3A | Conventional Boiler | Stoker - underfeed | 28.7 | 375 | 13.0662 | bituminous | bituminous | 0.00052263 | 1.992e-06 | 2.6028e-05 |  |  | 1.992e-06 | 2.6028e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | SO2 control | Dry FGD - Spray Dryer | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01 | PM control | Fabric Filter, pulse | 1992-05-01
2094_2 | coal | 172 |  | 2094 | Sibley | MO | 2 | 2 | Conventional Boiler | Cyclone firing | 51 | 627.3 | 12.3 | subbituminous, bituminous | subbituminous, bituminous | 0.00029355 | 2.1273e-06 | 2.6166e-05 |  |  | 2.1273e-06 | 2.6166e-05 | NOx control | Selective Noncatalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-01-01
47_3 | coal | 173 |  | 47 | Colbert | AL | 3 | 3 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | 10.605 | other--subbituminous/bituminous blend | other--subbituminous/bituminous blend | 0.00028973 | 2.4785e-06 | 2.6285e-05 |  |  | 2.4785e-06 | 2.6285e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-05-01
3118_1 | coal | 174 |  | 3118 | Conemaugh | PA | CON-1 | 1 | Conventional Boiler | Tangential firing | 936 | 8985 | 9.5994 | bituminous | bituminous |  |  |  | 2.8067e-06 | 2.6942e-05 | 2.8067e-06 | 2.6942e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-05-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
3131_4 | coal | 175 |  | 3131 | Shawville | PA | SHAW4-2 | 4 | Conventional Boiler | Tangential firing | 188 | 1794 | 9.5426 | bituminous | bituminous | 0.00090428 | 5.8665e-05 | 0.00055981 | 2.87e-06 | 2.7387e-05 | 2.87e-06 | 2.7387e-05 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
3131_3 | coal | 176 |  | 3131 | Shawville | PA | SHAW3-2 | 3 | Conventional Boiler | Tangential firing | 188 | 1794 | 9.5426 | bituminous | bituminous | 0.00090428 | 5.8665e-05 | 0.00055981 | 2.87e-06 | 2.7387e-05 | 2.87e-06 | 2.7387e-05 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1959-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
3161_2 | coal | 177 |  | 3161 | Eddystone Generating Station | PA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 339 | 2808 | 8.2832 | bituminous | bituminous | 0.00033197 | 3.6615e-06 | 3.0329e-05 | 3.3133e-06 | 2.7445e-05 | 3.3133e-06 | 2.7445e-05 | NOx control | Selective Noncatalytic Reduction | 2003-06-01 | PM control | Multiple cyclone | 1960-11-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1960-11-01 | PM control | PM scrubber - Venturi | 1982-12-01 | SO2 control | Wet FGD - Spray Type | 1982-12-01
10151_BLR1A | coal | 178 |  | 10151 | Grant Town Power Plant | WV | GEN1 | BLR1A | Fluidized bed firing | Fluidized bed firing | 47.5 | 675 | 14.2105 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0014988 | 2.0624e-06 | 2.9307e-05 |  |  | 2.0624e-06 | 2.9307e-05 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | PM control | Fabric Filter, pulse | 1992-07-01 | PM control | Fabric Filter, pulse | 2005-05-01
10151_BLR1B | coal | 179 |  | 10151 | Grant Town Power Plant | WV | GEN1 | BLR1B | Fluidized bed firing | Fluidized bed firing | 47.5 | 675 | 14.2105 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0014988 | 2.0624e-06 | 2.9307e-05 |  |  | 2.0624e-06 | 2.9307e-05 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 1992-07-01 | PM control | Fabric Filter, pulse | 1992-07-01 | PM control | Fabric Filter, pulse | 2005-05-01
892_Unit 1 | coal | 180 |  | 892 | Hennepin Power Station | IL | 001 | Unit 1 | Conventional Boiler | Tangential firing | 75 | 776 | 10.3467 | subbituminous | subbituminous | 0.0002165 | 2.8625e-06 | 2.9617e-05 |  |  | 2.8625e-06 | 2.9617e-05 | PM control | Electrostatic precipitator, cold side, unspecified | 1972-08-01 | Other control | Activated carbon injection | 2009-12-01 | PM control | Fabric Filter, unspecified | 2008-10-01
50776_BLR2 | coal | 181 |  | 50776 | PANTHER CREEK ENERGY FACILITY | PA | BG2 | BLR2 | Fluidized bed firing | Fluidized bed firing | 46.5 | 600 | 12.9032 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.002716 | 2.3008e-06 | 2.9688e-05 |  |  | 2.3008e-06 | 2.9688e-05 | NOx control | Selective Noncatalytic Reduction | 1992-10-01 | PM control | Fabric Filter, pulse | 1992-10-01
50776_BLR1 | coal | 182 |  | 50776 | PANTHER CREEK ENERGY FACILITY | PA | BG1 | BLR1 | Fluidized bed firing | Fluidized bed firing | 46.5 | 600 | 12.9032 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.002716 | 2.3008e-06 | 2.9688e-05 |  |  | 2.3008e-06 | 2.9688e-05 | NOx control | Selective Noncatalytic Reduction | 1992-10-01 | PM control | Fabric Filter, pulse | 1992-10-01
492_7 | coal | 183 |  | 492 | Martin Drake | CO | Unit 7 - Coal | 7 | Conventional Boiler | Wall firing - front firing | 141 | 1475 | 10.461 | subbituminous, bituminous | subbituminous, bituminous | 0.0005029 | 2.868e-06 | 3.0002e-05 |  |  | 2.868e-06 | 3.0002e-05 | PM control | Fabric Filter, reverse air | 1993-11-01
2403_U2 | coal | 184 |  | 2403 | PSEG Hudson Generating Station | NJ | HUDU2E2PT2OS1-Coal | U2 | Conventional Boiler | Wall firing - opposed firing | 659.7 | 6600 | 10.0045 | natural gas | subbituminous |  |  |  | 3.0333e-06 | 3.0347e-05 | 3.0333e-06 | 3.0347e-05 | NOx control | Selective Noncatalytic Reduction | 1999-03-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-12-01
892_Unit 2 | coal | 185 |  | 892 | Hennepin Power Station | IL | 002 | Unit 2 | Conventional Boiler | Tangential firing | 234 | 2500 | 10.6838 | subbituminous | subbituminous | 0.0002165 | 2.8625e-06 | 3.0582e-05 |  |  | 2.8625e-06 | 3.0582e-05 | PM control | Electrostatic precipitator, cold side, unspecified | 1974-06-01 | Other control | Activated carbon injection | 2009-06-01 | PM control | Fabric Filter, unspecified | 2008-12-01
3152_4 | coal | 186 |  | 3152 | Sunbury Generation LP | PA | Boiler 4 | 4 | Conventional Boiler | Wall firing - front firing | 128 | 1360 | 10.625 | bituminous | bituminous | 0.00050125 | 2.9645e-06 | 3.1498e-05 |  |  | 2.9645e-06 | 3.1498e-05 | Other control | Other (specify): SO3 injection | 1980-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-06-01
864_5 | coal | 187 |  | 864 | Meredosia | IL | 005 | 5 | Conventional Boiler | Tangential firing | 204 | 2784 | 13.6471 | subbituminous | subbituminous | 0.00020224 | 2.3292e-06 | 3.1787e-05 |  |  | 2.3292e-06 | 3.1787e-05 | Other control | Activated carbon injection | 2009-08-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1992-11-01
10603_031 | coal | 188 |  | 10603 | Ebensburg Power Company | PA | EPC01 | 031 | Fluidized bed firing | Fluidized bed firing | 58 | 830 | 14.3103 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0094723 | 7.2598e-06 | 0.00010389 | 2.27e-06 | 3.2484e-05 | 2.27e-06 | 3.2484e-05 | PM control | Fabric Filter, pulse | 1990-11-01
52007_BLR1 | coal | 189 |  | 52007 | Mecklenburg Power Station | VA | Unit 1 & 2 | BLR1 | Conventional Boiler | Wall firing - front firing | 76 | 916 | 12.0526 | bituminous | bituminous | 0.0010179 | 2.8561e-06 | 3.4462e-05 |  |  | 2.8561e-06 | 3.4462e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01
52007_BLR2 | coal | 190 |  | 52007 | Mecklenburg Power Station | VA | Unit 1 & 2 | BLR2 | Conventional Boiler | Wall firing - front firing | 76 | 918 | 12.0789 | bituminous | bituminous | 0.0010179 | 2.8561e-06 | 3.4462e-05 |  |  | 2.8561e-06 | 3.4462e-05 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | SO2 control | Dry FGD - Spray Dryer | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01 | PM control | Fabric Filter, pulse | 1992-11-01
6041_1 | coal | 191 |  | 6041 | H L Spurlock Station | KY | Unit 01 | 1 | Conventional Boiler | Wall firing - opposed firing | 344 | 3641 | 10.5843 | bituminous | bituminous | 0.0011469 | 3.3462e-06 | 3.5417e-05 |  |  | 3.3462e-06 | 3.5417e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2003-05-01 | NOx control | Selective Catalytic Reduction | 2003-05-01 | SO2 control | Wet FGD - Unspecified | 2009-04-01 | Other control | Wet electrostatic precipitator | 2009-04-01
7343_4 | coal | 192 |  | 7343 | George Neal South | IA | 4 | 4 | Conventional Boiler | Wall firing - unspecified | 682 | 6900 | 10.1173 |  | Subbituminous |  |  |  | 3.63e-06 | 3.6726e-05 | 3.63e-06 | 3.6726e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1989-11-01
6098_001 | coal | 193 |  | 6098 | Big Stone | SD | 001 | 001 | Conventional Boiler | Cyclone firing | 495 | 5309 | 10.7253 | subbituminous | subbituminous | 0.00017163 | 3.4555e-06 | 3.7061e-05 |  |  | 3.4555e-06 | 3.7061e-05 | PM control | Fabric Filter, pulse | 2007-12-01
10771_10771-01 | coal | 194 |  | 10771 | Hopewell | VA | 1 & 2 | 10771-01 | Conventional Boiler | Stoker - spreader | 34 | 433 | 12.7353 | bituminous | bituminous | 0.00092946 | 2.967e-06 | 3.7306e-05 |  |  | 2.967e-06 | 3.7306e-05 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01
10771_10771-02 | coal | 195 |  | 10771 | Hopewell | VA | 1 & 2 | 10771-02 | Conventional Boiler | Stoker - underfeed | 34 | 422 | 12.4118 | bituminous | bituminous | 0.00092946 | 2.967e-06 | 3.7306e-05 |  |  | 2.967e-06 | 3.7306e-05 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | NOx control | Selective Noncatalytic Reduction | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | PM control | Multiple cyclone | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | SO2 control | Dry FGD - Spray Dryer | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01 | PM control | Fabric Filter, pulse | 1992-04-01
10743_CFB1 | coal | 196 |  | 10743 | Morgantown Energy Facility | WV | Unit 1&2 | CFB1 | Fluidized bed firing | Fluidized bed firing | 29 | 457 | 15.7586 | bituminous | bituminous | 0.0024342 | 2.3841e-06 | 3.7406e-05 |  |  | 2.3841e-06 | 3.7406e-05 | PM control | Fabric Filter, pulse | 1992-01-01 | PM control | Fabric Filter, pulse | 1992-01-01
10743_CFB2 | coal | 197 |  | 10743 | Morgantown Energy Facility | WV | Unit 1&2 | CFB2 | Fluidized bed firing | Fluidized bed firing | 29 | 453 | 15.6207 | bituminous | bituminous | 0.0024342 | 2.3841e-06 | 3.7406e-05 |  |  | 2.3841e-06 | 3.7406e-05 | PM control | Fabric Filter, pulse | 1992-01-01 | PM control | Fabric Filter, pulse | 1992-01-01
8023_1 | coal | 198 |  | 8023 | Columbia | WI | Unit 1 | 1 | Conventional Boiler | Tangential firing | 590.3 | 6090 | 10.3168 | coal - subbituminous | subbituminous |  |  |  | 3.63e-06 | 3.745e-05 | 3.63e-06 | 3.745e-05 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1975-03-01
897_Unit 2 | coal | 199 |  | 897 | Vermilion | IL | 002 | Unit 2 | Conventional Boiler | Tangential firing | 110 | 1076 | 9.7818 | subbituminous | subbituminous | 0.00020438 | 3.8822e-06 | 3.7975e-05 |  |  | 3.8822e-06 | 3.7975e-05 | PM control | Electrostatic precipitator, unspecified | 1974-01-01 | Other control | Activated carbon injection | 2007-05-01 | PM control | Fabric Filter, unspecified | 2007-05-01
3131_2 | coal | 200 |  | 3131 | Shawville | PA | SHAW2-2 | 2 | Conventional Boiler | Wall firing - front firing | 125 | 1349 | 10.792 | coal - bituminous | bituminous |  |  |  | 3.63e-06 | 3.9175e-05 | 3.63e-06 | 3.9175e-05 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1954-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-06-01
1104_1 | coal | 201 |  | 1104 | Burlington | IA | Unit 1 | 1 | Conventional Boiler | Tangential firing | 212.02 | 2228 | 10.5084 | coal - subbituminous | subbituminous |  |  |  | 3.78e-06 | 3.9722e-05 | 3.78e-06 | 3.9722e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-06-01
3251_1 | coal | 202 |  | 3251 | HB Robinson / Darlington Electric Power Plant | SC | Rob_Cfg_1 | 1 | Conventional Boiler | Tangential firing | 187 | 1733 | 9.2674 | bituminous | bituminous | 0.00039227 | 4.3432e-06 | 4.025e-05 |  |  | 4.3432e-06 | 4.025e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-07-01
883_8 | coal | 203 |  | 883 | Waukegan | IL | WK8CONFIG | 8 | Conventional Boiler | Tangential firing | 383 | 3960.892 | 10.3418 | subbituminous | subbituminous | 0.00016709 | 4.0178e-06 | 4.1551e-05 |  |  | 4.0178e-06 | 4.1551e-05 | Other control | Activated carbon injection | 2008-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1962-07-01
1241_2 | coal | 204 |  | 1241 | La Cygne | KS | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 685 | 7700 | 11.2409 | subbituminous | subbituminous | 0.00022021 | 3.7716e-06 | 4.2396e-05 |  |  | 3.7716e-06 | 4.2396e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
6254_1 | coal | 205 |  | 6254 | Ottumwa | IA | Unit 1 | 1 | Conventional Boiler | Tangential firing | 765.1 | 7990 | 10.4431 | coal - subbituminous | subbituminous |  |  |  | 4.22e-06 | 4.407e-05 | 4.22e-06 | 4.407e-05 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1981-05-01
897_Unit 1 | coal | 206 |  | 897 | Vermilion | IL | 001 | Unit 1 | Conventional Boiler | Tangential firing | 72 | 831 | 11.5417 | subbituminous | subbituminous | 0.00020438 | 3.8822e-06 | 4.4808e-05 |  |  | 3.8822e-06 | 4.4808e-05 | PM control | Electrostatic precipitator, unspecified | 1973-06-01 | Other control | Activated carbon injection | 2007-05-01 | PM control | Fabric Filter, unspecified | 2007-05-01
6076_3 | coal | 207 |  | 6076 | Colstrip | MT | Unit3 | 3 | Conventional Boiler | Tangential firing | 805 | 7573 | 9.4075 | subbituminous | subbituminous | 0.00048814 | 4.7694e-06 | 4.4868e-05 |  |  | 4.7694e-06 | 4.4868e-05 | Other control | Activated carbon injection | 2009-12-01 | SO2 control | Wet FGD - Venturi Type | 1984-01-01 | PM control | PM scrubber - Venturi | 1984-01-01
54035_BLR1 | coal | 208 |  | 54035 | Roanoke Valley I | NC | Boiler 1 | BLR1 | Conventional Boiler | Wall firing - front firing | 182 | 1700 | 9.3407 | bituminous | bituminous | 0.0010722 | 4.8313e-06 | 4.5128e-05 |  |  | 4.8313e-06 | 4.5128e-05 | SO2 control | Dry FGD - Spray Dryer | 1994-05-01 | PM control | Fabric Filter, reverse air | 1994-05-01
1295_2 | coal | 209 |  | 1295 | Quindaro | KS | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 119.8 | 1394 | 11.6361 | bituminous | bituminous | 0.00016693 | 3.9254e-06 | 4.5676e-05 |  |  | 3.9254e-06 | 4.5676e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1986-05-01
2708_5 | coal | 210 |  | 2708 | Cape Fear Steam Electric Plant | NC | Cap_Cfg_5b | 5 | Conventional Boiler | Tangential firing | 153 | 1242 | 8.1176 | bituminous | bituminous | 0.00022647 | 5.8286e-06 | 4.7315e-05 |  |  | 5.8286e-06 | 4.7315e-05 | NOx control | Selective Noncatalytic Reduction | 2006-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-11-01
1943_002 | coal | 211 |  | 1943 | Hoot Lake | MN | 2 | 002 | Conventional Boiler | Tangential firing | 60.7 | 747.2 | 12.3097 | subbituminous | subbituminous | 9.6038e-05 | 4.1259e-06 | 5.0789e-05 |  |  | 4.1259e-06 | 5.0789e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-06-01
1250_3 | coal | 212 |  | 1250 | Lawrence Energy Center | KS | 3 | 3 | Conventional Boiler | Tangential firing | 58 | 645 | 11.1207 | bituminous | bituminous | 0.00018561 | 4.5987e-06 | 5.1141e-05 |  |  | 4.5987e-06 | 5.1141e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
4042_1 | coal | 213 |  | 4042 | Valley | WI | VAPP-B1 | 1 | Conventional Boiler | Wall firing - front firing | 72 | 868 | 12.0556 | bituminous | bituminous | 0.00040748 | 4.4693e-06 | 5.388e-05 |  |  | 4.4693e-06 | 5.388e-05 | PM control | Fabric Filter, pulse | 1994-06-01
976_123 | coal | 214 |  | 976 | Marion Generating Station | IL | 123 | 123 | Fluidized bed firing | Fluidized bed firing | 120 | 1250 | 10.4167 | bituminous | bituminous | 0.0032672 | 5.3424e-06 | 5.565e-05 |  |  | 5.3424e-06 | 5.565e-05 | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified
1048_2 | coal | 215 |  | 1048 | ML Kapp | IA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 229 | 2332 | 10.1834 | coal - subbituminous | subbituminous |  |  |  | 5.68e-06 | 5.7842e-05 | 5.68e-06 | 5.7842e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-07-01
990_60 | coal | 216 |  | 990 | Harding Street | IN | 60s | 60 | Conventional Boiler | Tangential firing | 112 | 1017 | 9.0804 | bituminous | bituminous | 0.0010142 | 6.9041e-06 | 6.2692e-05 |  |  | 6.9041e-06 | 6.2692e-05 | NOx control | Selective Noncatalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-12-01
1363_4 | coal | 217 |  | 1363 | Cane Run | KY | CR4 | 4 | Conventional Boiler | Wall firing - front firing | 168 | 2310 | 13.75 | bituminous | bituminous | 0.0011627 | 4.7726e-06 | 6.5623e-05 |  |  | 4.7726e-06 | 6.5623e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1963-06-01 | SO2 control | Wet FGD - Spray Type | 1976-12-01
874_5 | coal | 218 |  | 874 | Joliet 9 | IL | JOL5 CONFIG | 5 | Conventional Boiler | Cyclone firing | 326 | 3572.378 | 10.9582 | subbituminous | subbituminous | 0.00016513 | 6.3056e-06 | 6.9098e-05 |  |  | 6.3056e-06 | 6.9098e-05 | Other control | Activated carbon injection | 2009-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-03-01
2364_2 | coal | 219 |  | 2364 | Merrimack Station | NH | mk2 | 2 | Conventional Boiler | Cyclone firing | 337 | 3017 | 8.9525 | bituminous | bituminous | 0.00022283 | 7.7833e-06 | 6.9681e-05 |  |  | 7.7833e-06 | 6.9681e-05 | NOx control | Selective Catalytic Reduction | 1995-05-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1999-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-05-01
991_6 | coal | 220 |  | 991 | Eagle Valley | IN | 6 | 6 | Conventional Boiler | Tangential firing | 105 | 1017 | 9.6857 | bituminous | bituminous | 0.0011631 | 7.2803e-06 | 7.0515e-05 |  |  | 7.2803e-06 | 7.0515e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-12-01
3131_1 | coal | 221 |  | 3131 | Shawville | PA | SHAW1-2 | 1 | Conventional Boiler | Wall firing - front firing | 125 | 1349 | 10.792 | coal - bituminous | bituminous |  |  |  | 6.6e-06 | 7.1227e-05 | 6.6e-06 | 7.1227e-05 | NOx control | Selective Noncatalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1954-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-06-01
3130_1 | coal | 222 |  | 3130 | Seward | PA | SEW-1 | 1 | Fluidized bed firing | Fluidized bed firing | 292.5 | 3100 | 10.5983 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0050912 | 6.9533e-06 | 7.3693e-05 |  |  | 6.9533e-06 | 7.3693e-05 | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Fabric Filter, pulse | 2004-03-01
3130_2 | coal | 223 |  | 3130 | Seward | PA | SEW-1 | 2 | Fluidized bed firing | Fluidized bed firing | 292.5 | 3100 | 10.5983 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0050912 | 6.9533e-06 | 7.3693e-05 |  |  | 6.9533e-06 | 7.3693e-05 | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Fabric Filter, pulse | 2004-03-01
1091_2 | coal | 224 |  | 1091 | George Neal North | IA | 2 | 2 | Conventional Boiler | Wall firing - unspecified | 325 | 3081 | 9.48 |  | Subbituminous |  |  |  | 7.882e-06 | 7.4721e-05 | 7.882e-06 | 7.4721e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1977-11-01
7253_3 | coal | 225 |  | 7253 | Richard Gorsuch | OH | UNIT3 | 3 | Conventional Boiler | Radiant | 53.3 | 553 | 10.3752 | bituminous | bituminous | 0.00090809 | 7.2109e-06 | 7.4815e-05 |  |  | 7.2109e-06 | 7.4815e-05 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-06-01
990_70 | coal | 226 |  | 990 | Harding Street | IN | 70ss | 70 | Conventional Boiler | Tangential firing | 463 | 4123 | 8.905 | bituminous | bituminous | 0.00049664 | 8.5786e-06 | 7.6392e-05 |  |  | 8.5786e-06 | 7.6392e-05 | NOx control | Selective Catalytic Reduction | 2005-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-12-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
1010_6 | coal | 227 |  | 1010 | Wabash River | IN | 6 | 6 | Conventional Boiler | Tangential firing | 342 | 3059.0605 | 8.9446 | bituminous | bituminous | 0.0013972 | 9.3568e-06 | 8.3693e-05 |  |  | 9.3568e-06 | 8.3693e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-05-01
628_1 | coal | 228 |  | 628 | Crystal River Power Plant | FL | CryR_Cfg_1 | 1 | Conventional Boiler | Tangential firing | 400 | 3837 | 9.5925 | bituminous | bituminous | 5.4674e-07 | 9.6333e-06 | 9.2408e-05 |  |  | 9.6333e-06 | 9.2408e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
997_12 | coal | 229 |  | 997 | Michigan City | IN | 12 | 12 | Conventional Boiler | Cyclone firing | 495 | 4650 | 9.3939 | subbituminous | subbituminous | 0.00013368 | 9.9384e-06 | 9.3361e-05 |  |  | 9.9384e-06 | 9.3361e-05 | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1992-05-01
1385_3 | coal | 230 |  | 1385 | Dale Station | KY | 03 | 3 | Conventional Boiler | Wall firing - front firing | 80 | 944 | 11.8 | bituminous | bituminous | 0.00034574 | 7.9858e-06 | 9.4233e-05 |  |  | 7.9858e-06 | 9.4233e-05 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning
1010_4 | coal | 231 |  | 1010 | Wabash River | IN | 4 | 4 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | 10.2633 | bituminous | bituminous | 0.0013972 | 9.3568e-06 | 9.6031e-05 |  |  | 9.3568e-06 | 9.6031e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1993-10-01
1363_5 | coal | 232 |  | 1363 | Cane Run | KY | CR5 | 5 | Conventional Boiler | Wall firing - front firing | 181 | 2182 | 12.0552 | bituminous | bituminous | 0.0011993 | 7.9696e-06 | 9.6076e-05 |  |  | 7.9696e-06 | 9.6076e-05 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-03-01 | SO2 control | Wet FGD - Spray Type | 1978-05-01
2840_3 | coal | 233 |  | 2840 | Conesville | OH | CV-3 | 3 | Conventional Boiler | Wall firing - front firing | 165 | 1862 | 11.2848 | bituminous | bituminous | 0.00059415 | 8.9236e-06 | 0.0001007 |  |  | 8.9236e-06 | 0.0001007 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-01-01
1091_3 | coal | 234 |  | 1091 | George Neal North | IA | 3 | 3 | Conventional Boiler | Wall firing - unspecified | 531 | 5021 | 9.4557 |  | Subbituminous |  |  |  | 1.112e-05 | 0.00010515 | 1.112e-05 | 0.00010515 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-10-01
1073_4 | coal | 235 |  | 1073 | Prairie Creek | IA | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 148.3 | 1611 | 10.8631 | subbituminous | subbituminous |  |  |  | 1.02e-05 | 0.0001108 | 1.02e-05 | 0.0001108 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-06-01
2161_5 | coal | 236 |  | 2161 | James River Power Station | MO | Unit_5_JRPS | 5 | Conventional Boiler | Wall firing - front firing | 105 | 1010 | 9.619 | subbituminous | subbituminous | 0.00019936 | 1.1603e-05 | 0.00011161 |  |  | 1.1603e-05 | 0.00011161 | NOx control | Selective Noncatalytic Reduction | 2009-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-05-01
3115_2 | coal | 237 |  | 3115 | Titus | PA | TI-2 | 2 | Conventional Boiler | Tangential firing | 86.2 | 900 | 10.4408 | coal - bituminous | bituminous |  |  |  | 1.1583e-05 | 0.00012094 | 1.1583e-05 | 0.00012094 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-02-01
1082_3 | coal | 238 |  | 1082 | Walter Scott Jr. Energy Center | IA | 3 | 3 | Conventional Boiler | Wall firing - unspecified | 765 | 7700 | 10.0654 |  | Subbituminous |  |  |  | 1.23e-05 | 0.0001238 | 1.23e-05 | 0.0001238 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-05-01 | PM control | Fabric Filter, pulse | 2009-05-01
1167_9 | coal | 239 |  | 1167 | Muscatine #1 | IA | 9 | 9 | Conventional Boiler | Tangential firing | 175.5 | 1837 | 10.4672 | coal - subbituminous | subbituminous |  |  |  | 1.3733e-05 | 0.00014375 | 1.3733e-05 | 0.00014375 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-05-01 | SO2 control | Wet FGD - Spray Type | 1983-05-01
1218_2 | coal | 240 |  | 1218 | Fair Station | IA | U2 | 2 | Conventional Boiler | Wall firing - front firing | 44 | 465 | 10.5682 | bituminous | bituminous | 0.0010123 | 1.4066e-05 | 0.00014865 |  |  | 1.4066e-05 | 0.00014865 | Other control | Other (specify): Flue gas conditioning for opacity control | 2006-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-10-01
10143_AAB01 | coal | 241 |  | 10143 | Colver Power Project | PA | AAB01 | AAB01 | Fluidized bed firing | Fluidized bed firing | 131 | 1204 | 9.1908 | coal refuse (culm or gob) | coal refuse (culm or gob) | 0.0043412 | 1.7142e-05 | 0.00015755 |  |  | 1.7142e-05 | 0.00015755 | NOx control | Selective Noncatalytic Reduction | 1995-05-01 | PM control | Fabric Filter, pulse | 1995-05-01
6041_3 | coal | 242 |  | 6041 | H L Spurlock Station | KY | Unit 03 | 3 | Fluidized bed firing | Fluidized bed firing | 300 | 2500 | 8.3333 | bituminous | bituminous | 0.00072832 | 1.9948e-05 | 0.00016623 |  |  | 1.9948e-05 | 0.00016623 | NOx control | Selective Noncatalytic Reduction | 2005-03-01 | SO2 control | Dry FGD - Unspecified | 2005-03-01 | PM control | Fabric Filter, pulse | 2005-03-01
1091_1 | coal | 243 |  | 1091 | George Neal North | IA | 1 | 1 | Conventional Boiler | Cyclone firing | 145 | 1363 | 9.4 |  | Subbituminous |  |  |  | 1.86e-05 | 0.00017484 | 1.86e-05 | 0.00017484 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-07-01
3942_1 | coal | 244 |  | 3942 | Albright Power Station | WV | Unit_1 | 1 | Conventional Boiler | Wall firing - unspecified | 81 | 786 | 9.7037 | bituminous | bituminous | 0.00054696 | 1.8071e-05 | 0.00017536 |  |  | 1.8071e-05 | 0.00017536 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning
2732_7 | coal | 245 |  | 2732 | Riverbend | NC | 7 | 7 | Conventional Boiler | Tangential firing | 99.5 | 1059 | 10.6432 | bituminous | bituminous | 0.0007233 | 1.8077e-05 | 0.0001924 |  |  | 1.8077e-05 | 0.0001924 | NOx control | Selective Noncatalytic Reduction | 2007-02-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1995-01-01
3295_URQ3 | coal | 246 |  | 3295 | Urquhart | SC | URQ003 | URQ3 | Conventional Boiler | Tangential firing | 103 | 1048 | 10.1748 | bituminous | bituminous | 0.00070046 | 2.0752e-05 | 0.00021115 |  |  | 2.0752e-05 | 0.00021115 | PM control | Electrostatic precipitator, cold side, unspecified | 1969-11-01
2098_6 | coal | 247 |  | 2098 | Lake Road | MO | 6 | 6 | Conventional Boiler | Cyclone firing | 99 | 980 | 9.899 | subbituminous, bituminous | subbituminous, bituminous | 0.00030359 | 2.1752e-05 | 0.00021533 |  |  | 2.1752e-05 | 0.00021533 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1995-07-01
6085_14 | coal | 248 |  | 6085 | R.M. Schahfer | IN | R.M.0014 | 14 | Conventional Boiler | Cyclone firing | 468 | 4650 | 9.9359 | subbituminous | subbituminous | 0.00019016 | 2.2686e-05 | 0.00022541 |  |  | 2.2686e-05 | 0.00022541 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-06-01
3098_4 | coal | 249 |  | 3098 | Elrama Power Plant | PA | ELR4-2 | 4 | Conventional Boiler | Wall firing - front firing | 185 | 1921 | 10.3838 | bituminous | bituminous | 0.00028778 | 3.7007e-05 | 0.00038427 |  |  | 3.7007e-05 | 0.00038427 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1960-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-11-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
3098_3 | coal | 250 |  | 3098 | Elrama Power Plant | PA | ELR3-2 | 3 | Conventional Boiler | Vertical firing | 125 | 1303 | 10.424 | bituminous | bituminous | 0.00028778 | 3.7007e-05 | 0.00038576 |  |  | 3.7007e-05 | 0.00038576 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1954-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1954-11-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
1218_1 | coal | 251 |  | 1218 | Fair Station | IA | U1 | 1 | Conventional Boiler | Wall firing - front firing | 24.5 | 330 | 13.4694 | coal - bituminous | bituminous |  |  |  | 2.9e-05 | 0.00039061 | 2.9e-05 | 0.00039061 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
3098_2 | coal | 252 |  | 3098 | Elrama Power Plant | PA | ELR2-2 | 2 | Conventional Boiler | Vertical firing | 100 | 1254 | 12.54 | bituminous | bituminous | 0.00028778 | 3.7007e-05 | 0.00046407 |  |  | 3.7007e-05 | 0.00046407 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1953-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1953-03-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
3098_1 | coal | 253 |  | 3098 | Elrama Power Plant | PA | ELR1-2 | 1 | Conventional Boiler | Vertical firing | 100 | 1254 | 12.54 | bituminous | bituminous | 0.00028778 | 3.7007e-05 | 0.00046407 |  |  | 3.7007e-05 | 0.00046407 | NOx control | Selective Noncatalytic Reduction | 2001-07-01 | PM control | Multiple cyclone | 1952-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1952-06-01 | SO2 control | Wet FGD - Venturi Type | 1975-06-01
2848_H-5 | coal | 254 |  | 2848 | O H Hutchings | OH | H-5 | H-5 | Conventional Boiler | Tangential firing | 63 | 641 | 10.1746 | coal - bituminous | bituminous |  |  |  | 5.72e-05 | 0.00058199 | 5.72e-05 | 0.00058199 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2161_4 | coal | 255 |  | 2161 | James River Power Station | MO | Unit_4_JRPS | 4 | Conventional Boiler | Wall firing - front firing | 60 | 600 | 10 | subbituminous | subbituminous | 0.00020184 | 0.0028105 | 0.028105 |  |  | 0.0028105 | 0.028105 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-08-01
10773_1 | coal |  |  | 10773 | Altavista Power Station | VA | U1 & 2 | 1 | Conventional Boiler | Stoker - spreader | 34.5 | 442 | 12.8116 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1992-02-01 | NOx control | Selective Noncatalytic Reduction | 1992-02-01 | PM control | Multiple cyclone | 1992-02-01 | PM control | Multiple cyclone | 1992-02-01 | SO2 control | Dry FGD - Spray Dryer | 1992-02-01 | SO2 control | Dry FGD - Spray Dryer | 1992-02-01 | PM control | Fabric Filter, pulse | 1992-02-01 | PM control | Fabric Filter, pulse | 1992-02-01
10769_C-E CONTRACT 24687 | coal |  |  | 10769 | Rio Bravo Poso | CA | Config 1 | C-E CONTRACT 24687 | Fluidized bed firing | Fluidized bed firing | 36 | 407.93 | 11.3314 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1990-03-01 | PM control | Fabric Filter, reverse air | 1990-03-01
10773_2 | coal |  |  | 10773 | Altavista Power Station | VA | U1 & 2 | 2 | Conventional Boiler | Stoker - spreader | 34.5 | 447 | 12.9565 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1992-02-01 | NOx control | Selective Noncatalytic Reduction | 1992-02-01 | PM control | Multiple cyclone | 1992-02-01 | PM control | Multiple cyclone | 1992-02-01 | SO2 control | Dry FGD - Spray Dryer | 1992-02-01 | SO2 control | Dry FGD - Spray Dryer | 1992-02-01 | PM control | Fabric Filter, pulse | 1992-02-01 | PM control | Fabric Filter, pulse | 1992-02-01
50879_50879 | coal |  |  | 50879 | Wheelabrator Frackville Energy Co. | PA | 1 | 50879 | Fluidized bed firing | Fluidized bed firing | 45 | 590 | 13.1111 | coal refuse (culm or gob) | coal refuse (culm or gob) | [7 empty] | PM control | Fabric Filter, unspecified | 1988-12-01
8224_1 | coal |  |  | 8224 | North Valmy | NV | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 243.5 | 2560 | 10.5133 |  | subbituminous, bituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1981-12-01
10768_S-1715-3-13 | coal |  |  | 10768 | Rio Bravo Jasmin | CA | Config 1 | S-1715-3-13 | Fluidized bed firing | Fluidized bed firing | 36 | 412.16 | 11.4489 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1990-03-01 | PM control | Fabric Filter, reverse air | 1990-03-01
8102_1 | coal |  |  | 8102 | General James M. Gavin | OH | GA-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11936 | 9.0424 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2000-01-01 | Other control | Dry sorbent injection | 2001-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-04-01 | SO2 control | Wet FGD - Spray Type | 1994-12-01
8224_2 | coal |  |  | 8224 | North Valmy | NV | 2 | 2 | Conventional Boiler | Wall firing - front firing | 270.2 | 2881 | 10.6625 |  | subbituminous, bituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1985-05-01 | PM control | Fabric Filter, reverse air | 1985-05-01
10343_SG-101 | coal |  |  | 10343 | Foster Wheeler Mt Carmel Cogen | PA | SG-101 | SG-101 | Fluidized bed firing | Fluidized bed firing | 43 | 505 | 11.7442 | coal refuse (culm or gob) | coal refuse (culm or gob) | [7 empty] | PM control | Fabric Filter, reverse air | 1990-01-01
8102_2 | coal |  |  | 8102 | General James M. Gavin | OH | GA-2 | 2 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11936 | 9.0424 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2000-01-01 | Other control | Dry sorbent injection | 2001-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-03-01 | SO2 control | Wet FGD - Spray Type | 1995-03-01
50835_2 | coal |  |  | 50835 | TES Filer City Station | MI | TES2-Conf | 2 | Conventional Boiler | Stoker - spreader | 32.2 | 408 | 12.6708 | other--Fuel Type 1 - Coal/Coke/TDF Fuel Type 2 - Wood Chip | other--Fuel Type 1 - Coal/Coke/TDF Fuel Type 2 - Wood Chip | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1990-06-01 | PM control | Fabric Filter, pulse | 1990-06-01
50835_1 | coal |  |  | 50835 | TES Filer City Station | MI | TES1-Conf | 1 | Conventional Boiler | Stoker - spreader | 32.2 | 408 | 12.6708 | other--Fuel Type 1 - Coal/Coke/TDF Fuel Type 2 - Wood Chips | other--Fuel Type 1 - Coal/Coke/TDF Fuel Type 2 - Wood Chips | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1990-06-01 | PM control | Fabric Filter, pulse | 1990-06-01
54634_1 | coal |  |  | 54634 | St. Nicholas Cogen Project | PA | 1 | 1 | Fluidized bed firing | Fluidized bed firing | 99.2 | 1300 | 13.1048 | coal refuse (culm or gob) | coal refuse (culm or gob) | [7 empty] | PM control | Fabric Filter, pulse | 1990-09-01
50611_031 | coal |  |  | 50611 | WPS Westwood Generation, LLC | PA | 001 | 031 | Fluidized bed firing | Fluidized bed firing | 36 | 615 | 17.0833 | coal refuse (culm or gob) | coal refuse (culm or gob) | [7 empty] | PM control | Fabric Filter, pulse | 1987-12-01
889_Unit 1 | coal |  |  | 889 | Baldwin Energy Complex | IL | 001 | Unit 1 | Conventional Boiler | Cyclone firing | 626 | 5892 | 9.4121 |  | Subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-12-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1970-07-01 | Other control | Activated carbon injection | 2009-06-01 | SO2 control | Dry FGD - Spray Dryer |  | PM control | Fabric Filter, pulse
889_Unit 2 | coal |  |  | 889 | Baldwin Energy Complex | IL | 002 | Unit 2 | Conventional Boiler | Cyclone firing | 628 | 5996 | 9.5478 |  | Subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-12-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1973-05-01 | Other control | Activated carbon injection | 2009-06-01 | SO2 control | Dry FGD - Spray Dryer |  | PM control | Fabric Filter, pulse
889_Unit 3 | coal |  |  | 889 | Baldwin Energy Complex | IL | 003 | Unit 3 | Conventional Boiler | Tangential firing | 622 | 6031 | 9.6961 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1975-01-01 | Other control | Activated carbon injection | 2009-06-01 | SO2 control | Dry FGD - Spray Dryer |  | PM control | Fabric Filter, pulse
983_5 | coal |  |  | 983 | Clifty Creek | IN | Unit 5 | 5 | Conventional Boiler | Wall firing - front firing | 215 | 2176.51 | 10.1233 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-11-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-12-01
981_4 | coal |  |  | 981 | State Line | IN | Unit 4 | 4 | Conventional Boiler | Cyclone firing | 344 | 3478 | 10.1105 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1962-05-01
983_1 | coal |  |  | 983 | Clifty Creek | IN | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 215 | 2305.842 | 10.7248 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-07-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-08-01
983_2 | coal |  |  | 983 | Clifty Creek | IN | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 215 | 2247.252 | 10.4523 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-06-01
988_1 | coal |  |  | 988 | Tanners Creek | IN | TC-1 | 1 | Conventional Boiler | Vertical firing | 152.5 | 1391 | 9.1213 |  | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-03-01
988_2 | coal |  |  | 988 | Tanners Creek | IN | TC-2 | 2 | Conventional Boiler | Vertical firing | 152.5 | 1391 | 9.1213 |  | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-04-01
988_3 | coal |  |  | 988 | Tanners Creek | IN | TC-3 | 3 | Conventional Boiler | Vertical firing | 215.4 | 1844 | 8.5608 |  | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
990_50 | coal |  |  | 990 | Harding Street | IN | 50s | 50 | Conventional Boiler | Tangential firing | 112 | 1017 | 9.0804 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-12-01
963_33 | coal |  |  | 963 | Dallman | IL | 33 | 33 | Conventional Boiler | Tangential firing | 208 | 2089.8 | 10.0471 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1980-01-01
709_4 | coal |  |  | 709 | Harllee Branch | GA | Unit 4 | 4 | Conventional Boiler | Cell burner | 520 | 4874.298 | 9.3737 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-06-01
710_MB1 | coal |  |  | 710 | Jack McDonough | GA | MB1 | MB1 | Conventional Boiler | Tangential firing | 270 | 2490.99 | 9.2259 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-04-01
728_Y4BR | coal |  |  | 728 | Yates | GA | Y4BR | Y4BR | Conventional Boiler | Tangential firing | 138 | 1421.82 | 10.303 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-03-01
728_Y5BR | coal |  |  | 728 | Yates | GA | Y5BR | Y5BR | Conventional Boiler | Tangential firing | 145 | 1440.692 | 9.9358 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-02-01
728_Y7BR | coal |  |  | 728 | Yates | GA | Y7BR | Y7BR | Conventional Boiler | Tangential firing | 361 | 3437.82 | 9.523 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-04-01
983_6 | coal |  |  | 983 | Clifty Creek | IN | Unit 6 | 6 | Conventional Boiler | Wall firing - front firing | 215 | 2206.022 | 10.2606 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1977-09-01
898_Unit 4 | coal |  |  | 898 | Wood River | IL | 4 | Unit 4 | Conventional Boiler | Tangential firing | 97 | 1181 | 12.1753 |  | Subbituminous | [7 empty] | PM control | Multiple cyclone | 1954-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-01-01
898_Unit 5 | coal |  |  | 898 | Wood River | IL | 5 | Unit 5 | Conventional Boiler | Tangential firing | 391 | 4123 | 10.5448 |  | Subbituminous | [7 empty] | Other control | Activated carbon injection | 2009-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2002-05-01
983_3 | coal |  |  | 983 | Clifty Creek | IN | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 215 | 2233.798 | 10.3898 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-04-01
983_4 | coal |  |  | 983 | Clifty Creek | IN | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 215 | 2224.467 | 10.3464 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-03-01
991_4 | coal |  |  | 991 | Eagle Valley | IN | 4 | 4 | Conventional Boiler | Tangential firing | 60 | 741 | 12.35 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1973-12-01
728_Y6BR | coal |  |  | 728 | Yates | GA | Y6BR | Y6BR | Conventional Boiler | Tangential firing | 363 | 3492.896 | 9.6223 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-07-01
1008_1 | coal |  |  | 1008 | R. Gallagher | IN | 1-2007 | 1 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | 9.7333 | coal - bituminous | bituminous | [7 empty] | PM control | Fabric Filter, shake and deflate | 2007-12-01
1010_2 | coal |  |  | 1010 | Wabash River | IN | 2 | 2 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | 10.2633 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-01-01
1010_3 | coal |  |  | 1010 | Wabash River | IN | 3 | 3 | Conventional Boiler | Wall firing - front firing | 90 | 923.695 | 10.2633 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-03-01
1010_5 | coal |  |  | 1010 | Wabash River | IN | 5 | 5 | Conventional Boiler | Wall firing - front firing | 103 | 1079.0931 | 10.4766 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1994-04-01
1040_1 | coal |  |  | 1040 | Whitewater Valley | IN | 001 | 1 | Conventional Boiler | Wall firing - unspecified | 36 | 385 | 10.6944 |  | Bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2004-03-01 | PM control | Electrostatic precipitator, unspecified | 1974-01-11 | PM control | Fabric Filter, unspecified | 2009-01-06
1040_2 | coal |  |  | 1040 | Whitewater Valley | IN | 002 | 2 | Conventional Boiler | Tangential firing | 69 | 730 | 10.5797 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2003-09-01 | PM control | Electrostatic precipitator, unspecified | 1973-05-16 | PM control | Fabric Filter, unspecified | 2009-01-06
2527_6 | coal |  |  | 2527 | AES Greenidge | NY | Unit 4 | 6 | Conventional Boiler | Tangential firing | 112 | 1117 | 9.9732 | coal - bituminous, petroleum coke | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-05-01 | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | Other control | Activated carbon injection | 2007-05-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2007-05-01 | PM control | Fabric Filter, pulse | 2006-11-01
1043_2SG1 | coal |  |  | 1043 | Frank E. Ratts | IN | 2SG1conf1 | 2SG1 | Conventional Boiler | Wall firing - front firing | 131 | 1142 | 8.7176 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-12-01
995_7 | coal |  |  | 995 | Bailly | IN | 7 | 7 | Conventional Boiler | Cyclone firing | 176 | 1638 | 9.3068 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-06-01 | SO2 control | Wet FGD - Packed Type | 1992-06-01
1058_2 | coal |  |  | 1058 | Sixth Street | IA | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 13.3 | 304 | 22.8571 | coal - subbituminous | natural gas, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-06-01
1058_3 | coal |  |  | 1058 | Sixth Street | IA | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 13.9 | 304 | 21.8705 | coal - subbituminous | natural gas, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-12-01
1058_4 | coal |  |  | 1058 | Sixth Street | IA | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 14.8 | 304 | 20.5405 | coal - subbituminous | natural gas, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-08-01
1058_5 | coal |  |  | 1058 | Sixth Street | IA | Unit 5 | 5 | Conventional Boiler | Wall firing - front firing | 32.3 | 389 | 12.0433 | coal - subbituminous | natural gas, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-08-01
1082_1 | coal |  |  | 1082 | Walter Scott Jr. Energy Center | IA | 1 | 1 | Conventional Boiler | Wall firing - unspecified | 45 | 656 | 14.5778 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-12-01
1082_2 | coal |  |  | 1082 | Walter Scott Jr. Energy Center | IA | 2 | 2 | Conventional Boiler | Tangential firing | 94 | 935 | 9.9468 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-11-01
1131_7 | coal |  |  | 1131 | Streeter Station | IA | 7 | 7 | Conventional Boiler | Wall firing - front firing | 38.4 | 473 | 12.3177 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-06-01
1043_1SG1 | coal |  |  | 1043 | Frank E. Ratts | IN | 1SG1conf1 | 1SG1 | Conventional Boiler | Wall firing - front firing | 130 | 1142 | 8.7846 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-12-01
1046_1 | coal |  |  | 1046 | Dubuque | IA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 37.6 | 605.8 | 16.1117 | coal - bituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01
994_2 | coal |  |  | 994 | AES Petersburg | IN | 2ss | 2 | Conventional Boiler | Tangential firing | 445 | 4144 | 9.3124 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-12-01 | SO2 control | Wet FGD - Spray Type | 1996-12-01
995_8 | coal |  |  | 995 | Bailly | IN | 8 | 8 | Conventional Boiler | Cyclone firing | 352 | 3374 | 9.5852 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-02-01 | SO2 control | Wet FGD - Packed Type | 1992-06-01
1001_2 | coal |  |  | 1001 | Cayuga | IN | 2-2008-FGDIN | 2 | Conventional Boiler | Tangential firing | 525 | 5040 | 9.6 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2006-01-01 | SO2 control | Wet FGD - Spray Type | 2008-09-01
1004_7-1 | coal |  |  | 1004 | Edwardsport | IN | 7-1 | 7-1 | Conventional Boiler | Wall firing - front firing | 42.75 | 510 | 11.9298 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-12-01
1008_3 | coal |  |  | 1008 | R. Gallagher | IN | 3-2008 | 3 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | 9.7333 | coal - bituminous | bituminous | [7 empty] | PM control | Fabric Filter, shake and deflate | 2008-05-01
1004_8-1 | coal |  |  | 1004 | Edwardsport | IN | 8-1 | 8-1 | Conventional Boiler | Wall firing - front firing | 42.75 | 510 | 11.9298 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-12-01
991_3 | coal |  |  | 991 | Eagle Valley | IN | 3 | 3 | Conventional Boiler | Tangential firing | 46 | 524 | 11.3913 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1975-12-01
1046_5 | coal |  |  | 1046 | Dubuque | IA | Unit 5 | 5 | Conventional Boiler | Wall firing - front firing | 29.2 | 337.3 | 11.5514 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-08-01
1047_3 | coal |  |  | 1047 | Lansing | IA | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 31.9 | 452.9 | 14.1975 | coal - bituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01
991_5 | coal |  |  | 991 | Eagle Valley | IN | 5 | 5 | Conventional Boiler | Tangential firing | 66 | 741 | 11.2273 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-12-01
994_1 | coal |  |  | 994 | AES Petersburg | IN | 1s | 1 | Conventional Boiler | Tangential firing | 255 | 2200 | 8.6275 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1967-12-01 | SO2 control | Wet FGD - Spray Type | 1996-12-01
994_3 | coal |  |  | 994 | AES Petersburg | IN | 3ss | 3 | Conventional Boiler | Tangential firing | 580 | 5540 | 9.5517 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1977-12-01 | SO2 control | Wet FGD - Spray Type | 1977-12-01
3_1 | coal |  |  | 3 | Barry | AL | Unit 1 | 1 | Conventional Boiler | Tangential firing | 145 | 1380.8842 | 9.5233 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1976-07-01
1008_4 | coal |  |  | 1008 | R. Gallagher | IN | 4-2008 | 4 | Conventional Boiler | Wall firing - front firing | 150 | 1460 | 9.7333 | coal - bituminous | bituminous | [7 empty] | PM control | Fabric Filter, shake and deflate | 2008-04-01
59_1 | coal |  |  | 59 | Platte | NE | 1 | 1 | Conventional Boiler | Tangential firing | 110 | 1048 | 9.5273 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1982-12-01
50_2 | coal |  |  | 50 | Widows Creek | AL | 2 | 2 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | 10.8677 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-08-01
50_3 | coal |  |  | 50 | Widows Creek | AL | 3 | 3 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | 10.8677 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-05-01
50_4 | coal |  |  | 50 | Widows Creek | AL | 4 | 4 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | 10.8677 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
50_5 | coal |  |  | 50 | Widows Creek | AL | 5 | 5 | Conventional Boiler | Wall firing - front firing | 140.6 | 1589 | 11.3016 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-09-01
50_6 | coal |  |  | 50 | Widows Creek | AL | 6 | 6 | Conventional Boiler | Wall firing - front firing | 140.6 | 1589 | 11.3016 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-11-01
50_7 | coal |  |  | 50 | Widows Creek | AL | 7 | 7 | Conventional Boiler | Tangential firing | 575 | 5681 | 9.88 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | Other control | Other (specify): Sodium bisulfite to control opacity | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-12-01 | SO2 control | Wet FGD - Venturi Type | 1981-12-01
50_8 | coal |  |  | 50 | Widows Creek | AL | 8 | 8 | Conventional Boiler | Tangential firing | 550 | 5839 | 10.6164 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Hydrated lime to control opacity | 2004-05-01 | PM control | PM scrubber - Venturi | 1978-01-01 | SO2 control | Wet FGD - Venturi Type | 1978-01-01
645_3 | coal |  |  | 645 | Big Bend | FL | BB03_SCR_iso | 3 | Conventional Boiler | Wall firing - opposed firing | 400 | 4115 | 10.2875 | coal - bituminous, petroleum coke | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2008-07-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1976-05-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
56_3 | coal |  |  | 56 | Charles R. Lowman | AL | 3D | 3 | Conventional Boiler | Wall firing - opposed firing | 258 | 2500 | 9.6899 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-06-01 | NOx control | Selective Catalytic Reduction | 2007-12-01 | SO2 control | Wet FGD - Spray Type | 1980-06-01
87_1 | coal |  |  | 87 | Escalante | NM | 1 | 1 | Conventional Boiler | Tangential firing | 260 | 2366 | 9.1 | coal - subbituminous | subbituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1984-01-01 | SO2 control | Wet FGD - Spray Type | 1984-01-01
108_SGU1 | coal |  |  | 108 | HOLCOMB | KS | SGU1 | SGU1 | Conventional Boiler | Wall firing - opposed firing | 387 | 3389 | 8.7571 |  | subbituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1983-08-01 | PM control | Fabric Filter, reverse air | 1983-08-01
113_1 | coal |  |  | 113 | Cholla | AZ | 001 | 1 | Conventional Boiler | Tangential firing | 131 | 1270 | 9.6947 |  | Bituminous, Subbituminous | [7 empty] | PM control | Fabric Filter, unspecified | 2007-01-01 | SO2 control | Wet FGD - Venturi Type | 1972-01-01
113_2 | coal |  |  | 113 | Cholla | AZ | 002 | 2 | Conventional Boiler | Tangential firing | 305 | 2938 | 9.6328 |  | Bituminous, Subbituminous | [7 empty] | PM control | PM scrubber - Venturi | 1978-01-01 | SO2 control | Wet FGD - Venturi Type | 1978-01-01
56_2 | coal |  |  | 56 | Charles R. Lowman | AL | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 258 | 2500 | 9.6899 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-06-01 | NOx control | Selective Catalytic Reduction | 2007-12-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2007-12-01
10_1 | coal |  |  | 10 | Greene County | AL | Unit 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 272 | 2452.624 | 9.017 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1975-01-01
3_2 | coal |  |  | 3 | Barry | AL | Unit 2 | 2 | Conventional Boiler | Tangential firing | 145 | 1372.7464 | 9.4672 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-07-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1976-05-01
3_3 | coal |  |  | 3 | Barry | AL | Unit 3 | 3 | Conventional Boiler | Tangential firing | 263 | 2434.4652 | 9.2565 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-07-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1976-01-01
3_4 | coal |  |  | 3 | Barry | AL | Unit 4 | 4 | Conventional Boiler | Tangential firing | 376 | 3512.6521 | 9.3422 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1985-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-03-01
7_1 | coal |  |  | 7 | Gadsden | AL | Unit 1 | 1 | Conventional Boiler | Tangential firing | 68 | 792.0615 | 11.648 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1964-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-01-01
7_2 | coal |  |  | 7 | Gadsden | AL | Unit 2 | 2 | Conventional Boiler | Tangential firing | 70 | 847.8367 | 12.112 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1964-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-01-01
8_10 | coal |  |  | 8 | Gorgas | AL | Unit 10 | 10 | Conventional Boiler | Tangential firing | 720 | 6523.794 | 9.0608 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-10-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
8_6 | coal |  |  | 8 | Gorgas | AL | Unit 6 | 6 | Conventional Boiler | Wall firing - front firing | 110 | 1291.846 | 11.7441 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-05-01
8_7 | coal |  |  | 8 | Gorgas | AL | Unit 7 | 7 | Conventional Boiler | Wall firing - front firing | 110 | 1218.3294 | 11.0757 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-06-01
50_1 | coal |  |  | 50 | Widows Creek | AL | 1 | 1 | Conventional Boiler | Wall firing - front firing | 140.6 | 1528 | 10.8677 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-12-01
8_9 | coal |  |  | 8 | Gorgas | AL | Unit 9 | 9 | Conventional Boiler | Tangential firing | 185 | 1738.6247 | 9.398 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
47_5 | coal |  |  | 47 | Colbert | AL | 5 | 5 | Conventional Boiler | Wall firing - opposed firing | 550 | 5547 | 10.0855 | coal - bituminous, coal - subbituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-06-01
10_2 | coal |  |  | 10 | Greene County | AL | Unit 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 260 | 2392.821 | 9.2032 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1975-01-01
26_1 | coal |  |  | 26 | E. C. Gaston | AL | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 270 | 2430.2362 | 9.0009 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1974-04-01
26_2 | coal |  |  | 26 | E. C. Gaston | AL | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 270 | 2511.8462 | 9.3031 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1975-04-01 | PM control | Fabric Filter, pulse | 1999-06-01
26_3 | coal |  |  | 26 | E. C. Gaston | AL | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 270 | 2462.7795 | 9.1214 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1973-12-01 | PM control | Fabric Filter, pulse | 1996-12-01
26_4 | coal |  |  | 26 | E. C. Gaston | AL | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 270 | 2468.352 | 9.142 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-10-01
47_1 | coal |  |  | 47 | Colbert | AL | 1 | 1 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | 10.605 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-11-01
47_2 | coal |  |  | 47 | Colbert | AL | 2 | 2 | Conventional Boiler | Wall firing - front firing | 200 | 2121 | 10.605 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-08-01
8_8 | coal |  |  | 8 | Gorgas | AL | Unit 8 | 8 | Conventional Boiler | Tangential firing | 175 | 1600.8973 | 9.148 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1972-06-01 | SO2 control | Wet FGD - Spray Type | 2007-12-01
709_2 | coal |  |  | 709 | Harllee Branch | GA | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 332 | 3091.725 | 9.3124 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1967-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1977-12-01
130_2 | coal |  |  | 130 | Cross | SC | C2 | 2 | Conventional Boiler | Tangential firing | 595 | 6011 | 10.1025 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-05-01 | SO2 control | Wet FGD - Spray Type | 1984-05-01
643_1 | coal |  |  | 643 | Lansing Smith | FL | Unit 1 | 1 | Conventional Boiler | Tangential firing | 172 | 1728.216 | 10.0478 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-06-01 | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-01-01
645_1 | coal |  |  | 645 | Big Bend | FL | BB01_pre-SCR | 1 | Conventional Boiler | Wall firing - opposed firing | 410 | 4037 | 9.8463 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1970-10-01 | SO2 control | Wet FGD - Packed Type | 1999-12-01
645_4 | coal |  |  | 645 | Big Bend | FL | BB04_SCR_iso | 4 | Conventional Boiler | Tangential firing | 465 | 4330 | 9.3118 | coal - bituminous, petroleum coke, coal refuse | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-06-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1985-02-01 | SO2 control | Wet FGD - Packed Type | 2008-01-01
663_B-2 | coal |  |  | 663 | Deerhaven Generating Station | FL | 001 | B-2 | Conventional Boiler | Wall firing - unspecified | 235 | 2428 | 10.3319 |  | Bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, unspecified | 1987-10-01 | NOx control | Selective Catalytic Reduction | 2009-05-01 | SO2 control | Dry FGD - Unspecified | 2009-05-01
593_4 | coal |  |  | 593 | Edge Moor | DE | 4 | 4 | Conventional Boiler | Tangential firing | 182 | 1900 | 10.4396 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-05-01 | SO2 control | Dry FGD - Sorbent Injection | 2009-01-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-01-01
709_1 | coal |  |  | 709 | Harllee Branch | GA | Unit 1 | 1 | Conventional Boiler | Cell burner | 267 | 2542.694 | 9.5232 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1965-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-01-01
593_3 | coal |  |  | 593 | Edge Moor | DE | 3 | 3 | Conventional Boiler | Tangential firing | 92 | 991 | 10.7717 |  | oil - other, bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-05-01 | SO2 control | Dry FGD - Sorbent Injection | 2009-01-01 | Other control | Activated carbon injection |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-01-01
709_3 | coal |  |  | 709 | Harllee Branch | GA | Unit 3 | 3 | Conventional Boiler | Cell burner | 513 | 4825.829 | 9.4071 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-07-01
727_3 | coal |  |  | 727 | Mitchell | GA | Unit 3 | 3 | Conventional Boiler | Tangential firing | 164 | 855 | 5.2134 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-04-01
728_Y2BR | coal |  |  | 728 | Yates | GA | Y2BR | Y2BR | Conventional Boiler | Tangential firing | 105 | 1171.8 | 11.16 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1968-05-01
728_Y3BR | coal |  |  | 728 | Yates | GA | Y3BR | Y3BR | Conventional Boiler | Tangential firing | 105 | 1250.704 | 11.9115 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-02-01
733_1 | coal |  |  | 733 | Kraft | GA | Unit 1 | 1 | Conventional Boiler | Tangential firing | 50 | 547.536 | 10.9507 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
733_2 | coal |  |  | 733 | Kraft | GA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 54 | 532.584 | 9.8627 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
733_3 | coal |  |  | 733 | Kraft | GA | Unit 3 | 3 | Conventional Boiler | Tangential firing | 107 | 1052.334 | 9.8349 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
1004_7-2 | coal |  |  | 1004 | Edwardsport | IN | 7-2 | 7-2 | Conventional Boiler | Wall firing - front firing | 42.75 | 510 | 11.9298 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-12-01
136_1 | coal |  |  | 136 | Seminole Generating Station | FL | Unit 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 694 | 7172 | 10.3343 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2009-02-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-01-01 | Other control | Dry sorbent injection | 2009-02-01 | SO2 control | Wet FGD - Spray Type | 1984-01-01
136_2 | coal |  |  | 136 | Seminole Generating Station | FL | Unit 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 694 | 7172 | 10.3343 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2009-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-12-01 | Other control | Dry sorbent injection | 2009-04-01 | SO2 control | Wet FGD - Spray Type | 1984-12-01
160_2 | coal |  |  | 160 | Apache Station | AZ | ST2 | 2 | Conventional Boiler | Turbo | 204 | 1932.521 | 9.4731 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1978-06-01
160_3 | coal |  |  | 160 | Apache Station | AZ | ST3 | 3 | Conventional Boiler | Turbo | 204 | 1932.521 | 9.4731 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1978-06-01
207_PPBoiler1 | coal |  |  | 207 | St Johns River Power Park | FL | PPUnit1Configuration | PPBoiler1 | Conventional Boiler | Wall firing - opposed firing | 660 | 6144 | 9.3091 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2009-07-01 | NOx control | Other (specify): Ammonia Injection for SO3 Mitigation | 2009-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1988-03-01 | SO2 control | Wet FGD - Spray/Tray Type | 1986-12-01 | SO2 control | Wet FGD - Spray Type | 1986-12-01
207_PPBoiler2 | coal |  |  | 207 | St Johns River Power Park | FL | PPUnit2Configuration | PPBoiler2 | Conventional Boiler | Wall firing - opposed firing | 660 | 6144 | 9.3091 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2009-03-01 | NOx control | Other (specify): Ammonia Injection for SO3 Mitigation | 2009-03-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1986-12-01 | SO2 control | Wet FGD - Spray/Tray Type | 1988-03-01 | SO2 control | Wet FGD - Spray Type | 1988-03-01
508_4 | coal |  |  | 508 | Lamar Plant | CO | 001 | 4 | Fluidized bed firing | Fluidized bed firing | 44 | 509.8 | 11.5864 |  | subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified | 2009-05-01
564_1 | coal |  |  | 564 | Stanton Energy Center | FL | 1 coal | 1 | Conventional Boiler | Wall firing - opposed firing | 468 | 4286 | 9.1581 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1987-05-01 | SO2 control | Wet FGD - Spray Type | 1987-05-01
628_2 | coal |  |  | 628 | Crystal River Power Plant | FL | CryR_Cfg_2 | 2 | Conventional Boiler | Tangential firing | 515 | 4161 | 8.0796 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
628_4 | coal |  |  | 628 | Crystal River Power Plant | FL | CryR_Cfg_4 | 4 | Conventional Boiler | Wall firing - opposed firing | 769 | 7613 | 9.8999 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-01-01
492_6 | coal |  |  | 492 | Martin Drake | CO | Unit 6 - Coal | 6 | Conventional Boiler | Wall firing - front firing | 85 | 930 | 10.9412 |  | bituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1978-09-01
1745_9A | coal |  |  | 1745 | Trenton Channel Power Plant | MI | TC9A-Config | 9A | Conventional Boiler | Tangential firing | 540 | 4045 | 7.4907 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-06-01
1695_4 | coal |  |  | 1695 | B.C. Cobb | MI | BCCobb4-Conf | 4 | Conventional Boiler | Tangential firing | 167 | 1656 | 9.9162 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2000-12-01
1702_1 | coal |  |  | 1702 | D.E. Karn | MI | DEK1-Conf | 1 | Conventional Boiler | Tangential firing | 275 | 2445 | 8.8909 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1959-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-12-01
1702_2 | coal |  |  | 1702 | D.E. Karn | MI | DEK2-Conf | 2 | Conventional Boiler | Wall firing - front firing | 281 | 2587 | 9.2064 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1959-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-12-01
1720_8 | coal |  |  | 1720 | J.C. Weadock | MI | JCW8-Conf | 8 | Conventional Boiler | Tangential firing | 166.5 | 1475 | 8.8589 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-12-01
1733_1 | coal |  |  | 1733 | Monroe Power Plant | MI | MN1-Config | 1 | Conventional Boiler | Wall firing - opposed firing | 810 | 7140 | 8.8148 |  | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-01-01
1733_2 | coal |  |  | 1733 | Monroe Power Plant | MI | MN2-Config | 2 | Conventional Boiler | Wall firing - opposed firing | 815 | 7140 | 8.7607 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-01-01
1743_2 | coal |  |  | 1743 | St Clair Power Plant | MI | SC2-Config | 2 | Conventional Boiler | Wall firing - front firing | 163 | 1750 | 10.7362 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
1743_3 | coal |  |  | 1743 | St Clair Power Plant | MI | SC3-Config | 3 | Conventional Boiler | Wall firing - front firing | 174 | 1765 | 10.1437 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
1897_3 | coal |  |  | 1897 | Hibbard Energy Center | MN | HREC3 | 3 | Conventional Boiler | Stoker - spreader | 35 | 518 | 14.8 | [9 empty] | PM control | Multiple cyclone | 1949-01-01 | PM control | Electrostatic precipitator, unspecified | 1987-01-01
1743_6 | coal |  |  | 1743 | St Clair Power Plant | MI | SC6-Config | 6 | Conventional Boiler | Tangential firing | 331 | 3045 | 9.1994 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-01-01
1893_4 | coal |  |  | 1893 | Boswell Energy Center | MN | BEC4 | 4 | Conventional Boiler | Tangential firing | 587.5 | 5947 | 10.1226 |  | Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | PM scrubber - Venturi | 1980-01-01 | SO2 control | Wet FGD - Unspecified | 1980-01-01
1831_EUBoiler1 | coal |  |  | 1831 | Otto E. Eckert Station | MI | 001 | EUBoiler1 | Conventional Boiler | Wall firing - front firing | 40 | 509 | 12.725 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1978-01-01
1831_EUBoiler2 | coal |  |  | 1831 | Otto E. Eckert Station | MI | 002 | EUBoiler2 | Conventional Boiler | Tangential firing | 38 | 522 | 13.7368 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1978-01-01
1831_EUBoiler3 | coal |  |  | 1831 | Otto E. Eckert Station | MI | 003 | EUBoiler3 | Conventional Boiler | Tangential firing | 40 | 522 | 13.05 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1978-01-01
1831_EUBoiler4 | coal |  |  | 1831 | Otto E. Eckert Station | MI | 004 | EUBoiler4 | Conventional Boiler | Wall firing - front firing | 72 | 807 | 11.2083 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1976-01-01
1891_1 | coal |  |  | 1891 | Laskin Energy Center | MN | LEC1 | 1 | Conventional Boiler | Tangential firing | 60 | 725 | 12.0833 | coal - bituminous, coal - subbituminous | natural gas, subbituminous, bituminous | [7 empty] | PM control | PM scrubber - wet | 1971-01-01
1891_2 | coal |  |  | 1891 | Laskin Energy Center | MN | LEC2 | 2 | Conventional Boiler | Tangential firing | 55 | 660 | 12 | coal - bituminous, coal - subbituminous | natural gas, subbituminous, bituminous | [7 empty] | PM control | PM scrubber - wet | 1971-01-01
1893_1 | coal |  |  | 1893 | Boswell Energy Center | MN | BEC1 | 1 | Conventional Boiler | Wall firing - front firing | 73 | 750 | 10.274 |  | Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Fabric Filter, unspecified | 1977-01-01
1893_2 | coal |  |  | 1893 | Boswell Energy Center | MN | BEC2 | 2 | Conventional Boiler | Wall firing - front firing | 72 | 750 | 10.4167 |  | Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | Fabric Filter, unspecified | 1977-01-01
1904_3 | coal |  |  | 1904 | Black Dog | MN | Boiler 3 | 3 | Conventional Boiler | Wall firing - front firing | 96 | 985 | 10.2604 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1956-08-01
1743_4 | coal |  |  | 1743 | St Clair Power Plant | MI | SC4-Config | 4 | Conventional Boiler | Wall firing - front firing | 157 | 1692 | 10.7771 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
994_4 | coal |  |  | 994 | AES Petersburg | IN | 4s | 4 | Conventional Boiler | Tangential firing | 584 | 5550 | 9.5034 | bituminous, No.2 Fuel Oil (distillate) | bituminous, No.2 Fuel Oil (distillate) | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1986-12-01 | SO2 control | Wet FGD - Spray Type | 1986-12-01
1695_5 | coal |  |  | 1695 | B.C. Cobb | MI | BCCobb5-Conf | 5 | Conventional Boiler | Tangential firing | 167.5 | 1623 | 9.6896 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2000-12-01
1710_Unit 3 | coal |  |  | 1710 | Consumers Energy - J.H. Campbell | MI | JHC3-Conf | Unit 3 | Conventional Boiler | Wall firing - front firing | 869 | 8199 | 9.435 | coal - subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-06-01
1720_7 | coal |  |  | 1720 | J.C. Weadock | MI | JCW7-Conf | 7 | Conventional Boiler | Tangential firing | 166 | 1560 | 9.3976 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-12-01
1731_1 | coal |  |  | 1731 | Harbor Beach Power Plant | MI | HB1-Config | 1 | Conventional Boiler | Wall firing - front firing | 110 | 1181 | 10.7364 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-04-01
1733_4 | coal |  |  | 1733 | Monroe Power Plant | MI | MN4-Config | 4 | Conventional Boiler | Wall firing - opposed firing | 815 | 7140 | 8.7607 |  | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-01-01 | SO2 control | Wet FGD - Unspecified | 2009-06-01
1740_2 | coal |  |  | 1740 | River Rouge Power Plant | MI | RR2-Config | 2 | Conventional Boiler | Tangential firing | 269 | 2317 | 8.6134 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
1897_4 | coal |  |  | 1897 | Hibbard Energy Center | MN | HREC4 | 4 | Conventional Boiler | Stoker - spreader | 36 | 471 | 13.0833 | [9 empty] | PM control | Multiple cyclone | 1951-01-01 | PM control | Electrostatic precipitator, unspecified | 1987-01-01
1743_1 | coal |  |  | 1743 | St Clair Power Plant | MI | SC1-Config | 1 | Conventional Boiler | Wall firing - front firing | 161 | 1753 | 10.8882 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
1745_16 | coal |  |  | 1745 | Trenton Channel Power Plant | MI | TC16-Config | 16 | Conventional Boiler | Tangential firing | 58 | 603 | 10.3966 |  | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1948-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1966-06-01
1745_17 | coal |  |  | 1745 | Trenton Channel Power Plant | MI | TC16-Config | 17 | Conventional Boiler | Tangential firing | 58 | 603 | 10.3966 |  | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1948-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1966-06-01
1745_18 | coal |  |  | 1745 | Trenton Channel Power Plant | MI | TC16-Config | 18 | Conventional Boiler | Tangential firing | 58 | 603 | 10.3966 |  | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1948-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1966-06-01
1745_19 | coal |  |  | 1745 | Trenton Channel Power Plant | MI | TC16-Config | 19 | Conventional Boiler | Tangential firing | 58 | 603 | 10.3966 |  | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1948-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1966-06-01
1825_3 | coal |  |  | 1825 | Grand Haven City of J.B. Sims | MI | 001 | 3 | Conventional Boiler | Wall firing - unspecified | 79.7 | 755 | 9.473 |  | Bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | Electrostatic precipitator, unspecified | 1983-08-01 | SO2 control | Wet FGD - Tray Type | 1983-08-01
1831_EUBoiler5 | coal |  |  | 1831 | Otto E. Eckert Station | MI | 005 | EUBoiler5 | Conventional Boiler | Wall firing - front firing | 71 | 807 | 11.3662 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1976-01-01
1831_EUBoiler6 | coal |  |  | 1831 | Otto E. Eckert Station | MI | 006 | EUBoiler6 | Conventional Boiler | Wall firing - front firing | 71 | 807 | 11.3662 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1976-01-01
1832_EU001 | coal |  |  | 1832 | Erickson Station | MI | 001 | EU001 | Conventional Boiler | Wall firing - front firing | 165 | 1668 | 10.1091 | bituminous | bituminous | 0.00014684 | [6 empty] | PM control | Electrostatic precipitator, unspecified | 1998-01-01
1893_3 | coal |  |  | 1893 | Boswell Energy Center | MN | BEC3 | 3 | Conventional Boiler | Tangential firing | 371.3 | 4115 | 11.0827 | subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction |  | SO2 control | Wet FGD - Spray Type | 2009-01-01 | Other control | Activated carbon injection |  | PM control | Fabric Filter, unspecified | 2009-01-01
1239_39 | coal |  |  | 1239 | Riverton | KS | 039 | 39 | Conventional Boiler | Wall firing - unspecified | 40 | 426 | 10.65 |  | petroleum coke, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1976-01-01
2324_3 | coal |  |  | 2324 | Reid Gardner | NV | 3 | 3 | Conventional Boiler | Wall firing - front firing | 111 | 1237 | 11.1441 | coal - bituminous, other non-fossil fuel (specify) | bituminous | [7 empty] | PM control | Fabric Filter, pulse | 2009-02-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
2104_4 | coal |  |  | 2104 | Meramec | MO | 004 | 4 | Conventional Boiler | Wall firing - unspecified | 362 | 3782 | 10.4475 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1980-12-01
2167_1 | coal |  |  | 2167 | New Madrid | MO | con1 | 1 | Conventional Boiler | Cyclone firing | 600 | 6000 | 10 | coal - subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-02-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-04-01
2167_2 | coal |  |  | 2167 | New Madrid | MO | con2 | 2 | Conventional Boiler | Cyclone firing | 600 | 6000 | 10 | coal - subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2000-02-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-05-01
2187_2 | coal |  |  | 2187 | JE Corette Plant | MT | Corette1 | 2 | Conventional Boiler | Tangential firing | 163 | 1750 | 10.7362 |  | subbituminous | [7 empty] | Other control | Activated carbon injection | 2009-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-09-01
1904_4 | coal |  |  | 1904 | Black Dog | MN | Boiler 4 | 4 | Conventional Boiler | Wall firing - front firing | 178 | 1735 | 9.7472 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-01-01
2324_2 | coal |  |  | 2324 | Reid Gardner | NV | 2 | 2 | Conventional Boiler | Wall firing - front firing | 111 | 1215 | 10.9459 |  | bituminous | [7 empty] | PM control | Fabric Filter, pulse | 2009-04-01 | SO2 control | Wet FGD - Venturi Type | 1976-07-01
2104_1 | coal |  |  | 2104 | Meramec | MO | 001 | 1 | Conventional Boiler | Tangential firing | 128 | 1566 | 12.2344 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1979-12-01
2324_4 | coal |  |  | 2324 | Reid Gardner | NV | 4 | 4 | Conventional Boiler | Wall firing - front firing | 281 | 2956 | 10.5196 |  | bituminous | [7 empty] | PM control | Fabric Filter, pulse | 1983-07-01 | SO2 control | Wet FGD - Venturi Type | 1983-07-01
2442_1 | coal |  |  | 2442 | Four Corners | NM | 001 | 1 | Conventional Boiler | Wall firing - unspecified | 199 | 1707.7 | 8.5814 |  | Subbituminous | [7 empty] | PM control | Other (specify): PM scrubber - Venturi with FGD | 1972-01-01
2442_2 | coal |  |  | 2442 | Four Corners | NM | 002 | 2 | Conventional Boiler | Wall firing - unspecified | 197 | 1707.7 | 8.6685 |  | Subbituminous | [7 empty] | PM control | Other (specify): PM scrubber - Venturi with FGD | 1972-01-01
2442_3 | coal |  |  | 2442 | Four Corners | NM | 003 | 3 | Conventional Boiler | Wall firing - unspecified | 256 | 2189.6 | 8.5531 |  | Subbituminous | [7 empty] | PM control | Other (specify): PM scrubber - Venturi with FGD | 1972-01-01
2442_4 | coal |  |  | 2442 | Four Corners | NM | 004 | 4 | Conventional Boiler | Cell burner | 825 | 7520 | 9.1152 |  | Subbituminous | [7 empty] | PM control | Fabric Filter, unspecified | 1982-01-01 | SO2 control | Wet FGD - Tray Type | 1985-01-01
2442_5 | coal |  |  | 2442 | Four Corners | NM | 005 | 5 | Conventional Boiler | Cell burner | 825 | 7520 | 9.1152 |  | Subbituminous | [7 empty] | PM control | Fabric Filter, unspecified | 1982-01-01 | SO2 control | Wet FGD - Tray Type | 1985-01-01
2291_NO4 | coal |  |  | 2291 | North Omaha | NE | NO4 | NO4 | Conventional Boiler | Tangential firing | 138.2 | 1471.0008 | 10.644 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-04-01
1740_3 | coal |  |  | 1740 | River Rouge Power Plant | MI | RR3-Config | 3 | Conventional Boiler | Wall firing - front firing | 293 | 2679 | 9.1433 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-06-01
1943_003 | coal |  |  | 1943 | Hoot Lake | MN | 3 | 003 | Conventional Boiler | Wall firing - front firing | 83.5 | 978.7 | 11.721 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-05-01
2049_4 | coal |  |  | 2049 | Jack Watson | MS | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 250 | 2226.86 | 8.9074 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1968-07-01
2103_1 | coal |  |  | 2103 | Labadie | MO | 001 | 1 | Conventional Boiler | Tangential firing | 630 | 6183 | 9.8143 |  | Bituminous, Subbituminous | [7 empty] | Other control | Other (specify): FGC SO3 Injection | 1992-11-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1983-06-01
2103_2 | coal |  |  | 2103 | Labadie | MO | 002 | 2 | Conventional Boiler | Tangential firing | 623 | 6183 | 9.9246 |  | Bituminous, Subbituminous | [7 empty] | Other control | Other (specify): FGC SO3 Injection | 1992-11-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1982-12-01
2103_3 | coal |  |  | 2103 | Labadie | MO | 003 | 3 | Conventional Boiler | Tangential firing | 633 | 6107 | 9.6477 |  | Bituminous, Subbituminous | [7 empty] | Other control | Other (specify): FGC SO3 Injection | 1992-11-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1983-01-01
2103_4 | coal |  |  | 2103 | Labadie | MO | 004 | 4 | Conventional Boiler | Tangential firing | 633 | 6107 | 9.6477 |  | Bituminous, Subbituminous | [7 empty] | Other control | Other (specify): FGC SO3 Injection | 1992-11-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1983-11-01
2104_3 | coal |  |  | 2104 | Meramec | MO | 003 | 3 | Conventional Boiler | Wall firing - unspecified | 282 | 3172 | 11.2482 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1980-12-01
2169_2 | coal |  |  | 2169 | Chamois Power Plant | MO | Unit 2 | 2 | Conventional Boiler | Cyclone firing | 50 | 563 | 11.26 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-06-01
2104_2 | coal |  |  | 2104 | Meramec | MO | 002 | 2 | Conventional Boiler | Tangential firing | 128 | 1566 | 12.2344 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1979-12-01
2291_NO5 | coal |  |  | 2291 | North Omaha | NE | NO5 | NO5 | Conventional Boiler | Wall firing - front firing | 224 | 2348.64 | 10.485 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1976-05-01
2384_8 | coal |  |  | 2384 | Deepwater | NJ | Coal-firing | 8 | Conventional Boiler | Wall firing - front firing | 87 | 820 | 9.4253 |  | bituminous | [7 empty] | Other control | Other (specify): Hydrated lime injection to control HCl | 2008-09-01 | NOx control | Selective Noncatalytic Reduction | 2008-09-01 | PM control | Fabric Filter, reverse air | 1981-01-01
2049_5 | coal |  |  | 2049 | Jack Watson | MS | Unit 5 | 5 | Conventional Boiler | Wall firing - front firing | 500 | 4752.86 | 9.5057 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1973-05-01
1915_Boiler 1 | coal |  |  | 1915 | Allen S King | MN | Unit 1 | Boiler 1 | Conventional Boiler | Cyclone firing | 580 | 4730 | 8.1552 | coal - subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-04-01 | SO2 control | Dry FGD - Spray Dryer | 2007-04-01 | Other control | Activated carbon injection |  | PM control | Fabric Filter, pulse | 2007-04-01
2161_3 | coal |  |  | 2161 | James River Power Station | MO | Unit_3_JRPS | 3 | Conventional Boiler | Wall firing - front firing | 44 | 496 | 11.2727 | coal - subbituminous | subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-06-01
1378_2 | coal |  |  | 1378 | Paradise | KY | 2 | 2 | Conventional Boiler | Cyclone firing | 704 | 6959 | 9.8849 | coal - bituminous, coal - subbituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2000-05-01 | PM control | PM scrubber - Venturi | 1983-12-01 | SO2 control | Wet FGD - Venturi Type | 1983-12-01
1353_BSU2 | coal |  |  | 1353 | Big Sandy | KY | BSU-2 | BSU2 | Conventional Boiler | Wall firing - opposed firing | 800 | 7914 | 9.8925 |  | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-07-01
1356_1 | coal |  |  | 1356 | Ghent | KY | GH1 | 1 | Conventional Boiler | Tangential firing | 520 | 6286 | 12.0885 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-12-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
1356_2 | coal |  |  | 1356 | Ghent | KY | GH2 | 2 | Conventional Boiler | Tangential firing | 510 | 5705 | 11.1863 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1977-03-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
1357_5 | coal |  |  | 1357 | Green River | KY | GR04 | 5 | Conventional Boiler | Wall firing - front firing | 102 | 1374 | 13.4706 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1975-12-01
1361_5 | coal |  |  | 1361 | Tyrone | KY | TY3 | 5 | Conventional Boiler | Wall firing - front firing | 75 | 995 | 13.2667 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-12-01
1364_4 | coal |  |  | 1364 | Mill Creek | KY | MC4 | 4 | Conventional Boiler | Wall firing - opposed firing | 517 | 5805 | 11.2282 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-07-01 | SO2 control | Wet FGD - Spray Type | 1982-09-01
1250_4 | coal |  |  | 1250 | Lawrence Energy Center | KS | 4 | 4 | Conventional Boiler | Tangential firing | 126 | 1276 | 10.127 | coal - subbituminous | subbituminous | [7 empty] | PM control | PM scrubber - Venturi | 1976-01-01 | PM control | PM scrubber - Venturi | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 1976-01-01 | SO2 control | Wet FGD - Spray Type | 1976-01-01
1378_1 | coal |  |  | 1378 | Paradise | KY | 1 | 1 | Conventional Boiler | Cyclone firing | 704 | 6959 | 9.8849 | coal - bituminous, coal - subbituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-05-01 | PM control | PM scrubber - Venturi | 1983-09-01 | SO2 control | Wet FGD - Venturi Type | 1983-09-01
1378_3 | coal |  |  | 1378 | Paradise | KY | 3 | 3 | Conventional Boiler | Cyclone firing | 1150.2 | 11457 | 9.9609 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-06-01 | SO2 control | Wet FGD - Spray Type | 2006-10-01
1379_1 | coal |  |  | 1379 | Shawnee | KY | 1 | 1 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1981-06-01 | PM control | Fabric Filter, reverse air | 1981-06-01
1379_6 | coal |  |  | 1379 | Shawnee | KY | 6 | 6 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1980-02-01 | PM control | Fabric Filter, reverse air | 1980-02-01
1379_7 | coal |  |  | 1379 | Shawnee | KY | 7 | 7 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1980-07-01 | PM control | Fabric Filter, reverse air | 1980-07-01
1379_8 | coal |  |  | 1379 | Shawnee | KY | 8 | 8 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1981-02-01 | PM control | Fabric Filter, reverse air | 1981-02-01
1379_9 | coal |  |  | 1379 | Shawnee | KY | 9 | 9 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1981-04-01 | PM control | Fabric Filter, reverse air | 1981-04-01
1743_7 | coal |  |  | 1743 | St Clair Power Plant | MI | SC7-Config | 7 | Conventional Boiler | Tangential firing | 465 | 4547 | 9.7785 |  | bituminous, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-04-01
1382_H2 | coal |  |  | 1382 | HMP&L Station Two Henderson | KY | 2 | H2 | Conventional Boiler | Wall firing - rear firing | 173.1 | 1866.2 | 10.7811 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-04-01 | SO2 control | Wet FGD - Tray Type | 1995-06-01
1239_40 | coal |  |  | 1239 | Riverton | KS | 040 | 40 | Conventional Boiler | Tangential firing | 58 | 600 | 10.3448 |  | petroleum coke, subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1976-01-01
1252_10 | coal |  |  | 1252 | Tecumseh Energy Center | KS | 10 | 10 | Conventional Boiler | Tangential firing | 145 | 1423 | 9.8138 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-08-01
1252_9 | coal |  |  | 1252 | Tecumseh Energy Center | KS | 9 | 9 | Conventional Boiler | Tangential firing | 82 | 846 | 10.3171 | subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-08-01
1295_1 | coal |  |  | 1295 | Quindaro | KS | Unit 1 | 1 | Conventional Boiler | Cyclone firing | 77 | 782 | 10.1558 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-11-01
1356_3 | coal |  |  | 1356 | Ghent | KY | GH3 | 3 | Conventional Boiler | Wall firing - opposed firing | 525 | 5868 | 11.1771 | bituminous | bituminous | [7 empty] | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1981-05-01 | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
1356_4 | coal |  |  | 1356 | Ghent | KY | GH4 | 4 | Conventional Boiler | Wall firing - opposed firing | 525 | 5967 | 11.3657 | bituminous | bituminous | [7 empty] | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1984-06-01 | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-06-01 | SO2 control | Wet FGD - Spray Type | 2008-06-01
1357_4 | coal |  |  | 1357 | Green River | KY | GR03 | 4 | Conventional Boiler | Wall firing - front firing | 72 | 1047 | 14.5417 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-12-01
1363_6 | coal |  |  | 1363 | Cane Run | KY | CR6 | 6 | Conventional Boiler | Tangential firing | 261 | 3017 | 11.5594 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-05-01 | SO2 control | Wet FGD - Spray Type | 1979-04-01
1364_1 | coal |  |  | 1364 | Mill Creek | KY | MC1 | 1 | Conventional Boiler | Tangential firing | 330 | 3723 | 11.2818 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-07-01 | SO2 control | Wet FGD - Spray Type | 1980-12-01
1353_BSU1 | coal |  |  | 1353 | Big Sandy | KY | BSU-1 | BSU1 | Conventional Boiler | Wall firing - opposed firing | 280.5 | 2512 | 8.9554 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-10-01
1364_3 | coal |  |  | 1364 | Mill Creek | KY | MC3 | 3 | Conventional Boiler | Wall firing - opposed firing | 422 | 4896 | 11.6019 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-06-01 | SO2 control | Wet FGD - Spray Type | 1978-08-01
1383_R1 | coal |  |  | 1383 | Robert A Reid | KY | 1 | R1 | Conventional Boiler | Wall firing - front firing | 72 | 616.6 | 8.5639 | coal - bituminous | bituminous | [7 empty] | PM control | Single cyclone | 1966-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-01-01
1077_1 | coal |  |  | 1077 | Sutherland | IA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 31 | 401.5 | 12.9516 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-11-01
1077_2 | coal |  |  | 1077 | Sutherland | IA | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 30.9 | 375.6 | 12.1553 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-11-01
1364_2 | coal |  |  | 1364 | Mill Creek | KY | MC2 | 2 | Conventional Boiler | Tangential firing | 330 | 3788 | 11.4788 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-06-01 | SO2 control | Wet FGD - Spray Type | 1981-12-01
1384_2 | coal |  |  | 1384 | Cooper Station. | KY | Unit 02 | 2 | Conventional Boiler | Wall firing - front firing | 240 | 2418 | 10.075 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-04-01
1379_10 | coal |  |  | 1379 | Shawnee | KY | 10 | 10 | Fluidized bed firing | Fluidized bed firing | 175 | 1800 | 10.2857 | bituminous | bituminous | [7 empty] | PM control | Multiple cyclone | 1981-07-01 | PM control | Fabric Filter, reverse air | 1981-07-01
1379_2 | coal |  |  | 1379 | Shawnee | KY | 2 | 2 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1981-03-01 | PM control | Fabric Filter, reverse air | 1981-03-01
1379_3 | coal |  |  | 1379 | Shawnee | KY | 3 | 3 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1980-11-01 | PM control | Fabric Filter, reverse air | 1980-11-01
1379_4 | coal |  |  | 1379 | Shawnee | KY | 4 | 4 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1980-05-01 | PM control | Fabric Filter, reverse air | 1980-05-01
1379_5 | coal |  |  | 1379 | Shawnee | KY | 5 | 5 | Conventional Boiler | Wall firing - front firing | 175 | 1691 | 9.6629 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Multiple cyclone | 1979-11-01 | PM control | Fabric Filter, reverse air | 1979-11-01
1381_C1 | coal |  |  | 1381 | Kenneth C Coleman | KY | 4 | C1 | Conventional Boiler | Wall firing - front firing | 157.6 | 1623 | 10.2982 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-07-01 | SO2 control | Wet FGD - Tray Type | 2006-02-01
1619_2 | coal |  |  | 1619 | Brayton Point | MA | BP2 | 2 | Conventional Boiler | Tangential firing | 259 | 2458 | 9.4903 | coal - bituminous | subbituminous | [7 empty] | Other control | Other (specify): passes a split stream of flue gas over a vanadium catalyst to generate SO3 from the SO2 in the gas which enhances ESP performance. | 1995-03-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1981-07-01 | Other control | Activated carbon injection | 2008-12-01 | SO2 control | Dry FGD - Spray Dryer | 2008-06-01 | PM control | Fabric Filter, pulse | 2007-09-01
1382_H1 | coal |  |  | 1382 | HMP&L Station Two Henderson | KY | 1 | H1 | Conventional Boiler | Wall firing - rear firing | 166.1 | 1799 | 10.8308 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-06-01 | SO2 control | Wet FGD - Tray Type | 1995-06-01
1381_C2 | coal |  |  | 1381 | Kenneth C Coleman | KY | 4 | C2 | Conventional Boiler | Wall firing - front firing | 146 | 1632 | 11.1781 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-07-01 | SO2 control | Wet FGD - Tray Type | 2006-02-01
1385_1 | coal |  |  | 1385 | Dale Station | KY | 01 | 1 | Conventional Boiler | Wall firing - front firing | 24 | 278 | 11.5833 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-11-01
1385_2 | coal |  |  | 1385 | Dale Station | KY | 02 | 2 | Conventional Boiler | Wall firing - front firing | 24 | 278 | 11.5833 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-10-01
1606_1 | coal |  |  | 1606 | Mount Tom | MA | 1 current | 1 | Conventional Boiler | Wall firing - front firing | 155 | 1480 | 9.5484 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2006-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-09-01 | SO2 control | Dry FGD - Circulating Dry Scrubber | 2009-12-01 | PM control | Fabric Filter, pulse | 2009-12-01
1619_1 | coal |  |  | 1619 | Brayton Point | MA | BP1 | 1 | Conventional Boiler | Tangential firing | 258 | 2528 | 9.7984 | coal - bituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2006-10-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1981-03-01 | Other control | Activated carbon injection | 2007-12-01 | SO2 control | Dry FGD - Spray Dryer | 2008-07-01 | PM control | Fabric Filter, pulse | 2008-03-01
1626_2 | coal |  |  | 1626 | Salem Harbor | MA | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 78.763 | 1014 | 12.8741 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1992-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-09-01
1626_3 | coal |  |  | 1626 | Salem Harbor | MA | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 151.751 | 1783 | 11.7495 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1993-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-06-01
1381_C3 | coal |  |  | 1381 | Kenneth C Coleman | KY | 4 | C3 | Conventional Boiler | Wall firing - rear firing | 165 | 1660 | 10.0606 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-08-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-07-01 | SO2 control | Wet FGD - Tray Type | 2006-02-01
1384_1 | coal |  |  | 1384 | Cooper Station. | KY | Unit 01 | 1 | Conventional Boiler | Wall firing - front firing | 124 | 1381 | 11.1371 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-06-01
3403_4 | coal |  |  | 3403 | Gallatin | TN | 4 | 4 | Conventional Boiler | Tangential firing | 327.6 | 3032 | 9.2552 | coal - subbituminous, coal - bituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-04-01
3138_4 | coal |  |  | 3138 | New Castle Plant | PA | NC4-2 | 4 | Conventional Boiler | Wall firing - front firing | 114 | 1025 | 8.9912 | coal - subbituminous, coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
3264_3 | coal |  |  | 3264 | W. S. Lee | SC | 3 | 3 | Conventional Boiler | Tangential firing | 182.1 | 2252 | 12.3668 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1971-01-01
3280_CAN1 | coal |  |  | 3280 | Canadys Steam | SC | CAN001 | CAN1 | Conventional Boiler | Tangential firing | 121 | 1141.5 | 9.4339 |  | Bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-06-01
3280_CAN2 | coal |  |  | 3280 | Canadys Steam | SC | CAN002 | CAN2 | Conventional Boiler | Tangential firing | 123 | 1175.7 | 9.5585 |  | Bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-12-01
3317_1 | coal |  |  | 3317 | Dolphus M Grainger | SC | G1 | 1 | Conventional Boiler | Wall firing - front firing | 87 | 940 | 10.8046 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-06-01
3317_2 | coal |  |  | 3317 | Dolphus M Grainger | SC | G2 | 2 | Conventional Boiler | Wall firing - front firing | 87 | 972 | 11.1724 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1966-06-01
3393_3 | coal |  |  | 3393 | Allen Steam Plant | TN | 3 | 3 | Conventional Boiler | Cyclone firing | 330 | 3064 | 9.2848 | coal - subbituminous, coal - bituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-01-01
3406_9 | coal |  |  | 3406 | Johnsonville | TN | 9 | 9 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | 10.0347 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-02-01
3152_2A | coal |  |  | 3152 | Sunbury Generation LP | PA | Boiler 2A | 2A | Conventional Boiler | Arch firing | 40 | 525 | 13.125 | coal - bituminous | petroleum coke, bituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1970-06-01
2872_4 | coal |  |  | 2872 | Muskingum River | OH | MR-4 | 4 | Conventional Boiler | Cyclone firing | 237.5 | 2150 | 9.0526 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-11-01
2952_5 | coal |  |  | 2952 | Muskogee | OK | MK5 Config | 5 | Conventional Boiler | Tangential firing | 415 | 5373.0016 | 12.947 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-10-01
2952_6 | coal |  |  | 2952 | Muskogee | OK | MK6 Config | 6 | Conventional Boiler | Tangential firing | 371 | 5214.89 | 14.0563 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1984-06-01
3122_2 | coal |  |  | 3122 | Homer City Station | PA | HC2CONFIG | 2 | Conventional Boiler | Wall firing - opposed firing | 655 | 5690.552 | 8.6879 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2000-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-04-01
3122_3 | coal |  |  | 3122 | Homer City Station | PA | HC3CONFIG | 3 | Conventional Boiler | Wall firing - opposed firing | 680 | 6175 | 9.0809 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1977-12-01 | SO2 control | Wet FGD - Spray Type | 2001-09-01
3122_1 | coal |  |  | 3122 | Homer City Station | PA | HC1CONFIG | 1 | Conventional Boiler | Wall firing - opposed firing | 655 | 5898.68 | 9.0056 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1969-08-01
3405_1 | coal |  |  | 3405 | John Sevier | TN | 1 | 1 | Conventional Boiler | Tangential firing | 200 | 1967 | 9.835 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-04-01
2872_5 | coal |  |  | 2872 | Muskingum River | OH | MR-5 | 5 | Conventional Boiler | Cyclone firing | 615.2 | 5550 | 9.0215 |  | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2005-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-08-01
2876_1 | coal |  |  | 2876 | Kyger Creek | OH | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 214 | 2111.41 | 9.8664 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-10-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-06-01
2876_2 | coal |  |  | 2876 | Kyger Creek | OH | Unit 2 | 2 | Conventional Boiler | Wall firing - front firing | 213 | 2135.931 | 10.0278 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-04-01
2963_3313 | coal |  |  | 2963 | Northeastern | OK | NE-3 | 3313 | Conventional Boiler | Tangential firing | 490 | 4775 | 9.7449 | subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
2963_3314 | coal |  |  | 2963 | Northeastern | OK | NE-4 | 3314 | Conventional Boiler | Tangential firing | 490 | 4775 | 9.7449 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-09-01
3113_1 | coal |  |  | 3113 | Portland | PA | POR-1 | 1 | Conventional Boiler | Tangential firing | 172 | 1719 | 9.9942 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1989-01-01
3113_2 | coal |  |  | 3113 | Portland | PA | POR-2 | 2 | Conventional Boiler | Tangential firing | 255 | 2542 | 9.9686 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1987-05-01
2535_1 | coal |  |  | 2535 | AES Cayuga, LLC | NY | Unit_1 | 1 | Conventional Boiler | Tangential firing | 164 | 1462 | 8.9146 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning |  | SO2 control | Wet FGD - Spray Type | 1995-06-01
3399_1 | coal |  |  | 3399 | Cumberland | TN | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1300 | 14130 | 10.8692 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | Other control | Other (specify): Hydrated Lime for Opacity | 2006-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-06-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
3406_4 | coal |  |  | 3406 | Johnsonville | TN | 4 | 4 | Conventional Boiler | Tangential firing | 125 | 1405 | 11.24 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-09-01
3406_5 | coal |  |  | 3406 | Johnsonville | TN | 5 | 5 | Conventional Boiler | Tangential firing | 147 | 1566 | 10.6531 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-08-01
3406_6 | coal |  |  | 3406 | Johnsonville | TN | 6 | 6 | Conventional Boiler | Tangential firing | 147 | 1566 | 10.6531 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-07-01
3407_2 | coal |  |  | 3407 | Kingston | TN | 2 | 2 | Conventional Boiler | Tangential firing | 175 | 1641 | 9.3771 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-12-01
3407_3 | coal |  |  | 3407 | Kingston | TN | 3 | 3 | Conventional Boiler | Tangential firing | 175 | 1641 | 9.3771 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-11-01
3407_4 | coal |  |  | 3407 | Kingston | TN | 4 | 4 | Conventional Boiler | Tangential firing | 175 | 1641 | 9.3771 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-10-01
3407_5 | coal |  |  | 3407 | Kingston | TN | 5 | 5 | Conventional Boiler | Tangential firing | 200 | 2056 | 10.28 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-09-01
3406_10 | coal |  |  | 3406 | Johnsonville | TN | 10 | 10 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | 10.0347 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-07-01
3776_52 | coal |  |  | 3776 | Glen Lyn | VA | GL-5 | 52 | Conventional Boiler | Tangential firing | 50 | 572 | 11.44 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
3406_1 | coal |  |  | 3406 | Johnsonville | TN | 1 | 1 | Conventional Boiler | Tangential firing | 125 | 1405 | 11.24 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2005-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01
3788_4 | coal |  |  | 3788 | Potomac River | VA | 4 | 4 | Conventional Boiler | Tangential firing | 108 | 961 | 8.8981 | coal - bituminous | bituminous | [7 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1956-02-01
3936_2 | coal |  |  | 3936 | Kanawha River | WV | KR-2 | 2 | Conventional Boiler | Vertical firing | 219.6 | 1950 | 8.8798 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-06-01
3938_11 | coal |  |  | 3938 | Philip Sporn | WV | SP-1 | 11 | Conventional Boiler | Vertical firing | 152.5 | 1311 | 8.5967 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-01-01
3938_21 | coal |  |  | 3938 | Philip Sporn | WV | SP-2 | 21 | Conventional Boiler | Vertical firing | 152.5 | 1311 | 8.5967 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-01-01
3938_31 | coal |  |  | 3938 | Philip Sporn | WV | SP-3 | 31 | Conventional Boiler | Vertical firing | 152.5 | 1311 | 8.5967 |  | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-10-01
3406_7 | coal |  |  | 3406 | Johnsonville | TN | 7 | 7 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | 10.0347 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1989-11-01
3406_8 | coal |  |  | 3406 | Johnsonville | TN | 8 | 8 | Conventional Boiler | Wall firing - front firing | 172.8 | 1734 | 10.0347 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-05-01
3776_51 | coal |  |  | 3776 | Glen Lyn | VA | GL-5 | 51 | Conventional Boiler | Tangential firing | 50 | 572 | 11.44 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
3297_WAT1 | coal |  |  | 3297 | Wateree | SC | WAT001 | WAT1 | Conventional Boiler | Wall firing - unspecified | 383 | 3329.7 | 8.6937 |  | Bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Fabric Filter, unspecified | 2001-05-01 | SO2 control | Wet FGD - Unspecified
3140_3 | coal |  |  | 3140 | PPL Brunner Island | PA | U3 | 3 | Conventional Boiler | Tangential firing | 780 | 7239 | 9.2808 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2007-06-01 | SO2 control | Wet FGD - Tray Type | 2009-03-01
3178_1 | coal |  |  | 3178 | Armstrong Power Station | PA | Unit 1 | 1 | Conventional Boiler | Wall firing - unspecified | 184 | 1749 | 9.5054 |  | Bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01
3178_2 | coal |  |  | 3178 | Armstrong Power Station | PA | Unit 2 | 2 | Conventional Boiler | Wall firing - unspecified | 183 | 1706 | 9.3224 |  | Bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-06-01
3181_33 | coal |  |  | 3181 | Mitchell Power Station | PA | 033 | 33 | Conventional Boiler | Tangential firing | 289 | 2563 | 8.8685 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1971-01-01 | SO2 control | Wet FGD - Spray Type | 1983-01-01
3264_1 | coal |  |  | 3264 | W. S. Lee | SC | 1 | 1 | Conventional Boiler | Tangential firing | 105.9 | 1215 | 11.4731 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1969-08-01
3264_2 | coal |  |  | 3264 | W. S. Lee | SC | 2 | 2 | Conventional Boiler | Tangential firing | 105.8 | 1215 | 11.4839 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/ flue gas conditioning | 1969-08-01
3406_2 | coal |  |  | 3406 | Johnsonville | TN | 2 | 2 | Conventional Boiler | Tangential firing | 125 | 1405 | 11.24 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2008-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-03-01
2876_5 | coal |  |  | 2876 | Kyger Creek | OH | Unit 5 | 5 | Conventional Boiler | Wall firing - front firing | 213 | 2129.638 | 9.9983 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-05-01
3297_WAT2 | coal |  |  | 3297 | Wateree | SC | WAT002 | WAT2 | Conventional Boiler | Wall firing - unspecified | 380 | 3305.1 | 8.6976 |  | Bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-04-01 | PM control | Fabric Filter, unspecified | 2001-07-01 | SO2 control | Wet FGD - Unspecified
3319_3 | coal |  |  | 3319 | Jefferies | SC | J3 | 3 | Conventional Boiler | Wall firing - front firing | 164 | 1780 | 10.8537 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-01-01
3319_4 | coal |  |  | 3319 | Jefferies | SC | J4 | 4 | Conventional Boiler | Wall firing - front firing | 162 | 1602 | 9.8889 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1970-07-01
3393_1 | coal |  |  | 3393 | Allen Steam Plant | TN | 1 | 1 | Conventional Boiler | Cyclone firing | 330 | 3064 | 9.2848 | coal - subbituminous, coal - bituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-11-01
3393_2 | coal |  |  | 3393 | Allen Steam Plant | TN | 2 | 2 | Conventional Boiler | Cyclone firing | 330 | 3064 | 9.2848 | coal - subbituminous, coal - bituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-09-01
3399_2 | coal |  |  | 3399 | Cumberland | TN | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 1300 | 14130 | 10.8692 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | Other control | Other (specify): Hydrated Lime for opacity | 2006-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-06-01 | SO2 control | Wet FGD - Spray Type | 1995-01-01
3403_1 | coal |  |  | 3403 | Gallatin | TN | 1 | 1 | Conventional Boiler | Tangential firing | 300 | 2750 | 9.1667 | coal - subbituminous, coal - bituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-02-01
3403_3 | coal |  |  | 3403 | Gallatin | TN | 3 | 3 | Conventional Boiler | Tangential firing | 327.6 | 3032 | 9.2552 | coal - subbituminous, coal - bituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-01-01
2713_3 | coal |  |  | 2713 | L.V. Sutton Electric Plant | NC | Sut_Cfg_3b | 3 | Conventional Boiler | Wall firing - rear firing | 420 | 3695 | 8.7976 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2005-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-06-01
2952_4 | coal |  |  | 2952 | Muskogee | OK | MK4 Config | 4 | Conventional Boiler | Tangential firing | 391 | 5360.25 | 13.7091 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-12-01
2723_1 | coal |  |  | 2723 | Dan River | NC | 1 | 1 | Conventional Boiler | Tangential firing | 71 | 1140 | 16.0563 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-01-01
2723_2 | coal |  |  | 2723 | Dan River | NC | 2 | 2 | Conventional Boiler | Tangential firing | 70.4 | 1140 | 16.1932 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-01-01
2727_Unit 2 | coal |  |  | 2727 | Marshall | NC | U22007 | Unit 2 | Conventional Boiler | Tangential firing | 400 | 3663.2 | 9.158 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2002-01-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
2727_Unit 3 | coal |  |  | 2727 | Marshall | NC | U3 | Unit 3 | Conventional Boiler | Tangential firing | 700 | 6103.1 | 8.7187 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2008-12-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2006-12-01 | SO2 control | Wet FGD - Spray Type | 2007-03-01
2732_10 | coal |  |  | 2732 | Riverbend | NC | 10 | 10 | Conventional Boiler | Tangential firing | 141.1 | 1318 | 9.3409 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1995-01-01
2716_3 | coal |  |  | 2716 | W.H. Weatherspoon Plant | NC | Wea_Cfg_3 | 3 | Conventional Boiler | Tangential firing | 79 | 962 | 12.1772 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-12-01
2713_2 | coal |  |  | 2713 | L.V. Sutton Electric Plant | NC | Sut_Cfg_1 | 2 | Conventional Boiler | Wall firing - front firing | 110 | 1081 | 9.8273 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1975-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-07-01
2718_ES-2 | coal |  |  | 2718 | G G Allen | NC | 2-2009 | ES-2 | Conventional Boiler | Tangential firing | 177 | 1509 | 8.5254 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1988-10-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
2718_ES-5 | coal |  |  | 2718 | G G Allen | NC | 5-2009 | ES-5 | Conventional Boiler | Tangential firing | 285.3 | 2705 | 9.4812 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2008-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2000-06-01 | SO2 control | Wet FGD - Spray Type | 2009-03-01
2720_Boiler 5 | coal |  |  | 2720 | Buck | NC | 5 | Boiler 5 | Conventional Boiler | Tangential firing | 40 | 619 | 15.475 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-02-01
2720_Boiler 6 | coal |  |  | 2720 | Buck | NC | 6 | Boiler 6 | Conventional Boiler | Tangential firing | 40 | 619 | 15.475 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-02-01
2720_Boiler 7 | coal |  |  | 2720 | Buck | NC | 7 | Boiler 7 | Conventional Boiler | Tangential firing | 40 | 619 | 15.475 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-12-01
2723_3 | coal |  |  | 2723 | Dan River | NC | 3 | 3 | Conventional Boiler | Tangential firing | 151 | 1710 | 11.3245 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-01-01
2713_1 | coal |  |  | 2713 | L.V. Sutton Electric Plant | NC | Sut_Cfg_1 | 1 | Conventional Boiler | Tangential firing | 103 | 1081 | 10.4951 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1975-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-07-01
2535_2 | coal |  |  | 2535 | AES Cayuga, LLC | NY | Unit_2 | 2 | Conventional Boiler | Tangential firing | 168 | 1450 | 8.631 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning |  | SO2 control | Wet FGD - Spray Type | 1995-01-01
2718_ES-1 | coal |  |  | 2718 | G G Allen | NC | 1-2009 | ES-1 | Conventional Boiler | Tangential firing | 176.2 | 1738 | 9.8638 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1988-10-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
2549_68 | coal |  |  | 2549 | CR Huntley Generating Station | NY | 068 | 68 | Conventional Boiler | Tangential firing | 201 | 1836 | 9.1343 |  | Bituminous, Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Sorbent Injection |  | Other control | Activated carbon injection |  | PM control | Fabric Filter, unspecified | 2008-12-01
2732_8 | coal |  |  | 2732 | Riverbend | NC | 8 | 8 | Conventional Boiler | Tangential firing | 100 | 1059 | 10.59 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-10-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1995-01-01
2708_6 | coal |  |  | 2708 | Cape Fear Steam Electric Plant | NC | Cap_Cfg_6b | 6 | Conventional Boiler | Tangential firing | 184 | 1752 | 9.5217 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
2709_1 | coal |  |  | 2709 | H.F. Lee Plant | NC | Lee_Cfg_1 | 1 | Conventional Boiler | Tangential firing | 80 | 704 | 8.8 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1974-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
2709_2 | coal |  |  | 2709 | H.F. Lee Plant | NC | Lee_Cfg_1 | 2 | Conventional Boiler | Wall firing - front firing | 82 | 833 | 10.1585 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1974-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-11-01
2709_3 | coal |  |  | 2709 | H.F. Lee Plant | NC | Lee_Cfg_3b | 3 | Conventional Boiler | Wall firing - opposed firing | 260 | 2412 | 9.2769 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2007-03-19 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-12-01
2549_67 | coal |  |  | 2549 | CR Huntley Generating Station | NY | 067 | 67 | Conventional Boiler | Tangential firing | 204 | 1836 | 9 |  | Bituminous, Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | SO2 control | Dry FGD - Sorbent Injection |  | Other control | Activated carbon injection |  | PM control | Fabric Filter, unspecified | 2009-01-01
2830_4 | coal |  |  | 2830 | Walter C Beckjord | OH | 4 | 4 | Conventional Boiler | Tangential firing | 162 | 1423 | 8.784 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1974-01-01
2830_5 | coal |  |  | 2830 | Walter C Beckjord | OH | 5 | 5 | Conventional Boiler | Tangential firing | 255 | 2367 | 9.2824 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-01-01
2830_6 | coal |  |  | 2830 | Walter C Beckjord | OH | 6 | 6 | Conventional Boiler | Tangential firing | 443 | 3979 | 8.9819 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
2836_10 | coal |  |  | 2836 | Avon Lake | OH | AL10 | 10 | Conventional Boiler | Tangential firing | 101 | 1447 | 14.3267 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-01-01
2836_12 | coal |  |  | 2836 | Avon Lake | OH | AL12-2 | 12 | Conventional Boiler | Wall firing - opposed firing | 680 | 6581 | 9.6779 |  | subbituminous, bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1985-01-01
2840_4 | coal |  |  | 2840 | Conesville | OH | CV-4 | 4 | Conventional Boiler | Tangential firing | 841.5 | 7960 | 9.4593 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-06-01 | Other control | Dry sorbent injection | 2009-06-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2009-06-01
2840_5 | coal |  |  | 2840 | Conesville | OH | CV-5 | 5 | Conventional Boiler | Tangential firing | 443.9 | 4091 | 9.216 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-09-01 | SO2 control | Wet FGD - Spray Type | 1977-05-01
2727_Unit 1 | coal |  |  | 2727 | Marshall | NC | U12007 | Unit 1 | Conventional Boiler | Tangential firing | 400 | 3658.2 | 9.1455 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-12-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
2848_H-4 | coal |  |  | 2848 | O H Hutchings | OH | H-4 | H-4 | Conventional Boiler | Tangential firing | 64 | 696 | 10.875 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2824_10 | coal |  |  | 2824 | Stanton | ND | u10 | 10 | Conventional Boiler | Tangential firing | 60 | 642 | 10.7 | coal - subbituminous | subbituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 2000-01-01 | PM control | Fabric Filter, reverse air | 2000-01-01
2848_H-6 | coal |  |  | 2848 | O H Hutchings | OH | H-6 | H-6 | Conventional Boiler | Tangential firing | 60.5 | 646 | 10.6777 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2850_B003 | coal |  |  | 2850 | J M Stuart | OH | MS3W | B003 | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | 9.3098 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-02-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-05-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2008-02-01
2850_B004 | coal |  |  | 2850 | J M Stuart | OH | MS4W | B004 | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | 9.3098 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-02-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-06-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2008-02-01
2872_1 | coal |  |  | 2872 | Muskingum River | OH | MR-1 | 1 | Conventional Boiler | Wall firing - front firing | 219.6 | 2050 | 9.3352 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-05-01
2872_2 | coal |  |  | 2872 | Muskingum River | OH | MR-2 | 2 | Conventional Boiler | Wall firing - front firing | 219.6 | 2050 | 9.3352 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-03-01
2872_3 | coal |  |  | 2872 | Muskingum River | OH | MR-3 | 3 | Conventional Boiler | Cyclone firing | 237.5 | 2150 | 9.0526 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-06-01
2876_3 | coal |  |  | 2876 | Kyger Creek | OH | Unit 3 | 3 | Conventional Boiler | Wall firing - front firing | 213 | 2138.101 | 10.038 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-02-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-02-01
2876_4 | coal |  |  | 2876 | Kyger Creek | OH | Unit 4 | 4 | Conventional Boiler | Wall firing - front firing | 213 | 2158.716 | 10.1348 | coal - bituminous, coal - subbituminous | bituminous, subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-03-01
3788_5 | coal |  |  | 3788 | Potomac River | VA | 5 | 5 | Conventional Boiler | Tangential firing | 108 | 961 | 8.8981 | coal - bituminous | bituminous | [7 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1957-05-01
2848_H-3 | coal |  |  | 2848 | O H Hutchings | OH | H-3 | H-3 | Conventional Boiler | Tangential firing | 62.5 | 716 | 11.456 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2832_Unit 8 | coal |  |  | 2832 | Miami Fort | OH | U8 | Unit 8 | Conventional Boiler | Wall firing - opposed firing | 550 | 5003 | 9.0964 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-01-01 | SO2 control | Wet FGD - Spray Type | 2007-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-02-01
2917_9 | coal |  |  | 2917 | Hamilton | OH | Unit 9 | 9 | Conventional Boiler | Tangential firing | 50.6 | 729 | 14.4071 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1974-06-01 | SO2 control | Dry FGD - Spray Dryer | 2001-06-01 | PM control | Single cyclone | 1997-01-01 | PM control | Fabric Filter, pulse | 1997-01-01
2732_9 | coal |  |  | 2732 | Riverbend | NC | 9 | 9 | Conventional Boiler | Tangential firing | 141.7 | 1318 | 9.3013 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2006-11-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1995-01-01
2790_B1 | coal |  |  | 2790 | R.M. Heskett Station | ND | B1 | B1 | Conventional Boiler | Stoker - traveling grate | 22 | 320 | 14.5455 |  | Lignite, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1976-01-01
2790_B2 | coal |  |  | 2790 | R.M. Heskett Station | ND | B2 | B2 | Fluidized bed firing | Fluidized bed firing | 78 | 900 | 11.5385 |  | Lignite, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, unspecified | 1976-01-01
2828_2 | coal |  |  | 2828 | Cardinal | OH | CD-U2 | 2 | Conventional Boiler | Wall firing - opposed firing | 615.2 | 5275 | 8.5744 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-01-01 | Other control | Dry sorbent injection | 2007-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2007-12-01
2830_1 | coal |  |  | 2830 | Walter C Beckjord | OH | 1 | 1 | Conventional Boiler | Tangential firing | 100 | 971 | 9.71 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-01-01
2830_2 | coal |  |  | 2830 | Walter C Beckjord | OH | 2 | 2 | Conventional Boiler | Tangential firing | 100 | 999 | 9.99 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-01-01
2830_3 | coal |  |  | 2830 | Walter C Beckjord | OH | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 135 | 1215 | 9 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1971-01-01
2832_Unit 7 | coal |  |  | 2832 | Miami Fort | OH | U7 | Unit 7 | Conventional Boiler | Wall firing - opposed firing | 550 | 4995 | 9.0818 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-01-01 | SO2 control | Wet FGD - Spray Type | 2007-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-05-01
2828_1 | coal |  |  | 2828 | Cardinal | OH | CD-U1 | 1 | Conventional Boiler | Wall firing - opposed firing | 615.2 | 5275 | 8.5744 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-01-01 | Other control | Dry sorbent injection | 2008-03-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2008-03-01
2840_6 | coal |  |  | 2840 | Conesville | OH | CV-6 | 6 | Conventional Boiler | Tangential firing | 443.9 | 4091 | 9.216 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-03-01 | SO2 control | Wet FGD - Spray Type | 1977-08-01
2843_9 | coal |  |  | 2843 | Picway | OH | PI | 9 | Conventional Boiler | Wall firing - front firing | 106.2 | 1290 | 12.1469 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-12-01
2848_H-1 | coal |  |  | 2848 | O H Hutchings | OH | H-1 | H-1 | Conventional Boiler | Tangential firing | 53 | 607 | 11.4528 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2848_H-2 | coal |  |  | 2848 | O H Hutchings | OH | H-2 | H-2 | Conventional Boiler | Tangential firing | 53 | 574 | 10.8302 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1973-01-01
2850_B001 | coal |  |  | 2850 | J M Stuart | OH | MS1W | B001 | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | 9.3098 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-02-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-05-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2008-05-01
2850_B002 | coal |  |  | 2850 | J M Stuart | OH | MS2W | B002 | Conventional Boiler | Wall firing - opposed firing | 623 | 5800 | 9.3098 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-02-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-10-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2008-05-01
2824_1 | coal |  |  | 2824 | Stanton | ND | u1 | 1 | Conventional Boiler | Wall firing - front firing | 132 | 1800 | 13.6364 | subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 2000-01-01
2832_Unit 6 | coal |  |  | 2832 | Miami Fort | OH | U6 | Unit 6 | Conventional Boiler | Tangential firing | 175 | 1253 | 7.16 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1960-11-01
6166_MB2 | coal |  |  | 6166 | Rockport | IN | RP-2 | MB2 | Conventional Boiler | Wall firing - opposed firing | 1320 | 12374 | 9.3742 | subbituminous | subbituminous | [7 empty] | Other control | Activated carbon injection | 2009-09-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1989-12-01
6177_U2B | coal |  |  | 6177 | Coronado Generating Station | AZ | U2B | U2B | Conventional Boiler | Wall firing - unspecified | 456.6 | 4719 | 10.3351 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, unspecified | 1980-10-01
6113_5 | coal |  |  | 6113 | Gibson | IN | 5 | 5 | Conventional Boiler | Wall firing - opposed firing | 661 | 6655 | 10.0681 | coal - bituminous | bituminous | [7 empty] | Other control | Other (specify): Soda Ash Injection for SO3 mitigation | 2004-06-01 | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-01-01 | SO2 control | Wet FGD - Spray Type | 1982-09-01
6124_1 | coal |  |  | 6124 | McIntosh | GA | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 165 | 1598.3345 | 9.6869 | oil - distillate | No.2 Fuel Oil (distillate) | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1981-01-01
6139_2 | coal |  |  | 6139 | Welsh | TX | WE-2 | 2 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | 9.2401 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1980-04-01
6166_MB1 | coal |  |  | 6166 | Rockport | IN | RP-1 | MB1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 12374 | 9.3742 |  | bituminous, subbituminous | [7 empty] | Other control | Activated carbon injection | 2009-09-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-12-01
6170_1 | coal |  |  | 6170 | Pleasant Prairie | WI | PPPPB1 | 1 | Conventional Boiler | Wall firing - opposed firing | 655 | 6449 | 9.8458 | subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2006-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-06-01 | SO2 control | Wet FGD - Spray Type | 2006-11-01
6204_1 | coal |  |  | 6204 | Laramie River Station | WY | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 605 | 6420 | 10.6116 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-07-01 | SO2 control | Wet FGD - Tray Type | 1980-07-01
6204_2 | coal |  |  | 6204 | Laramie River Station | WY | 2 | 2 | Conventional Boiler | Wall firing - opposed firing | 602 | 6420 | 10.6645 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-07-01 | SO2 control | Wet FGD - Tray Type | 1981-07-01
6204_3 | coal |  |  | 6204 | Laramie River Station | WY | 3 | 3 | Conventional Boiler | Wall firing - opposed firing | 610 | 6600 | 10.8197 | coal - subbituminous | subbituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1982-11-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-11-01
6213_1SG1 | coal |  |  | 6213 | Merom | IN | 1SG1conf1 | 1SG1 | Conventional Boiler | Wall firing - opposed firing | 515 | 5088 | 9.8796 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-11-01 | SO2 control | Wet FGD - Packed Type | 1983-09-01
6213_2SG1 | coal |  |  | 6213 | Merom | IN | 2SG1conf2 | 2SG1 | Conventional Boiler | Wall firing - opposed firing | 515 | 5088 | 9.8796 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1982-02-01 | SO2 control | Wet FGD - Packed Type | 1982-02-01
6249_1 | coal |  |  | 6249 | Winyah | SC | W1 | 1 | Conventional Boiler | Wall firing - rear firing | 295 | 2904 | 9.8441 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-03-01 | SO2 control | Wet FGD - Spray Type | 2007-04-01
6249_2 | coal |  |  | 6249 | Winyah | SC | W2 | 2 | Conventional Boiler | Wall firing - opposed firing | 305 | 2908 | 9.5344 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-07-01 | SO2 control | Wet FGD - Spray Type | 2007-05-01
6139_3 | coal |  |  | 6139 | Welsh | TX | WE-3 | 3 | Conventional Boiler | Wall firing - opposed firing | 558 | 5156 | 9.2401 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1982-03-01
6090_1 | coal |  |  | 6090 | Sherburne County | MN | Unit 1 | 1 | Conventional Boiler | Tangential firing | 741 | 6909 | 9.3239 | coal - subbituminous | subbituminous | [7 empty] | PM control | PM scrubber - Venturi | 1976-05-01 | SO2 control | Wet FGD - Spray Type | 1976-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2001-01-01
6061_1 | coal |  |  | 6061 | South Mississippi El Pwr Assn | MS | 1 | 1 | Conventional Boiler | Turbo | 204 | 2600 | 12.7451 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-04-01 | SO2 control | Wet FGD - Venturi Type | 1978-04-01
6061_2 | coal |  |  | 6061 | South Mississippi El Pwr Assn | MS | 2 | 2 | Conventional Boiler | Turbo | 204 | 2600 | 12.7451 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-04-01 | SO2 control | Wet FGD - Venturi Type | 1978-04-01
6068_3 | coal |  |  | 6068 | Jeffrey Energy Center | KS | 3 | 3 | Conventional Boiler | Tangential firing | 783 | 7815 | 9.9808 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-05-01 | SO2 control | Wet FGD - Spray Type | 1983-05-01
6071_1 | coal |  |  | 6071 | Trimble Co. | KY | TC01 | 1 | Conventional Boiler | Tangential firing | 547 | 5602 | 10.2413 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-12-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1990-09-01 | Other control | Other (specify): Sorbent injection for SO3 reduction | 2008-07-01 | SO2 control | Wet FGD - Spray Type | 1990-12-01
3407_1 | coal |  |  | 3407 | Kingston | TN | 1 | 1 | Conventional Boiler | Tangential firing | 175 | 1641 | 9.3771 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-02-01
6073_2 | coal |  |  | 6073 | Victor J. Daniel Jr | MS | Unit 2 | 2 | Conventional Boiler | Tangential firing | 536 | 5166.728 | 9.6394 | coal - subbituminous, coal - bituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01
6177_U1B | coal |  |  | 6177 | Coronado Generating Station | AZ | U1B | U1B | Conventional Boiler | Wall firing - unspecified | 456.6 | 4719 | 10.3351 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, unspecified | 1979-12-01
6170_2 | coal |  |  | 6170 | Pleasant Prairie | WI | PPPPB2 | 2 | Conventional Boiler | Wall firing - opposed firing | 643 | 6449 | 10.0295 | subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-04-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1985-05-01 | SO2 control | Wet FGD - Spray Type | 2007-03-01
6090_2 | coal |  |  | 6090 | Sherburne County | MN | Unit 2 | 2 | Conventional Boiler | Tangential firing | 737 | 6770 | 9.1859 | coal - subbituminous | subbituminous | [7 empty] | PM control | PM scrubber - Venturi | 1977-04-01 | SO2 control | Wet FGD - Spray Type | 1977-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 2001-01-01
6096_NC1 | coal |  |  | 6096 | Nebraska City | NE | NC1 | NC1 | Conventional Boiler | Wall firing - front firing | 646 | 6554.962 | 10.147 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-05-01
6138_1 | coal |  |  | 6138 | Flint Creek | AR | FC-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 558 | 6324 | 11.3333 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-05-01
6082_1 | coal |  |  | 6082 | AES Somerset LLC | NY | 001 | 1 | Conventional Boiler | Wall firing - opposed firing | 680.8 | 6280 | 9.2244 |  | Bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 1999-01-01 | Other control | Dry sorbent injection |  | PM control | Electrostatic precipitator, unspecified | 1984-01-01 | SO2 control | Wet FGD - Spray Type | 1984-01-01
8223_1 | coal |  |  | 8223 | Springerville | AZ | 1 | 1 | Conventional Boiler | Tangential firing | 427 | 3830 | 8.9696 | coal - subbituminous | subbituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1985-06-01 | PM control | Fabric Filter, reverse air | 1985-06-01
7253_2 | coal |  |  | 7253 | Richard Gorsuch | OH | UNIT2 | 2 | Conventional Boiler | Radiant | 53.3 | 550.9 | 10.3358 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-06-01
7253_4 | coal |  |  | 7253 | Richard Gorsuch | OH | UNIT4 | 4 | Conventional Boiler | Radiant | 53.3 | 519 | 9.7373 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-06-01
8042_Unit 2 | coal |  |  | 8042 | Belews Creek Steam Station | NC | 2-2008 | Unit 2 | Conventional Boiler | Wall firing - opposed firing | 1183 | 10800 | 9.1293 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1974-01-01 | SO2 control | Wet FGD - Spray Type | 2008-05-01
6641_2 | coal |  |  | 6641 | Independence | AR | 002 | 2 | Conventional Boiler | Tangential firing | 879 | 8700 | 9.8976 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1984-12-06
8223_2 | coal |  |  | 8223 | Springerville | AZ | 2 | 2 | Conventional Boiler | Tangential firing | 430 | 3830 | 8.907 | bituminous | bituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1990-06-01 | PM control | Fabric Filter, reverse air | 1990-06-01
8226_1 | coal |  |  | 8226 | Cheswick Power Plant | PA | CH2 | 1 | Conventional Boiler | Tangential firing | 612 | 6000 | 9.8039 | coal - subbituminous, coal - bituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1970-12-01
10002_1 | coal |  |  | 10002 | ACE Cogeneration Company | CA | Config 1 | 1 | Fluidized bed firing | Fluidized bed firing | 117 | 1052 | 8.9915 | bituminous | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 1991-01-01 | PM control | Fabric Filter, reverse air | 1991-01-01
8219_1 | coal |  |  | 8219 | Ray D Nixon | CO | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 225 | 2095 | 9.3111 | subbituminous | subbituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1980-04-01
7790_1-1 | coal |  |  | 7790 | Bonanza Power Plant | UT | 1-1 | 1-1 | Conventional Boiler | Wall firing - opposed firing | 483 | 4899 | 10.1429 | Bituminous | Bituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1985-11-01 | SO2 control | Wet FGD - Spray Type | 1985-11-01
6073_1 | coal |  |  | 6073 | Victor J. Daniel Jr | MS | Unit 1 | 1 | Conventional Boiler | Tangential firing | 537 | 5206.306 | 9.6952 | coal - subbituminous, coal - bituminous | subbituminous, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1998-01-01
6481_1SGA | coal |  |  | 6481 | Intermountain Power Project | UT | U1 | 1SGA | Conventional Boiler | Wall firing - opposed firing | 950 | 8180 | 8.6105 | bituminous | bituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1986-06-01 | SO2 control | Wet FGD - Spray Type | 1986-06-01
6481_2SGA | coal |  |  | 6481 | Intermountain Power Project | UT | U2 | 2SGA | Conventional Boiler | Wall firing - opposed firing | 950 | 8220 | 8.6526 | bituminous | bituminous | [7 empty] | PM control | Fabric Filter, reverse air | 1987-05-01 | SO2 control | Wet FGD - Spray Type | 1987-05-01
6768_1 | coal |  |  | 6768 | Sikeston Power Station | MO | 1 | 1 | Conventional Boiler | Wall firing - opposed firing | 233 | 2780 | 11.9313 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-09-01
6772_1 | coal |  |  | 6772 | Hugo | OK | 001 | 1 | Conventional Boiler | Wall firing - unspecified | 465 | 4567 | 9.8215 |  | Bituminous, Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1982-01-01
6823_W1 | coal |  |  | 6823 | D B Wilson | KY | 1 | W1 | Conventional Boiler | Wall firing - opposed firing | 443 | 4477 | 10.1061 | Bituminous | Bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-09-01 | Other control | Dry sorbent injection | 2006-03-01 | SO2 control | Wet FGD - Spray Type | 1984-09-01
8042_Unit 1 | coal |  |  | 8042 | Belews Creek Steam Station | NC | 1-2008 | Unit 1 | Conventional Boiler | Wall firing - opposed firing | 1185.8 | 10800 | 9.1078 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-06-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1973-01-01 | SO2 control | Wet FGD - Spray Type | 2008-01-01
6249_3 | coal |  |  | 6249 | Winyah | SC | W3 | 3 | Conventional Boiler | Wall firing - opposed firing | 305 | 2877 | 9.4328 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2005-04-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Spray Type | 1980-05-01
6249_4 | coal |  |  | 6249 | Winyah | SC | W4 | 4 | Conventional Boiler | Wall firing - opposed firing | 305 | 3051 | 10.0033 | coal - bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1981-11-01 | SO2 control | Wet FGD - Spray Type | 1981-11-01
6257_3 | coal |  |  | 6257 | Scherer | GA | Unit 3 | 3 | Conventional Boiler | Tangential firing | 880 | 9362.5 | 10.6392 | subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1987-01-01 | Other control | Activated carbon injection | 2009-02-01 | PM control | Fabric Filter, pulse | 2009-02-01
6257_4 | coal |  |  | 6257 | Scherer | GA | Unit 4 | 4 | Conventional Boiler | Tangential firing | 880 | 8821.5854 | 10.0245 | subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1989-02-01 | Other control | Activated carbon injection |  | PM control | Fabric Filter, pulse
6264_1 | coal |  |  | 6264 | Mountaineer | WV | Mt-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 1320 | 11960 | 9.0606 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-01-01 | Other control | Dry sorbent injection | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-09-01 | SO2 control | Wet FGD - Spray Type | 2007-01-01
6639_G1 | coal |  |  | 6639 | R D Green | KY | 1 | G1 | Conventional Boiler | Wall firing - opposed firing | 250 | 2704.2 | 10.8168 | coal - bituminous, petroleum coke | petroleum coke, bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-12-01 | SO2 control | Wet FGD - Spray Type | 1979-12-01
6641_1 | coal |  |  | 6641 | Independence | AR | 001 | 1 | Conventional Boiler | Tangential firing | 853 | 8700 | 10.1993 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, unspecified | 1983-01-18
7253_1 | coal |  |  | 7253 | Richard Gorsuch | OH | UNIT1 | 1 | Conventional Boiler | Radiant | 53.3 | 455.3 | 8.5422 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1972-06-01
3944_2 | coal |  |  | 3944 | Harrison Power Station | WV | Boiler2 | 2 | Conventional Boiler | Wall firing - unspecified | 692 | 6042 | 8.7312 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1973-12-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
4072_7 | coal |  |  | 4072 | Pulliam | WI | 7 | 7 | Conventional Boiler | Wall firing - rear firing | 87.7 | 999 | 11.3911 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1958-11-01
4042_2 | coal |  |  | 4042 | Valley | WI | VAPP-B2 | 2 | Conventional Boiler | Wall firing - front firing | 72 | 868 | 12.0556 | bituminous | bituminous | 0.00037607 | [6 empty] | PM control | Fabric Filter, pulse | 1994-06-01
4042_4 | coal |  |  | 4042 | Valley | WI | VAPP-B4 | 4 | Conventional Boiler | Wall firing - front firing | 72 | 868 | 12.0556 | bituminous | bituminous | 0.00042245 | [6 empty] | PM control | Fabric Filter, pulse | 1995-06-01
4054_2 | coal |  |  | 4054 | Nelson Dewey | WI | Unit 2 | 2 | Conventional Boiler | Cyclone firing | 117.1 | 1161 | 9.9146 | coal - subbituminous, petroleum coke | petroleum coke, subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, unspecified | 1974-06-01
4072_5 | coal |  |  | 4072 | Pulliam | WI | 5 | 5 | Conventional Boiler | Wall firing - rear firing | 53.63 | 693 | 12.9219 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1953-01-01
4078_2 | coal |  |  | 4078 | Weston | WI | W2 | 2 | Conventional Boiler | Wall firing - front firing | 88.9 | 1000 | 11.2486 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1972-01-01
4041_8 | coal |  |  | 4041 | South Oak Creek | WI | OCPP-B8 | 8 | Conventional Boiler | Tangential firing | 336 | 3009 | 8.9554 | subbituminous | subbituminous | 0.00016794 | [6 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1991-07-01
4271_B1 | coal |  |  | 4271 | John P. Madgett | WI | 001 | B1 | Conventional Boiler | Turbo | 425.73 | 4029.5 | 9.4649 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, unspecified | 1979-12-01 | PM control | Fabric Filter, unspecified | 2007-10-01
3992_8 | coal |  |  | 3992 | Blount Street | WI | 8B6T | 8 | Conventional Boiler | Wall firing - front firing | 53.4 | 575 | 10.7678 | coal - bituminous, other non-fossil fuel (specify) | natural gas, bituminous | [7 empty] | PM control | Multiple cyclone | 1957-06-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-01-01
3944_3 | coal |  |  | 3944 | Harrison Power Station | WV | Boiler3 | 3 | Conventional Boiler | Wall firing - unspecified | 692 | 5876 | 8.4913 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1972-12-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
3948_1 | coal |  |  | 3948 | Mitchell | WV | MI-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1977-02-01 | SO2 control | Wet FGD - Tray Type | 2007-01-01
6031_2 | coal |  |  | 6031 | Killen Station | OH | 2-Operation | 2 | Conventional Boiler | Wall firing - opposed firing | 658 | 5928 | 9.0091 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1982-06-01 | NOx control | Selective Catalytic Reduction | 2003-11-01 | SO2 control | Wet FGD - Jet Bubbling Reactor | 2007-06-01
3992_9 | coal |  |  | 3992 | Blount Street | WI | 9B7T | 9 | Conventional Boiler | Wall firing - front firing | 53.2 | 575 | 10.8083 | coal - bituminous, other non-fossil fuel (specify) | natural gas, bituminous | [7 empty] | PM control | Multiple cyclone | 1961-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-01-01
4041_5 | coal |  |  | 4041 | South Oak Creek | WI | OCPP-B5 | 5 | Conventional Boiler | Wall firing - front firing | 273 | 2488 | 9.1136 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-03-01
4041_6 | coal |  |  | 4041 | South Oak Creek | WI | OCPP-B6 | 6 | Conventional Boiler | Wall firing - front firing | 278 | 2516 | 9.0504 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1972-04-01
4054_1 | coal |  |  | 4054 | Nelson Dewey | WI | Unit 1 | 1 | Conventional Boiler | Cyclone firing | 120 | 1222 | 10.1833 | coal - subbituminous, petroleum coke | petroleum coke, subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, unspecified | 1974-03-01
4072_6 | coal |  |  | 4072 | Pulliam | WI | 6 | 6 | Conventional Boiler | Wall firing - rear firing | 73.7 | 875 | 11.8725 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1951-11-01
3936_1 | coal |  |  | 3936 | Kanawha River | WV | KR-1 | 1 | Conventional Boiler | Vertical firing | 219.6 | 1950 | 8.8798 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1969-06-01
3407_6 | coal |  |  | 3407 | Kingston | TN | 6 | 6 | Conventional Boiler | Tangential firing | 200 | 2056 | 10.28 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-07-01
3407_7 | coal |  |  | 3407 | Kingston | TN | 7 | 7 | Conventional Boiler | Tangential firing | 200 | 2056 | 10.28 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-06-01
3407_8 | coal |  |  | 3407 | Kingston | TN | 8 | 8 | Conventional Boiler | Tangential firing | 200 | 2056 | 10.28 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2004-07-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-04-01
3407_9 | coal |  |  | 3407 | Kingston | TN | 9 | 9 | Conventional Boiler | Tangential firing | 200 | 2056 | 10.28 | coal - bituminous, coal - subbituminous | subbituminous, bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2006-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1976-02-01
3776_6 | coal |  |  | 3776 | Glen Lyn | VA | GL-6 | 6 | Conventional Boiler | Wall firing - front firing | 237.5 | 2040 | 8.5895 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-03-01
3788_1 | coal |  |  | 3788 | Potomac River | VA | 1 | 1 | Conventional Boiler | Tangential firing | 93 | 970 | 10.4301 | coal - bituminous | bituminous | [7 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1949-10-01
3788_2 | coal |  |  | 3788 | Potomac River | VA | 2 | 2 | Conventional Boiler | Tangential firing | 93 | 970 | 10.4301 | coal - bituminous | bituminous | [7 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1950-06-01
3788_3 | coal |  |  | 3788 | Potomac River | VA | 3 | 3 | Conventional Boiler | Tangential firing | 108 | 961 | 8.8981 | coal - bituminous | bituminous | [7 empty] | SO2 control | Dry FGD - Sorbent Injection | 2006-05-01 | PM control | Electrostatic precipitator, hot side, w/o flue gas conditioning | 1978-10-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1954-06-01
3935_3 | coal |  |  | 3935 | John E. Amos | WV | AM-3 | 3 | Conventional Boiler | Wall firing - opposed firing | 1300 | 11936 | 9.1815 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2001-05-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1973-10-01 | SO2 control | Wet FGD - Spray Type | 2009-02-01
3948_2 | coal |  |  | 3948 | Mitchell | WV | MI-2 | 2 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2007-01-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-08-01 | SO2 control | Wet FGD - Tray Type | 2007-01-01
3938_41 | coal |  |  | 3938 | Philip Sporn | WV | SP-4 | 41 | Conventional Boiler | Vertical firing | 152.5 | 1311 | 8.5967 |  | bituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction | 2009-01-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-10-01
3938_51 | coal |  |  | 3938 | Philip Sporn | WV | SP-5 | 51 | Conventional Boiler | Wall firing - opposed firing | 495.5 | 3961 | 7.9939 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-03-01
3944_1 | coal |  |  | 3944 | Harrison Power Station | WV | Boiler1 | 1 | Conventional Boiler | Wall firing - unspecified | 693 | 5779 | 8.3391 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2002-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1974-12-01 | SO2 control | Wet FGD - Spray Type | 1994-11-01
3947_1 | coal |  |  | 3947 | Kammer | WV | K-1 | 1 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | 9.0779 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-08-01
3947_2 | coal |  |  | 3947 | Kammer | WV | K-2 | 2 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | 9.0779 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-10-01
3982_5 | coal |  |  | 3982 | Bay Front | WI | 5 | 5 | Conventional Boiler | Cyclone firing | 32 | 389 | 12.1562 | coal - subbituminous | natural gas, subbituminous | [7 empty] | PM control | Multiple cyclone | 1976-08-01
3992_7 | coal |  |  | 3992 | Blount Street | WI | 7B1345T | 7 | Conventional Boiler | Cell burner | 22.4 | 310 | 13.8393 | coal - bituminous | bituminous, natural gas | [7 empty] | PM control | Multiple cyclone | 1949-12-01 | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1975-01-01
3935_1 | coal |  |  | 3935 | John E. Amos | WV | AM-1 | 1 | Conventional Boiler | Wall firing - opposed firing | 816.3 | 7020 | 8.5998 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction |  | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-04-01
6021_C3 | coal |  |  | 6021 | Craig | CO | C3 | C3 | Conventional Boiler | Wall firing - opposed firing | 478 | 4124 | 8.6276 | coal - subbituminous | subbituminous | [7 empty] | SO2 control | Dry FGD - Spray Dryer | 1984-10-01 | PM control | Fabric Filter, reverse air | 1984-10-01
6034_1 | coal |  |  | 6034 | Belle River | MI | BR1-Config | 1 | Conventional Boiler | Wall firing - opposed firing | 674 | 6814 | 10.1098 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1984-06-01
6034_2 | coal |  |  | 6034 | Belle River | MI | BR2-Config | 2 | Conventional Boiler | Wall firing - opposed firing | 677.1 | 6814 | 10.0635 | subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1985-07-01
6052_2 | coal |  |  | 6052 | Wansley | GA | Unit 2 | 2 | Conventional Boiler | Tangential firing | 920 | 8554.28 | 9.2981 | bituminous | bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1978-04-01 | SO2 control | Wet FGD - Spray Type | 2009-05-01
6064_N1 | coal |  |  | 6064 | Nearman Creek | KS | N1 | N1 | Conventional Boiler | Wall firing - front firing | 257.4 | 2433 | 9.4522 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1988-01-01
3947_3 | coal |  |  | 3947 | Kammer | WV | K-3 | 3 | Conventional Boiler | Cyclone firing | 237.5 | 2156 | 9.0779 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-04-01
6085_15 | coal |  |  | 6085 | R.M. Schahfer | IN | R.M.0015 | 15 | Conventional Boiler | Wall firing - opposed firing | 502 | 5100 | 10.1594 |  | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1979-01-01
6085_17 | coal |  |  | 6085 | R.M. Schahfer | IN | R.M.0017 | 17 | Conventional Boiler | Tangential firing | 393 | 3967 | 10.0941 |  | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-04-01 | SO2 control | Wet FGD - Spray Type | 1983-04-01
6085_18 | coal |  |  | 6085 | R.M. Schahfer | IN | R.M.0018 | 18 | Conventional Boiler | Tangential firing | 393 | 3967 | 10.0941 | bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1986-01-01 | SO2 control | Wet FGD - Spray Type | 1986-02-01
6095_1 | coal |  |  | 6095 | Sooner | OK | SO1 Config | 1 | Conventional Boiler | Tangential firing | 401 | 5428.8091 | 13.5382 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-11-01
6095_2 | coal |  |  | 6095 | Sooner | OK | SO2 Config | 2 | Conventional Boiler | Tangential firing | 383 | 5661.8362 | 14.7829 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-12-01
6068_1 | coal |  |  | 6068 | Jeffrey Energy Center | KS | 1 | 1 | Conventional Boiler | Tangential firing | 790 | 8396 | 10.6278 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1978-07-01 | SO2 control | Wet FGD - Spray Type | 1978-05-01
4143_1 | coal |  |  | 4143 | Genoa | WI | 001 | 1 | Conventional Boiler | Tangential firing | 373.5 | 3627.69 | 9.7127 |  | Bituminous, Subbituminous | [7 empty] | SO2 control | Dry FGD - Unspecified |  | PM control | Electrostatic precipitator, cold side, unspecified | 1969-07-01 | PM control | Fabric Filter, unspecified | 2007-05-01
6068_2 | coal |  |  | 6068 | Jeffrey Energy Center | KS | 2 | 2 | Conventional Boiler | Tangential firing | 786 | 8124 | 10.3359 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1980-05-01 | SO2 control | Wet FGD - Spray Type | 1980-05-01
4140_B5 | coal |  |  | 4140 | Alma | WI | B5 | B5 | Conventional Boiler | Wall firing - unspecified | 83.5 | 862.65 | 10.3311 |  | Bituminous, Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | Electrostatic precipitator, cold side, unspecified | 1974-06-01
4140_B4 | coal |  |  | 4140 | Alma | WI | B4 | B4 | Conventional Boiler | Wall firing - unspecified | 53.63 | 557.2 | 10.3897 |  | Bituminous, Subbituminous | [7 empty] | NOx control | Selective Noncatalytic Reduction |  | PM control | Electrostatic precipitator, cold side, unspecified | 1974-06-01
4259_1 | coal |  |  | 4259 | Endicott Station | MI | 1 | 1 | Conventional Boiler | Wall firing - front firing | 60 | 617 | 10.2833 | coal - bituminous | bituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1979-09-01 | SO2 control | Wet FGD - Tray Type | 1979-09-01
6002_1 | coal |  |  | 6002 | James H. Miller Jr. | AL | Unit 1 | 1 | Conventional Boiler | Wall firing - front firing | 725 | 7015.9856 | 9.6772 | coal - subbituminous | subbituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2005-05-01 | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1999-05-01
6009_2 | coal |  |  | 6009 | White Bluff | AR | 002 | 2 | Conventional Boiler | Tangential firing | 881 | 8700 | 9.8751 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1981-07-21
6009_1 | coal |  |  | 6009 | White Bluff | AR | 001 | 1 | Conventional Boiler | Tangential firing | 853 | 8700 | 10.1993 |  | Subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/o flue gas conditioning | 1983-06-17
4078_1 | coal |  |  | 4078 | Weston | WI | W1 | 1 | Conventional Boiler | Wall firing - front firing | 63.6 | 858 | 13.4906 | coal - subbituminous | subbituminous | [7 empty] | PM control | Electrostatic precipitator, cold side, w/ flue gas conditioning | 1971-01-01
6004_1 | coal |  |  | 6004 | Pleasants Power Station | WV | 001 | 1 | Conventional Boiler | Wall firing - unspecified | 700 | 5969 | 8.5271 |  | Bituminous | [7 empty] | NOx control | Selective Catalytic Reduction | 2003-05-01 | PM control | Electrostatic precipitator, cold side, unspecified | 1979-03-01 | SO2 control | Wet FGD - Tray Type | 1979-03-01

## Pb_Variability
facility_name | facility_id | boiler_id | configuration_id | compound | Final_EF | Final_EF_Units | Final_Output_EF | Final_Output_EF_Units | From | Report_id | Pb_Min_lb_per_MWh_Rank | New Souce MACT Floor Test_ID | New Source MACT Floor QA Calc | New Source Floor Agreement of QA Calc
Weston | 4078 | 4 | W4 | Lead | 9.9562e-08 | lb/MMBtu | 8.965e-07 | lb/MW | ERT |  | 1
Weston | 4078 | 4 | W4 | Lead | 1.5467e-06 | lb/MMBtu | 1.3927e-05 | lb/MW | Part II | W4 Metals 2008 | 1
Reid Gardner | 2324 | 1 | 1 | Lead | 9.0551e-08 | lb/MMBtu | 9.9116e-07 | lb/MW | ERT |  | 2
Dallman | 963 | 34 | 34 | Lead | 1.36e-07 | lb/MMBtu | 1.1412e-06 | lb/MW | Part II | Dallman 34 Test 1 | 3
Dallman | 963 | 34 | 34 | Lead | 1.39e-07 | lb/MMBtu | 1.1664e-06 | lb/MW | Part II | Dallman 34 Test 2 | 3
Dallman | 963 | 34 | 34 | Lead | 2.3e-07 | lb/MMBtu | 1.9299e-06 | lb/MW | ERT |  | 3
Rawhide | 6761 | 101 | Rawhide101 | Lead | 1.3236e-07 | lb/MMBtu | 1.2151e-06 | lb/MW | ERT |  | 4
Brandon Shores | 602 | 2 | 002 | Lead | 1.4171e-07 | lb/MMBtu | 1.376e-06 | lb/MW | ERT |  | 5
Logan Generating Plant | 10043 | B01 | Unit1 | Lead | 1.8499e-07 | lb/MMBtu | 1.6195e-06 | lb/MW | ERT |  | 6
Logan Generating Plant | 10043 | B01 | Unit1 | Lead | 4.41e-05 | lb/MMBtu | 0.00038608 | lb/MW | Part II | 2005 Annual Stack Test-4 | 6
Havana | 891 | Boiler 9 | Boiler 9 | Lead | 1.5555e-07 | lb/MMBtu | 1.6266e-06 | lb/MW | ERT |  | 7
TransAlta Centralia Generation | 3845 | BD21 | BW21CONFIG | Lead | 1.2896e-07 | lb/MMBtu | 1.6559e-06 | lb/MW | ERT |  | 8
PSEG Mercer Generating Station | 2408 | E1 | MERU1E1PT1OS1-Coal | Lead | 1.8879e-07 | lb/MMBtu | 1.7063e-06 | lb/MW | ERT |  | 9
PSEG Mercer Generating Station | 2408 | E1 | MERU1E1PT1OS1-Coal | Lead | 5.3333e-07 | lb/MMBtu | 4.8202e-06 | lb/MW | Part II | MER1 2009 1YR ST Co NG | 9
AES Hawaii | 10673 | BLR B | 002 | Lead | 1.8823e-07 | lb/MMBtu | 1.751e-06 | lb/MW | ERT |  | 10
Walter Scott Jr. Energy Center | 1082 | 4 | 4 | Lead | 2e-07 | lb/MMBtu | 1.8059e-06 | lb/MW | Part II | 8/2007 PB | 11
Walter Scott Jr. Energy Center | 1082 | 4 | 4 | Lead | 1.4205e-06 | lb/MMBtu | 1.2826e-05 | lb/MW | ERT |  | 11
Walter Scott Jr. Energy Center | 1082 | 4 | 4 | Lead | 3e-06 | lb/MMBtu | 2.7088e-05 | lb/MW | Part II | 5/2007 PB | 11
Cholla | 113 | 4 | 004 | Lead | 1.8284e-07 | lb/MMBtu | 1.8362e-06 | lb/MW | ERT |  | 12
Chambers Cogeneration LP | 10566 | Boil 2 | Boil 2 | Lead | 1.9971e-07 | lb/MMBtu | 1.9439e-06 | lb/MW | ERT |  | 13
Asheville Steam Electric Plant | 2706 | 1 | Ash_Cfg_1d | Lead | 2.1842e-07 | lb/MMBtu | 2.0196e-06 | lb/MW | Part II | Ash_Blr_1_Test_8t | 14
Asheville Steam Electric Plant | 2706 | 1 | Ash_Cfg_1d | Lead | 7.0733e-07 | lb/MMBtu | 6.5403e-06 | lb/MW | Part II | Ash_Blr_1_Test_10e | 14
Asheville Steam Electric Plant | 2706 | 1 | Ash_Cfg_1d | Lead | 4.0292e-06 | lb/MMBtu | 3.7256e-05 | lb/MW | ERT |  | 14
Asheville Steam Electric Plant | 2706 | 2 | Ash_Cfg_2 | Lead | 2.1983e-07 | lb/MMBtu | 2.0496e-06 | lb/MW | ERT |  | 15
Asheville Steam Electric Plant | 2706 | 2 | Ash_Cfg_2 | Lead | 4.31e-07 | lb/MMBtu | 4.0184e-06 | lb/MW | Part II | Ash_Blr_2_Test_8e | 15
Asheville Steam Electric Plant | 2706 | 2 | Ash_Cfg_2 | Lead | 6.28e-07 | lb/MMBtu | 5.8552e-06 | lb/MW | Part II | Ash_Blr_2_Test_7o | 15
Cope | 7210 | COP1 | COP001 | Lead | 2.3286e-07 | lb/MMBtu | 2.1433e-06 | lb/MW | ERT |  | 16
Craig | 6021 | C2 | C2 | Lead | 2.3491e-07 | lb/MMBtu | 2.1992e-06 | lb/MW | ERT |  | 17
Northampton Generating Company, L.P. | 50888 | BLR1 | GEN1 | Lead | 2.4467e-07 | lb/MMBtu | 2.3172e-06 | lb/MW | ERT |  | 18
Northampton Generating Company, L.P. | 50888 | BLR1 | GEN1 | Lead | 1.055e-06 | lb/MMBtu | 9.9918e-06 | lb/MW | Part II | TDF 2009 Stack Test - #226-013 | 18
AES Shady Point,LLC | 10671 | 2a | Unit 2 | Lead | 1.7942e-07 | lb/MMBtu | 2.4904e-06 | lb/MW | ERT |  | 19
AES Shady Point,LLC | 10671 | 2b | Unit 2 | Lead | 1.7942e-07 | lb/MMBtu | 2.4904e-06 | lb/MW | ERT |  | 20
AES Shady Point,LLC | 10671 | 1b | Unit 1 | Lead | 1.7942e-07 | lb/MMBtu | 2.4904e-06 | lb/MW | ERT |  | 21
AES Shady Point,LLC | 10671 | 1A | Unit 1 | Lead | 1.7942e-07 | lb/MMBtu | 2.4904e-06 | lb/MW | ERT |  | 22
H L Spurlock Station | 6041 | 4 | Unit 04 | Lead | 2.67e-07 | lb/MMBtu | 2.492e-06 | lb/MW | Part II | Compliance_metals_05/27/09 | 23
H L Spurlock Station | 6041 | 4 | Unit 04 | Lead | 3.3251e-06 | lb/MMBtu | 3.1034e-05 | lb/MW | ERT |  | 23
AES Thames | 10675 | B | B | Lead | 2.7067e-07 | lb/MMBtu | 2.6078e-06 | lb/MW | Part II | 8 | 24
AES Hawaii | 10673 | BLR A | 001 | Lead | 2.5955e-07 | lb/MMBtu | 2.6119e-06 | lb/MW | ERT |  | 25
Gerald Gentleman | 6077 | 2 | U2 | Lead | 2.6402e-07 | lb/MMBtu | 2.6536e-06 | lb/MW | ERT |  | 26
Elm Road Generating Station | 56068 | 1 | ERGS-B1 | Lead | 2.7919e-07 | lb/MMBtu | 2.6867e-06 | lb/MW | ERT |  | 27
Chambers Cogeneration LP | 10566 | Boil 1 | Boil 1 | Lead | 2.7617e-07 | lb/MMBtu | 2.688e-06 | lb/MW | ERT |  | 28
R D Green | 6639 | G2 | 2 | Lead | 2.3581e-07 | lb/MMBtu | 2.6902e-06 | lb/MW | ERT |  | 29
Crist | 641 | 5 | Unit 5 | Lead | 2.7154e-07 | lb/MMBtu | 2.7082e-06 | lb/MW | ERT |  | 30
Crist | 641 | 6 | Unit 6 | Lead | 2.7154e-07 | lb/MMBtu | 2.7097e-06 | lb/MW | ERT |  | 31
PSEG Mercer Generating Station | 2408 | E2 | MERU2E2PT2OS1-Coal | Lead | 3.0277e-07 | lb/MMBtu | 2.7364e-06 | lb/MW | ERT |  | 32
PSEG Mercer Generating Station | 2408 | E2 | MERU2E2PT2OS1-Coal | Lead | 5.3333e-07 | lb/MMBtu | 4.8202e-06 | lb/MW | Part II | MER2 2009 1YR ST Co NG | 32
Springerville | 8223 | 4 | 4 | Lead | 3e-07 | lb/MMBtu | 2.8e-06 | lb/MW | Part II | U4 INITIAL PERF 09DEC13 (HG, PB) | 33
Springerville | 8223 | 4 | 4 | Lead | 3.5303e-07 | lb/MMBtu | 3.295e-06 | lb/MW | ERT |  | 33
Crist | 641 | 7 | Unit 7 | Lead | 2.7154e-07 | lb/MMBtu | 2.8673e-06 | lb/MW | ERT |  | 34
Crist | 641 | 4 | Unit 4 | Lead | 2.7154e-07 | lb/MMBtu | 2.8771e-06 | lb/MW | ERT |  | 35
Welsh | 6139 | 1 | WE-1 | Lead | 3.119e-07 | lb/MMBtu | 2.882e-06 | lb/MW | ERT |  | 36
Cedar Bay Generating Company L.P. | 10672 | CBC | CBC1 | Lead | 2.5177e-07 | lb/MMBtu | 2.9091e-06 | lb/MW | Part II | CBCmetals2009 | 37
Cedar Bay Generating Company L.P. | 10672 | CBC | CBC1 | Lead | 9.3139e-07 | lb/MMBtu | 1.0762e-05 | lb/MW | ERT |  | 37
Springerville | 8223 | 3 | 3 | Lead | 3.15e-07 | lb/MMBtu | 2.94e-06 | lb/MW | Part II | U3 INITIAL PERF TESTS (PB, HG) | 38
Springerville | 8223 | 3 | 3 | Lead | 3.8553e-07 | lb/MMBtu | 3.5983e-06 | lb/MW | ERT |  | 38
Duck Creek | 6016 | 1 | 001 | Lead | 2.7008e-07 | lb/MMBtu | 3.0384e-06 | lb/MW | ERT |  | 39
Duck Creek | 6016 | 1 | 001 | Lead | 4.8e-07 | lb/MMBtu | 5.4e-06 | lb/MW | Part II | 3 | 39
A. B. Brown Generating Station | 6137 | 1 | 1Config | Lead | 3.2147e-07 | lb/MMBtu | 3.0545e-06 | lb/MW | ERT |  | 40
Sheldon Station | 2277 | 1 | U1 | Lead | 2.9119e-07 | lb/MMBtu | 3.1257e-06 | lb/MW | ERT |  | 41
Stanton Energy Center | 564 | 2 | 2 coal | Lead | 3.4737e-07 | lb/MMBtu | 3.1813e-06 | lb/MW | ERT |  | 42
Dunkirk Generating Plant | 2554 | 4 | 4 | Lead | 3.3841e-07 | lb/MMBtu | 3.1863e-06 | lb/MW | ERT |  | 43
Clover | 7213 | 2 | Unit 2 | Lead | 2.8178e-07 | lb/MMBtu | 3.273e-06 | lb/MW | ERT |  | 44
TransAlta Centralia Generation | 3845 | BD22 | BW22CONFIG | Lead | 2.4106e-07 | lb/MMBtu | 3.292e-06 | lb/MW | ERT |  | 45
Wygen 1 | 55479 | 3 | WYG1Cfg | Lead | 2.9383e-07 | lb/MMBtu | 3.4e-06 | lb/MW | ERT |  | 46
Dunkirk Generating Plant | 2554 | 1 | 1 | Lead | 3.1348e-07 | lb/MMBtu | 3.4011e-06 | lb/MW | ERT |  | 47
San Juan | 2451 | Unit 3 | Unit 3 | Lead | 3.2299e-07 | lb/MMBtu | 3.4187e-06 | lb/MW | ERT |  | 48
Sheldon Station | 2277 | 2 | U2 | Lead | 3.2129e-07 | lb/MMBtu | 3.4499e-06 | lb/MW | ERT |  | 49
J K Spruce | 7097 | BLR1 | 1 | Lead | 3.1761e-07 | lb/MMBtu | 3.4833e-06 | lb/MW | ERT |  | 50
J K Spruce | 7097 | BLR1 | 1 | Lead | 1.6433e-06 | lb/MMBtu | 1.8023e-05 | lb/MW | Part II | JKS Unit 1 Test Report June 2009 | 50
AES Warrior Run Cogeneration Facility | 10678 | BLR1 | BLR1 | Lead | 3.4524e-07 | lb/MMBtu | 3.4985e-06 | lb/MW | ERT |  | 51
Wygen 2 | 56319 | 0001 | WYG2Cfg | Lead | 2.6068e-07 | lb/MMBtu | 3.53e-06 | lb/MW | ERT |  | 52
Bridgeport Station | 568 | BHB3 | BHSEMU3OS2-Coal | Lead | 3.4743e-07 | lb/MMBtu | 3.5347e-06 | lb/MW | ERT |  | 53
James H. Miller Jr. | 6002 | 4 | Unit 4 | Lead | 3.7468e-07 | lb/MMBtu | 3.6154e-06 | lb/MW | ERT |  | 54
AES Thames | 10675 | A | A | Lead | 3.8033e-07 | lb/MMBtu | 3.6644e-06 | lb/MW | Part II | 7 | 55
Sunnyside Cogen Associates | 50951 | 1 | Config 1 | Lead | 3.1721e-07 | lb/MMBtu | 3.7007e-06 | lb/MW | ERT |  | 56
Gibson | 6113 | 1 | 1-2007-FGDIN | Lead | 3.9105e-07 | lb/MMBtu | 3.7673e-06 | lb/MW | ERT |  | 57
San Juan | 2451 | Unit 2 | Unit 2 | Lead | 3.7876e-07 | lb/MMBtu | 3.7753e-06 | lb/MW | ERT |  | 58
Cedar Bay Generating Company L.P. | 10672 | CBA | CBA1 | Lead | 3.2951e-07 | lb/MMBtu | 3.8072e-06 | lb/MW | ERT |  | 59
Cedar Bay Generating Company L.P. | 10672 | CBA | CBA1 | Lead | 4.2366e-07 | lb/MMBtu | 4.8951e-06 | lb/MW | Part II | CBA2009metals | 59
Cedar Bay Generating Company L.P. | 10672 | CBB | CBB1 | Lead | 3.3319e-07 | lb/MMBtu | 3.8498e-06 | lb/MW | ERT |  | 60
Cedar Bay Generating Company L.P. | 10672 | CBB | CBB1 | Lead | 5.3484e-07 | lb/MMBtu | 6.1798e-06 | lb/MW | Part II | CBB2009metals | 60
Cross | 130 | 3 | C3 | Lead | 3.9976e-07 | lb/MMBtu | 3.8748e-06 | lb/MW | ERT |  | 61
Cross | 130 | 3 | C3 | Lead | 2.2333e-06 | lb/MMBtu | 2.1647e-05 | lb/MW | Part II | C3TVM292007 | 61
Neil Simpson II | 7504 | 2 | NS2Cfg | Lead | 3.2935e-07 | lb/MMBtu | 4.1169e-06 | lb/MW | ERT |  | 62
Clover | 7213 | 1 | Unit 1 | Lead | 3.6458e-07 | lb/MMBtu | 4.1644e-06 | lb/MW | ERT |  | 63
G G Allen | 2718 | ES-3 | 3-2009 | Lead | 5.2983e-07 | lb/MMBtu | 4.1935e-06 | lb/MW | ERT |  | 64
G G Allen | 2718 | ES-4 | 4-2009 | Lead | 5.2983e-07 | lb/MMBtu | 4.2415e-06 | lb/MW | ERT |  | 65
Pulliam | 4072 | 8 | 8 | Lead | 3.9747e-07 | lb/MMBtu | 4.3522e-06 | lb/MW | ERT |  | 66
J T Deely | 6181 | 1 | 1 | Lead | 4.6153e-07 | lb/MMBtu | 4.3599e-06 | lb/MW | ERT |  | 67
J T Deely | 6181 | 2 | 2 | Lead | 4.6153e-07 | lb/MMBtu | 4.3599e-06 | lb/MW | ERT |  | 68
TS Power Plant | 56224 | BLR100 | TSPower | Lead | 5.0883e-07 | lb/MMBtu | 4.4407e-06 | lb/MW | Part II | Optimal 07/2009 | 69
TS Power Plant | 56224 | BLR100 | TSPower | Lead | 7.58e-07 | lb/MMBtu | 6.6153e-06 | lb/MW | Part II | TRC 04/2008 | 69
TS Power Plant | 56224 | BLR100 | TSPower | Lead | 8.4269e-07 | lb/MMBtu | 7.3544e-06 | lb/MW | ERT |  | 69
Roxboro Steam Electric Plant | 2712 | 1 | Rox_Cfg_1b | Lead | 4.5783e-07 | lb/MMBtu | 4.4654e-06 | lb/MW | ERT |  | 70
Roxboro Steam Electric Plant | 2712 | 1 | Rox_Cfg_1b | Lead | 9.8733e-07 | lb/MMBtu | 9.6297e-06 | lb/MW | Part II | Rox_Blr_1_Test_8e | 70
Roxboro Steam Electric Plant | 2712 | 1 | Rox_Cfg_1b | Lead | 6.37e-05 | lb/MMBtu | 0.00062128 | lb/MW | Part II | Rox_Blr_1_Test_7e | 70
INDIANTOWN COGENERATION L.P. | 50976 | AABO1 | 001 | Lead | 4.9e-07 | lb/MMBtu | 4.6448e-06 | lb/MW | Part II | 10669-3 | 71
INDIANTOWN COGENERATION L.P. | 50976 | AABO1 | 001 | Lead | 3.5017e-06 | lb/MMBtu | 3.3193e-05 | lb/MW | ERT |  | 71
RS Nelson | 1393 | 6 | 001 | Lead | 4.7787e-07 | lb/MMBtu | 4.7466e-06 | lb/MW | ERT |  | 72
PPL Montour | 3149 | 2 | U2 | Lead | 5.2017e-07 | lb/MMBtu | 4.7545e-06 | lb/MW | ERT |  | 73
Sioux | 2107 | 2 | 002 | Lead | 5.1346e-07 | lb/MMBtu | 4.8211e-06 | lb/MW | ERT |  | 74
Hatfield's Ferry Power Station | 3179 | 1 | 001 | Lead | 5.1104e-07 | lb/MMBtu | 4.9372e-06 | lb/MW | ERT |  | 75
Hatfield's Ferry Power Station | 3179 | 1 | 001 | Lead | 7.6e-06 | lb/MMBtu | 7.3424e-05 | lb/MW | Part II | Pb-11/09-1 | 75
Roxboro Steam Electric Plant | 2712 | 2 | Rox_Cfg_2c | Lead | 5.1169e-07 | lb/MMBtu | 5.0172e-06 | lb/MW | ERT |  | 76
Roxboro Steam Electric Plant | 2712 | 2 | Rox_Cfg_2c | Lead | 5.4013e-07 | lb/MMBtu | 5.2961e-06 | lb/MW | Part II | Rox_Blr_2_Test_8j | 76
Roxboro Steam Electric Plant | 2712 | 2 | Rox_Cfg_2c | Lead | 1.0705e-06 | lb/MMBtu | 1.0496e-05 | lb/MW | Part II | Rox_Blr_2_Test_10e | 76
Roxboro Steam Electric Plant | 2712 | 2 | Rox_Cfg_2c | Lead | 2.3177e-06 | lb/MMBtu | 2.2725e-05 | lb/MW | Part II | Rox_Blr_2_Test_9e | 76
Gerald Gentleman | 6077 | 1 | U1 | Lead | 4.7643e-07 | lb/MMBtu | 5.0228e-06 | lb/MW | ERT |  | 77
Eastlake | 2837 | 3 | Unit 3 | Lead | 6.3901e-07 | lb/MMBtu | 5.3473e-06 | lb/MW | ERT |  | 78
PPL Brunner Island | 3140 | 2 | U2 | Lead | 5.568e-07 | lb/MMBtu | 5.3696e-06 | lb/MW | ERT |  | 79
Gibson | 6113 | 2 | 2-2007-FGDIN | Lead | 5.6046e-07 | lb/MMBtu | 5.4639e-06 | lb/MW | ERT |  | 80
PPL Brunner Island | 3140 | 1 | U1 | Lead | 5.568e-07 | lb/MMBtu | 5.6439e-06 | lb/MW | ERT |  | 81
Cardinal | 2828 | 3 | CD-U3 | Lead | 7.0213e-07 | lb/MMBtu | 5.6981e-06 | lb/MW | ERT |  | 82
Newton | 6017 | 2 | 002 | Lead | 6.6673e-07 | lb/MMBtu | 5.9146e-06 | lb/MW | ERT |  | 83
Salem Harbor | 1626 | 1 | Unit 1 | Lead | 4.9694e-07 | lb/MMBtu | 5.9876e-06 | lb/MW | ERT |  | 84
Birchwood Power Facility | 54304 | 1A | 1A | Lead | 5.7816e-07 | lb/MMBtu | 5.9899e-06 | lb/MW | ERT |  | 85
Gallatin | 3403 | 2 | 2 | Lead | 6.5947e-07 | lb/MMBtu | 6.0451e-06 | lb/MW | ERT |  | 86
Marshall | 2727 | Unit 4 | U4 | Lead | 7.0461e-07 | lb/MMBtu | 6.0695e-06 | lb/MW | Part II | U4032707 | 87
San Juan | 2451 | Unit 4 | Unit 4 | Lead | 5.8652e-07 | lb/MMBtu | 6.0905e-06 | lb/MW | ERT |  | 88
Weston | 4078 | 3 | W3 | Lead | 6.5152e-07 | lb/MMBtu | 6.1008e-06 | lb/MW | ERT |  | 89
PPL Montour | 3149 | 1 | U1 | Lead | 6.7769e-07 | lb/MMBtu | 6.1554e-06 | lb/MW | ERT |  | 90
Mayo Electric Generating Facility | 6250 | 1A | May_Cfg_1b | Lead | 6.78e-07 | lb/MMBtu | 6.4085e-06 | lb/MW | Part II | May_Unit_1_Test_6e | 91
Mayo Electric Generating Facility | 6250 | 1B | May_Cfg_1b | Lead | 6.78e-07 | lb/MMBtu | 6.4085e-06 | lb/MW | Part II | May_Unit_1_Test_6e | 92
Hammond | 708 | 2 | Unit 2 | Lead | 6.4907e-07 | lb/MMBtu | 6.4232e-06 | lb/MW | ERT |  | 93
Hammond | 708 | 3 | Unit 3 | Lead | 6.4907e-07 | lb/MMBtu | 6.4421e-06 | lb/MW | ERT |  | 94
Comanche | 470 | 2 | Unit 2 | Lead | 6.8083e-07 | lb/MMBtu | 6.4949e-06 | lb/MW | ERT |  | 95
Hammond | 708 | 1 | Unit 1 | Lead | 6.4907e-07 | lb/MMBtu | 6.5401e-06 | lb/MW | ERT |  | 96
AES Puerto Rico Cogeneration Facility | 68029 | BLR1 | Unit_1 | Lead | 6.7876e-07 | lb/MMBtu | 6.5518e-06 | lb/MW | ERT |  | 97
Hammond | 708 | 4 | Unit 4 | Lead | 6.4907e-07 | lb/MMBtu | 6.8134e-06 | lb/MW | ERT |  | 98
Cambria Cogen | 10641 | B1 | 001 | Lead | 6.0585e-07 | lb/MMBtu | 6.924e-06 | lb/MW | ERT |  | 99
Spruance Genco, LLC | 54081 | 2A | GEN2 | Lead | 5.3829e-07 | lb/MMBtu | 7.0334e-06 | lb/MW | ERT |  | 100
Spruance Genco, LLC | 54081 | 2B | GEN2 | Lead | 5.3829e-07 | lb/MMBtu | 7.0334e-06 | lb/MW | ERT |  | 101
Herbert A. Wagner | 1554 | 2 | 002 | Lead | 7.3207e-07 | lb/MMBtu | 7.5126e-06 | lb/MW | ERT |  | 102
Silver Bay Power | 10849 | BLR1 | GEN1 | Lead | 9.211e-07 | lb/MMBtu | 7.6126e-06 | lb/MW | ERT |  | 103
Iatan | 6065 | 1 | 1 | Lead | 7.2e-07 | lb/MMBtu | 7.7355e-06 | lb/MW | Part II | LeadTestOct2009 | 104
Piney Creek Project | 54144 | BRBR1 | BRBRI | Lead | 6.2054e-07 | lb/MMBtu | 7.7568e-06 | lb/MW | Part II | 16-00127 Condition 4 & 12 | 105
Piney Creek Project | 54144 | BRBR1 | BRBRI | Lead | 1.4284e-06 | lb/MMBtu | 1.7855e-05 | lb/MW | ERT |  | 105
Whelan Energy Center Unit 1 (WEC1) | 60 | 1 | 1 | Lead | 7.7806e-07 | lb/MMBtu | 7.8653e-06 | lb/MW | ERT |  | 106
Craig | 6021 | C1 | C1 | Lead | 9.2528e-07 | lb/MMBtu | 8.1733e-06 | lb/MW | ERT |  | 107
McMeekin | 3287 | MCM2 | MCM002 | Lead | 1.0192e-06 | lb/MMBtu | 8.5032e-06 | lb/MW | ERT |  | 108
Cross | 130 | 4 | C4 | Lead | 7.8335e-07 | lb/MMBtu | 8.5204e-06 | lb/MW | ERT |  | 109
Cross | 130 | 4 | C4 | Lead | 2.0667e-06 | lb/MMBtu | 2.2479e-05 | lb/MW | Part II | C4TVICrpt2009 | 109
Cross | 130 | 4 | C4 | Lead | 4.4633e-05 | lb/MMBtu | 0.00048547 | lb/MW | Part II | C4TVIC2008 | 109
Roxboro Steam Electric Plant | 2712 | 3A | Rox_Cfg_3b | Lead | 9.39e-07 | lb/MMBtu | 8.7691e-06 | lb/MW | Part II | Rox_Unit_3_Test_7m | 110
Roxboro Steam Electric Plant | 2712 | 3B | Rox_Cfg_3b | Lead | 9.39e-07 | lb/MMBtu | 8.7691e-06 | lb/MW | Part II | Rox_Unit_3_Test_7m | 111
Roxboro Steam Electric Plant | 2712 | 4B | Rox_Cfg_4c | Lead | 9.5933e-07 | lb/MMBtu | 8.934e-06 | lb/MW | Part II | Rox_Unit_4_Test_12e | 112
Roxboro Steam Electric Plant | 2712 | 4A | Rox_Cfg_4c | Lead | 9.5933e-07 | lb/MMBtu | 8.934e-06 | lb/MW | Part II | Rox_Unit_4_Test_12e | 113
Southampton Power Station | 10774 | 2 | Unit 1 & 2 | Lead | 6.9037e-07 | lb/MMBtu | 9.0255e-06 | lb/MW | ERT |  | 114
Southampton Power Station | 10774 | 1 | Unit 1 & 2 | Lead | 6.9037e-07 | lb/MMBtu | 9.0255e-06 | lb/MW | ERT |  | 115
Hayden | 525 | 1 | Unit 1 | Lead | 9.5925e-07 | lb/MMBtu | 9.3218e-06 | lb/MW | ERT |  | 116
W H Zimmer | 6019 | 1 | 1 | Lead | 1.0471e-06 | lb/MMBtu | 9.4123e-06 | lb/MW | ERT |  | 117
East Bend Station | 6018 | 2 | 2 | Lead | 9.8002e-07 | lb/MMBtu | 9.5077e-06 | lb/MW | ERT |  | 118
Cholla | 113 | 3 | 003 | Lead | 1.0104e-06 | lb/MMBtu | 9.7028e-06 | lb/MW | ERT |  | 119
Eastlake | 2837 | 1 | Unit 1 | Lead | 1.1756e-06 | lb/MMBtu | 9.8376e-06 | lb/MW | ERT |  | 120
Nebraska City | 6096 | NC2 | NC2 | Lead | 9.7181e-07 | lb/MMBtu | 9.8609e-06 | lb/MW | ERT |  | 121
Elmer Smith Station | 1374 | 1374-2 | Unit001 | Lead | 1.1955e-06 | lb/MMBtu | 9.9164e-06 | lb/MW | ERT |  | 122
Elmer Smith Station | 1374 | 1374 | Unit001 | Lead | 1.1955e-06 | lb/MMBtu | 9.9164e-06 | lb/MW | ERT |  | 123
Hayden | 525 | 2 | Unit 2 | Lead | 1.065e-06 | lb/MMBtu | 1.0134e-05 | lb/MW | ERT |  | 124
AES Puerto Rico Cogeneration Facility | 68029 | BLR2 | Unit_2 | Lead | 1.057e-06 | lb/MMBtu | 1.0203e-05 | lb/MW | ERT |  | 125
Spruance Genco, LLC | 54081 | 1A | GEN1 | Lead | 7.8881e-07 | lb/MMBtu | 1.0307e-05 | lb/MW | ERT |  | 126
Spruance Genco, LLC | 54081 | 1B | GEN1 | Lead | 7.8881e-07 | lb/MMBtu | 1.0307e-05 | lb/MW | ERT |  | 127
San Juan | 2451 | Unit 1 | Unit 1 | Lead | 1.0505e-06 | lb/MMBtu | 1.0524e-05 | lb/MW | ERT |  | 128
Muscatine #1 | 1167 | 8 | 8 | Lead | 9.6746e-07 | lb/MMBtu | 1.0616e-05 | lb/MW | ERT |  | 129
Cambria Cogen | 10641 | B2 | 002 | Lead | 9.4512e-07 | lb/MMBtu | 1.0801e-05 | lb/MW | ERT |  | 130
New Castle Plant | 3138 | 3 | NC3-2 | Lead | 1.0528e-06 | lb/MMBtu | 1.1011e-05 | lb/MW | Part II | NC-50 | 131
Lansing | 1047 | 4 | Unit 4 | Lead | 1.11e-06 | lb/MMBtu | 1.1033e-05 | lb/MW | Part II | LANS4-Metals-20060502 | 132
Martin Drake | 492 | 5 | Unit 5 - Coal | Lead | 1.069e-06 | lb/MMBtu | 1.1078e-05 | lb/MW | ERT |  | 133
McMeekin | 3287 | MCM1 | MCM001 | Lead | 1.3181e-06 | lb/MMBtu | 1.1165e-05 | lb/MW | ERT |  | 134
Roanoke Valley II | 54755 | BLR2 | Boiler 2 | Lead | 1.0049e-06 | lb/MMBtu | 1.1255e-05 | lb/MW | ERT |  | 135
Hardin Generator Project | 55749 | PC1 | PC1 | Lead | 1.0484e-06 | lb/MMBtu | 1.1488e-05 | lb/MW | ERT |  | 136
W.H. Weatherspoon Plant | 2716 | 1 | Wea_Cfg_1 | Lead | 1.3095e-06 | lb/MMBtu | 1.1662e-05 | lb/MW | ERT |  | 137
W.H. Weatherspoon Plant | 2716 | 2 | Wea_Cfg_1 | Lead | 1.3095e-06 | lb/MMBtu | 1.1662e-05 | lb/MW | ERT |  | 138
Cross | 130 | 1 | C1 | Lead | 1.1159e-06 | lb/MMBtu | 1.1895e-05 | lb/MW | ERT |  | 139
Tanners Creek | 988 | 4 | TC-4 | Lead | 1.4723e-06 | lb/MMBtu | 1.2673e-05 | lb/MW | ERT |  | 140
Clinch River | 3775 | 1 | CR-1 | Lead | 1.4003e-06 | lb/MMBtu | 1.2791e-05 | lb/MW | ERT |  | 141
Scrubgrass Generating Company L.P. | 50974 | #2 CFB Boiler | Gen 1 | Lead | 1e-06 | lb/MMBtu | 1.2887e-05 | lb/MW | Part II | 12/13/2005 Waste Bituminous Coal Baseline Testing | 142
Scrubgrass Generating Company L.P. | 50974 | #2 CFB Boiler | Gen 1 | Lead | 3e-06 | lb/MMBtu | 3.866e-05 | lb/MW | Part II | common stack test 3-2-2005 | 142
Scrubgrass Generating Company L.P. | 50974 | #2 CFB Boiler | Gen 1 | Lead | 6.4563e-06 | lb/MMBtu | 8.32e-05 | lb/MW | ERT |  | 142
Scrubgrass Generating Company L.P. | 50974 | #1 CFB boiler | Gen 1 | Lead | 1e-06 | lb/MMBtu | 1.2887e-05 | lb/MW | Part II | 12/13/2005 Waste Bituminous Coal Baseline Testing | 143
Scrubgrass Generating Company L.P. | 50974 | #1 CFB boiler | Gen 1 | Lead | 3e-06 | lb/MMBtu | 3.866e-05 | lb/MW | Part II | common stack test 3-2-2005 | 143
Scrubgrass Generating Company L.P. | 50974 | #1 CFB boiler | Gen 1 | Lead | 6.4563e-06 | lb/MMBtu | 8.32e-05 | lb/MW | ERT |  | 143
Gibson | 6113 | 4 | 4 | Lead | 1.3776e-06 | lb/MMBtu | 1.3057e-05 | lb/MW | Part II | U4010506 | 144
R. Gallagher | 1008 | 2 | 2-2007 | Lead | 1.3928e-06 | lb/MMBtu | 1.3556e-05 | lb/MW | Part II | U2091409-BASE | 145
Conemaugh | 3118 | 2 | CON-2 | Lead | 1.4863e-06 | lb/MMBtu | 1.4268e-05 | lb/MW | Part II | C-193 | 146
Nucla | 527 | 1 | 001 | Lead | 1.5908e-06 | lb/MMBtu | 1.4925e-05 | lb/MW | ERT |  | 147
BL England | 2378 | 2 | 2 Coal w or w/o TDF | Lead | 1.5833e-06 | lb/MMBtu | 1.5142e-05 | lb/MW | Part II | CAM 238-012 | 148
BL England | 2378 | 2 | 2 Coal w or w/o TDF | Lead | 1.616e-05 | lb/MMBtu | 0.00015455 | lb/MW | Part II | CAM 238-026 | 148
State Line | 981 | 3 | Unit 3 | Lead | 1.4339e-06 | lb/MMBtu | 1.5799e-05 | lb/MW | ERT |  | 149
Spruance Genco, LLC | 54081 | 4B | GEN4 | Lead | 1.2123e-06 | lb/MMBtu | 1.5841e-05 | lb/MW | ERT |  | 150
Spruance Genco, LLC | 54081 | 4B | GEN4 | Lead | 2.452e-06 | lb/MMBtu | 3.2038e-05 | lb/MW | Part II | 2006 Emissions Testing at Boilers 4A and 4B | 150
Spruance Genco, LLC | 54081 | 4A | GEN4 | Lead | 1.2123e-06 | lb/MMBtu | 1.5841e-05 | lb/MW | ERT |  | 151
Spruance Genco, LLC | 54081 | 4A | GEN4 | Lead | 2.452e-06 | lb/MMBtu | 3.2038e-05 | lb/MW | Part II | 2006 Emissions Testing at Boilers 4A and 4B | 151
Consumers Energy - J.H. Campbell | 1710 | Unit 2 | JHC2-Conf | Lead | 1.8067e-06 | lb/MMBtu | 1.6386e-05 | lb/MW | ERT |  | 152
Consumers Energy - J.H. Campbell | 1710 | Unit 1 | JHC1-Conf | Lead | 1.8067e-06 | lb/MMBtu | 1.6887e-05 | lb/MW | ERT |  | 153
New Castle Plant | 3138 | 5 | NC5-2 | Lead | 1.76e-06 | lb/MMBtu | 1.7698e-05 | lb/MW | Part II | NC-48 | 154
Scholz | 642 | 1 | Unit 1 | Lead | 1.5356e-06 | lb/MMBtu | 1.8211e-05 | lb/MW | ERT |  | 155
Joppa Steam | 887 | 1 | 1 | Lead | 1.8556e-06 | lb/MMBtu | 1.8222e-05 | lb/MW | ERT |  | 156
Valley | 4042 | 3 | VAPP-B3 | Lead | 1.6039e-06 | lb/MMBtu | 1.9335e-05 | lb/MW | ERT |  | 157
Scholz | 642 | 2 | Unit 2 | Lead | 1.5356e-06 | lb/MMBtu | 2.0206e-05 | lb/MW | ERT |  | 158
Taconite Harbor Energy Center | 10075 | 2 | THEC2 | Lead | 1.7913e-06 | lb/MMBtu | 2.0649e-05 | lb/MW | ERT |  | 159
Sibley | 2094 | 3 | 3 | Lead | 2.1273e-06 | lb/MMBtu | 2.0787e-05 | lb/MW | ERT |  | 160
Canadys Steam | 3280 | CAN3 | CAN003 | Lead | 2.1183e-06 | lb/MMBtu | 2.0891e-05 | lb/MW | ERT |  | 161
Taconite Harbor Energy Center | 10075 | 1 | THEC1 | Lead | 2.0594e-06 | lb/MMBtu | 2.1016e-05 | lb/MW | ERT |  | 162
South Oak Creek | 4041 | 7 | OCPP-B7 | Lead | 2.4227e-06 | lb/MMBtu | 2.1622e-05 | lb/MW | ERT |  | 163
Will County | 884 | 4 | WC4CONFIG | Lead | 2.2532e-06 | lb/MMBtu | 2.1844e-05 | lb/MW | ERT |  | 164
Louisa | 6664 | 101 | 101 | Lead | 2.0583e-06 | lb/MMBtu | 2.2051e-05 | lb/MW | ERT |  | 165
Louisa | 6664 | 101 | 101 | Lead | 1.06e-05 | lb/MMBtu | 0.00011356 | lb/MW | Part II | 1/19/2010-Lead | 165
Colbert | 47 | 4 | 4 | Lead | 2.1675e-06 | lb/MMBtu | 2.2987e-05 | lb/MW | ERT |  | 166
Sibley | 2094 | 1 | 1 | Lead | 2.1273e-06 | lb/MMBtu | 2.3579e-05 | lb/MW | ERT |  | 167
Hawthorn | 2079 | 5A | 5A | Lead | 2.1791e-06 | lb/MMBtu | 2.4212e-05 | lb/MW | ERT |  | 168
Albright Power Station | 3942 | 2 | Unit_2 | Lead | 3.0663e-06 | lb/MMBtu | 2.4341e-05 | lb/MW | ERT |  | 169
Spruance Genco, LLC | 54081 | 3B | GEN3 | Lead | 1.992e-06 | lb/MMBtu | 2.6028e-05 | lb/MW | ERT |  | 170
Spruance Genco, LLC | 54081 | 3A | GEN3 | Lead | 1.992e-06 | lb/MMBtu | 2.6028e-05 | lb/MW | ERT |  | 171
Sibley | 2094 | 2 | 2 | Lead | 2.1273e-06 | lb/MMBtu | 2.6166e-05 | lb/MW | ERT |  | 172
Colbert | 47 | 3 | 3 | Lead | 2.4785e-06 | lb/MMBtu | 2.6285e-05 | lb/MW | ERT |  | 173
Conemaugh | 3118 | 1 | CON-1 | Lead | 2.8067e-06 | lb/MMBtu | 2.6942e-05 | lb/MW | Part II | C-190 | 174
Shawville | 3131 | 4 | SHAW4-2 | Lead | 2.87e-06 | lb/MMBtu | 2.7387e-05 | lb/MW | Part II | SH-184 U3-4 | 175
Shawville | 3131 | 4 | SHAW4-2 | Lead | 5.8665e-05 | lb/MMBtu | 0.00055981 | lb/MW | ERT |  | 175
Shawville | 3131 | 3 | SHAW3-2 | Lead | 2.87e-06 | lb/MMBtu | 2.7387e-05 | lb/MW | Part II | SH-184 U3-4 | 176
Shawville | 3131 | 3 | SHAW3-2 | Lead | 5.8665e-05 | lb/MMBtu | 0.00055981 | lb/MW | ERT |  | 176
Eddystone Generating Station | 3161 | 2 | Unit 2 | Lead | 3.3133e-06 | lb/MMBtu | 2.7445e-05 | lb/MW | Part II | Particulate Emissions Test - Unit 2 | 177
Eddystone Generating Station | 3161 | 2 | Unit 2 | Lead | 3.6615e-06 | lb/MMBtu | 3.0329e-05 | lb/MW | ERT |  | 177
Grant Town Power Plant | 10151 | BLR1A | GEN1 | Lead | 2.0624e-06 | lb/MMBtu | 2.9307e-05 | lb/MW | ERT |  | 178
Grant Town Power Plant | 10151 | BLR1B | GEN1 | Lead | 2.0624e-06 | lb/MMBtu | 2.9307e-05 | lb/MW | ERT |  | 179
Hennepin Power Station | 892 | Unit 1 | 001 | Lead | 2.8625e-06 | lb/MMBtu | 2.9617e-05 | lb/MW | ERT |  | 180
PANTHER CREEK ENERGY FACILITY | 50776 | BLR2 | BG2 | Lead | 2.3008e-06 | lb/MMBtu | 2.9688e-05 | lb/MW | ERT |  | 181
PANTHER CREEK ENERGY FACILITY | 50776 | BLR1 | BG1 | Lead | 2.3008e-06 | lb/MMBtu | 2.9688e-05 | lb/MW | ERT |  | 182
Martin Drake | 492 | 7 | Unit 7 - Coal | Lead | 2.868e-06 | lb/MMBtu | 3.0002e-05 | lb/MW | ERT |  | 183
PSEG Hudson Generating Station | 2403 | U2 | HUDU2E2PT2OS1-Coal | Lead | 3.0333e-06 | lb/MMBtu | 3.0347e-05 | lb/MW | Part II | EG08009 | 184
PSEG Hudson Generating Station | 2403 | U2 | HUDU2E2PT2OS1-Coal | Lead | 4.3667e-06 | lb/MMBtu | 4.3687e-05 | lb/MW | Part II | HUD2 2009 5YR ST CoNg | 184
PSEG Hudson Generating Station | 2403 | U2 | HUDU2E2PT2OS1-Coal | Lead | 4.5553e-06 | lb/MMBtu | 4.5574e-05 | lb/MW | Part II | EG07044 | 184
PSEG Hudson Generating Station | 2403 | U2 | HUDU2E2PT2OS1-Coal | Lead | 5.4601e-06 | lb/MMBtu | 5.4626e-05 | lb/MW | Part II | EG06031A | 184
Hennepin Power Station | 892 | Unit 2 | 002 | Lead | 2.8625e-06 | lb/MMBtu | 3.0582e-05 | lb/MW | ERT |  | 185
Sunbury Generation LP | 3152 | 4 | Boiler 4 | Lead | 2.9645e-06 | lb/MMBtu | 3.1498e-05 | lb/MW | ERT |  | 186
Meredosia | 864 | 5 | 005 | Lead | 2.3292e-06 | lb/MMBtu | 3.1787e-05 | lb/MW | ERT |  | 187
Ebensburg Power Company | 10603 | 031 | EPC01 | Lead | 2.27e-06 | lb/MMBtu | 3.2484e-05 | lb/MW | Part II | 2005 Emissions | 188
Ebensburg Power Company | 10603 | 031 | EPC01 | Lead | 7.2598e-06 | lb/MMBtu | 0.00010389 | lb/MW | ERT |  | 188
Mecklenburg Power Station | 52007 | BLR1 | Unit 1 & 2 | Lead | 2.8561e-06 | lb/MMBtu | 3.4462e-05 | lb/MW | ERT |  | 189
Mecklenburg Power Station | 52007 | BLR2 | Unit 1 & 2 | Lead | 2.8561e-06 | lb/MMBtu | 3.4462e-05 | lb/MW | ERT |  | 190
H L Spurlock Station | 6041 | 1 | Unit 01 | Lead | 3.3462e-06 | lb/MMBtu | 3.5417e-05 | lb/MW | ERT |  | 191
George Neal South | 7343 | 4 | 4 | Lead | 3.63e-06 | lb/MMBtu | 3.6726e-05 | lb/MW | Part II | Lead-Jan 2010 | 192
Big Stone | 6098 | 001 | 001 | Lead | 3.4555e-06 | lb/MMBtu | 3.7061e-05 | lb/MW | ERT |  | 193
Hopewell | 10771 | 10771-01 | 1 & 2 | Lead | 2.967e-06 | lb/MMBtu | 3.7306e-05 | lb/MW | ERT |  | 194
Hopewell | 10771 | 10771-02 | 1 & 2 | Lead | 2.967e-06 | lb/MMBtu | 3.7306e-05 | lb/MW | ERT |  | 195
Morgantown Energy Facility | 10743 | CFB1 | Unit 1&2 | Lead | 2.3841e-06 | lb/MMBtu | 3.7406e-05 | lb/MW | ERT |  | 196
Morgantown Energy Facility | 10743 | CFB2 | Unit 1&2 | Lead | 2.3841e-06 | lb/MMBtu | 3.7406e-05 | lb/MW | ERT |  | 197
Columbia | 8023 | 1 | Unit 1 | Lead | 3.63e-06 | lb/MMBtu | 3.745e-05 | lb/MW | Part II | COL-1-Stack-Metals-20050810 | 198
Vermilion | 897 | Unit 2 | 002 | Lead | 3.8822e-06 | lb/MMBtu | 3.7975e-05 | lb/MW | ERT |  | 199
Shawville | 3131 | 2 | SHAW2-2 | Lead | 3.63e-06 | lb/MMBtu | 3.9175e-05 | lb/MW | Part II | SH-184-U2 | 200
Burlington | 1104 | 1 | Unit 1 | Lead | 3.78e-06 | lb/MMBtu | 3.9722e-05 | lb/MW | Part II | BGS1-Metals-Stack-2006517 | 201
HB Robinson / Darlington Electric Power Plant | 3251 | 1 | Rob_Cfg_1 | Lead | 4.3432e-06 | lb/MMBtu | 4.025e-05 | lb/MW | ERT |  | 202
Waukegan | 883 | 8 | WK8CONFIG | Lead | 4.0178e-06 | lb/MMBtu | 4.1551e-05 | lb/MW | ERT |  | 203
La Cygne | 1241 | 2 | 2 | Lead | 3.7716e-06 | lb/MMBtu | 4.2396e-05 | lb/MW | ERT |  | 204
Ottumwa | 6254 | 1 | Unit 1 | Lead | 4.22e-06 | lb/MMBtu | 4.407e-05 | lb/MW | Part II | OGS1-Metals-20060615 | 205
Vermilion | 897 | Unit 1 | 001 | Lead | 3.8822e-06 | lb/MMBtu | 4.4808e-05 | lb/MW | ERT |  | 206
Colstrip | 6076 | 3 | Unit3 | Lead | 4.7694e-06 | lb/MMBtu | 4.4868e-05 | lb/MW | ERT |  | 207
Roanoke Valley I | 54035 | BLR1 | Boiler 1 | Lead | 4.8313e-06 | lb/MMBtu | 4.5128e-05 | lb/MW | ERT |  | 208
Quindaro | 1295 | 2 | Unit 2 | Lead | 3.9254e-06 | lb/MMBtu | 4.5676e-05 | lb/MW | ERT |  | 209
Cape Fear Steam Electric Plant | 2708 | 5 | Cap_Cfg_5b | Lead | 5.8286e-06 | lb/MMBtu | 4.7315e-05 | lb/MW | ERT |  | 210
Hoot Lake | 1943 | 002 | 2 | Lead | 4.1259e-06 | lb/MMBtu | 5.0789e-05 | lb/MW | ERT |  | 211
Lawrence Energy Center | 1250 | 3 | 3 | Lead | 4.5987e-06 | lb/MMBtu | 5.1141e-05 | lb/MW | ERT |  | 212
Valley | 4042 | 1 | VAPP-B1 | Lead | 4.4693e-06 | lb/MMBtu | 5.388e-05 | lb/MW | ERT |  | 213
Marion Generating Station | 976 | 123 | 123 | Lead | 5.3424e-06 | lb/MMBtu | 5.565e-05 | lb/MW | ERT |  | 214
ML Kapp | 1048 | 2 | Unit 2 | Lead | 5.68e-06 | lb/MMBtu | 5.7842e-05 | lb/MW | Part II | KAPP2-Metals-20060608 | 215
Harding Street | 990 | 60 | 60s | Lead | 6.9041e-06 | lb/MMBtu | 6.2692e-05 | lb/MW | ERT |  | 216
Cane Run | 1363 | 4 | CR4 | Lead | 4.7726e-06 | lb/MMBtu | 6.5623e-05 | lb/MW | ERT |  | 217
Joliet 9 | 874 | 5 | JOL5 CONFIG | Lead | 6.3056e-06 | lb/MMBtu | 6.9098e-05 | lb/MW | ERT |  | 218
Merrimack Station | 2364 | 2 | mk2 | Lead | 7.7833e-06 | lb/MMBtu | 6.9681e-05 | lb/MW | ERT |  | 219
Eagle Valley | 991 | 6 | 6 | Lead | 7.2803e-06 | lb/MMBtu | 7.0515e-05 | lb/MW | ERT |  | 220
Shawville | 3131 | 1 | SHAW1-2 | Lead | 6.6e-06 | lb/MMBtu | 7.1227e-05 | lb/MW | Part II | SH-184-U1 | 221
Seward | 3130 | 1 | SEW-1 | Lead | 6.9533e-06 | lb/MMBtu | 7.3693e-05 | lb/MW | ERT |  | 222
Seward | 3130 | 2 | SEW-1 | Lead | 6.9533e-06 | lb/MMBtu | 7.3693e-05 | lb/MW | ERT |  | 223
George Neal North | 1091 | 2 | 2 | Lead | 7.882e-06 | lb/MMBtu | 7.4721e-05 | lb/MW | Part II | 12/15/2008-Pb | 224
Richard Gorsuch | 7253 | 3 | UNIT3 | Lead | 7.2109e-06 | lb/MMBtu | 7.4815e-05 | lb/MW | ERT |  | 225
Harding Street | 990 | 70 | 70ss | Lead | 8.5786e-06 | lb/MMBtu | 7.6392e-05 | lb/MW | ERT |  | 226
Wabash River | 1010 | 6 | 6 | Lead | 9.3568e-06 | lb/MMBtu | 8.3693e-05 | lb/MW | ERT |  | 227
Crystal River Power Plant | 628 | 1 | CryR_Cfg_1 | Lead | 9.6333e-06 | lb/MMBtu | 9.2408e-05 | lb/MW | ERT |  | 228
Michigan City | 997 | 12 | 12 | Lead | 9.9384e-06 | lb/MMBtu | 9.3361e-05 | lb/MW | ERT |  | 229
Dale Station | 1385 | 3 | 03 | Lead | 7.9858e-06 | lb/MMBtu | 9.4233e-05 | lb/MW | ERT |  | 230
Wabash River | 1010 | 4 | 4 | Lead | 9.3568e-06 | lb/MMBtu | 9.6031e-05 | lb/MW | ERT |  | 231
Cane Run | 1363 | 5 | CR5 | Lead | 7.9696e-06 | lb/MMBtu | 9.6076e-05 | lb/MW | ERT |  | 232
Conesville | 2840 | 3 | CV-3 | Lead | 8.9236e-06 | lb/MMBtu | 0.0001007 | lb/MW | ERT |  | 233
George Neal North | 1091 | 3 | 3 | Lead | 1.112e-05 | lb/MMBtu | 0.00010515 | lb/MW | Part II | 1/20/2009-Pb | 234
Prairie Creek | 1073 | 4 | Unit 4 | Lead | 1.02e-05 | lb/MMBtu | 0.0001108 | lb/MW | Part II | PC4-Metals-20060822 | 235
James River Power Station | 2161 | 5 | Unit_5_JRPS | Lead | 1.1603e-05 | lb/MMBtu | 0.00011161 | lb/MW | ERT |  | 236
Titus | 3115 | 2 | TI-2 | Lead | 1.1583e-05 | lb/MMBtu | 0.00012094 | lb/MW | Part II | T-57 | 237
Walter Scott Jr. Energy Center | 1082 | 3 | 3 | Lead | 1.23e-05 | lb/MMBtu | 0.0001238 | lb/MW | Part II | 6/2009 PB | 238
Muscatine #1 | 1167 | 9 | 9 | Lead | 1.3733e-05 | lb/MMBtu | 0.00014375 | lb/MW | Part II | Lead Emission Test - Unit 9 | 239
Fair Station | 1218 | 2 | U2 | Lead | 1.4066e-05 | lb/MMBtu | 0.00014865 | lb/MW | ERT |  | 240
Colver Power Project | 10143 | AAB01 | AAB01 | Lead | 1.7142e-05 | lb/MMBtu | 0.00015755 | lb/MW | ERT |  | 241
H L Spurlock Station | 6041 | 3 | Unit 03 | Lead | 1.9948e-05 | lb/MMBtu | 0.00016623 | lb/MW | ERT |  | 242
George Neal North | 1091 | 1 | 1 | Lead | 1.86e-05 | lb/MMBtu | 0.00017484 | lb/MW | Part II | 1/13/2010-PB | 243
Albright Power Station | 3942 | 1 | Unit_1 | Lead | 1.8071e-05 | lb/MMBtu | 0.00017536 | lb/MW | ERT |  | 244
Riverbend | 2732 | 7 | 7 | Lead | 1.8077e-05 | lb/MMBtu | 0.0001924 | lb/MW | ERT |  | 245
Urquhart | 3295 | URQ3 | URQ003 | Lead | 2.0752e-05 | lb/MMBtu | 0.00021115 | lb/MW | ERT |  | 246
Lake Road | 2098 | 6 | 6 | Lead | 2.1752e-05 | lb/MMBtu | 0.00021533 | lb/MW | ERT |  | 247
R.M. Schahfer | 6085 | 14 | R.M.0014 | Lead | 2.2686e-05 | lb/MMBtu | 0.00022541 | lb/MW | ERT |  | 248
Elrama Power Plant | 3098 | 4 | ELR4-2 | Lead | 3.7007e-05 | lb/MMBtu | 0.00038427 | lb/MW | ERT |  | 249
Elrama Power Plant | 3098 | 3 | ELR3-2 | Lead | 3.7007e-05 | lb/MMBtu | 0.00038576 | lb/MW | ERT |  | 250
Fair Station | 1218 | 1 | U1 | Lead | 2.9e-05 | lb/MMBtu | 0.00039061 | lb/MW | Part II | MET05U1 | 251
Fair Station | 1218 | 1 | U1 | Lead | 9.6e-05 | lb/MMBtu | 0.0012931 | lb/MW | Part II | MACT06U1 | 251
Elrama Power Plant | 3098 | 2 | ELR2-2 | Lead | 3.7007e-05 | lb/MMBtu | 0.00046407 | lb/MW | ERT |  | 252
Elrama Power Plant | 3098 | 1 | ELR1-2 | Lead | 3.7007e-05 | lb/MMBtu | 0.00046407 | lb/MW | ERT |  | 253
O H Hutchings | 2848 | H-5 | H-5 | Lead | 5.72e-05 | lb/MMBtu | 0.00058199 | lb/MW | Part II | 2009 H-5 EF trail baseline metals | 254
James River Power Station | 2161 | 4 | Unit_4_JRPS | Lead | 0.0028105 | lb/MMBtu | 0.028105 | lb/MW | ERT |  | 255

## Pb_New_Sub1UPL Pooled Template
Emissions (lb/MW)
Runs | 4078 Weston Boiler 4
1 | 1.999e-05
2 | 1.5398e-05
3 | 6.3932e-06
4 | 7.9674e-07
5 | 9.1509e-07
6 | 9.7768e-07
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
Use for large sample sets and small sample sets that are Normal.
Testing Normality | Raw Data
Sample Size | 6
Kurtosis | -1.331 |  | Because only had two test averages, used the run by run data from each test. Changing m=1 to m=3.
SE Kurtosis | 1.0299
Result Kurtosis | normal
Skewness | 0.85315
SE Skewness | 0.84515
Result Skewness | normal
ni = number test runs = | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Number of sources = | 1
n =Total # test runs = | 6
5
This step is for QC only:
means | 7.4117e-06 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
7.4117e-06
Mean =
Pooled Variance = |  |  | 7.0077e-11
m= number future runs = | 3
Term1 | 0.5
Term2 | 3.5038e-11
Squared root Term2 |  | 5.9193e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | [5 empty] | 3.3649
UPL POOLED VARIANCE = |  |  |  |  | 2.733e-05 | lb/MW
[5 empty] | 0.02733 | lb/GW
|  |  |  | 3xRDL | 0.002 | lb/GW
|  |  |  | 3xRDL compared to UPL | 0.02733

## Pb_QA_Calcs
[7 empty] | Anthracite |  | Anthracite |  |  | fPM | 30B |  | μg/dscm | No |  | μg/dscm | 2.2046e-09 | lbs/μg | 0.028317 |  |  |  | cm/cf | [5 empty] | lb/hr |  |  | lb/MMBtu | [7 empty] | Round to |  |  |  | From |  | original database export===>
[7 empty] | Bituminous |  | Bituminous |  |  | Se | M5 |  | lb/dscf | Yes |  | ppm | 2.2046e-12 | lb/mg | [21 empty] | Same |  |  |  | Min |  | original database export===>
[7 empty] | Lignite |  | Lignite |  |  | Pb | M5B |  | ppm |  |  |  |  | lb/scf | [21 empty] | Sig Figs |  |  |  | Test |  | original database export===>
[7 empty] | Oil |  | Oil |  |  | Hg | M29 |  | ppm @ 3% O2 | [26 empty] | as Submitted |  |  |  | Sheet |  | original database export===>
[7 empty] | Pet Coke |  | Pet Coke |  |  | HCl | OTM27 |  | ppm @ 7% O2 | [26 empty] | prior to | [5 empty] | original database export===>
[7 empty] | Subbituminous |  | Sub Bituminous |  |  | SO2 | 26A | [28 empty] | Calc % Diff. | [5 empty] | original database export===>
[13 empty] | M6C | [34 empty] | original database export===>
original database export===>
RTI |  |  |  |  | As Submitted | [13 empty] | RTI-QA | [7 empty] | As Submitted | [9 empty] | RTI-QA | [7 empty] | Final for UPL |  | Final for UPL | original database export===> | Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | configuration_id | report_id | sampling_port_id | order | pollutant_id | pollutant_name | run_id | start_datetime | end_datetime | unit_load | fuel_flow_rate | fuel_heating_value | fg_moisture_content | fg_oxygen_content | fg_CO2_content | fg_temperature | test_method | conc | conc_units | conc_ND | conc_MDL | conc2 | conc2_units | emission_rate | emission_rate_units | emission_rate_ND | emission_rate_MDL | Calculated conc lb/dscf | 19-1 lb/MMBtu | %Diff 19-1 | 19-6 lb/MMBtu | %Diff 19-6 | emission_factor | emission_factor_units | emission_factor_ND | emission_factor_MDL | run_pollutant_comment | Fuel1 | Fuel1%Btu | Fuel2 | Fuel2%Btu | QA Comment
Comments | Use Run in UPL Calc? | Grade | Key | Facility_Name | Facility_ID | Boiler_ID | Fuel1 Used | Fuel1 Fraction | Fuel2 Used | Fuel2 Fraction | "Fuel Used/Fraction" Data Source | Pollutant | Reference Method | Concentration | Concentration UOM | Non-Detect? | MDL | MDL UOM | HAP Conversion Value to lbs | HAP Conversion UOM | Volume Conversion Value to cubic feet | Reserve | Reserve | Reserve | Volume Conversion UOM | Submitted F Factor | Bws (percent) | %O2d | %CO2d | Emission Rate Value | Emission Rate UOM | Emission Rate MDL | Emission Factor Value | Emission Factor UOM | Emission Factor MDL | MDL UOM | Fd | Fw | Fc | Calculated conc lb/dscf | 19-1 lb/MMBtu | %diff 19-1 | 19-6 lb/MMBtu | %diff 19-6 | lb/MMBtu Value Used for UPL Calcs | Unit Heat Rate (MMBtu/MWh) | lb/MWh Value Used in UPL Calcs | original database export===> | [50 empty] | average
| Yes | A | 1_Pb_T2_R1 | Weston | 4078 | W4 | Subbituminous | 100% |  |  | Part II Submittal | Pb | M29 | 2.855 | μg/dscm | No |  |  | 2.2046e-09 | lbs/μg | 0.028317 |  |  |  | cm/cf |  | 15.6 | 4.7 | 16.6 | 0.01 | lb/hr |  | 2.22e-06 | lb/MMBtu |  |  | 9820 | 0 | 1840 | 1.7823e-10 | 2.258e-06 | 1.713% | 1.9756e-06 | -11.01% | 2.22e-06 | 9.0045 | 1.999e-05 | original database export===> | 1_Pb_T2_R1 | AvgOfStackTemp | A | 2.22e-06 | pound per million British Thermal Unit (lb/MMBtu) | Yes |  | 4078 | W4 | W4 Metals 2008 | W4 Port | 6 | 23 | Lead (Pb) | 1 | 2008-07-11 07:40 | 2008-07-11 09:50 |  |  |  | 15.6 | 4.7 | 16.6 | 176.3 | 29 | 2.855 | microgram per dry standard cubic meter (μg/dscm) | FALSE |  |  |  | 0.01 | pound per hour (lb/hr) | FALSE | [6 empty] | 2.22e-06 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100 |  |  |  | 1.3927e-05
| Yes | A | 1_Pb_T2_R2 | Weston | 4078 | W4 | Subbituminous | 100% |  |  | Part II Submittal | Pb | M29 | 2.196 | μg/dscm | No |  |  | 2.2046e-09 | lbs/μg | 0.028317 |  |  |  | cm/cf |  | 15.8 | 4.7 | 14.6 | 0.01 | lb/hr |  | 1.71e-06 | lb/MMBtu |  |  | 9820 | 0 | 1840 | 1.3709e-10 | 1.7368e-06 | 1.568% | 1.7277e-06 | 1.037% | 1.71e-06 | 9.0045 | 1.5398e-05 | original database export===> | 1_Pb_T2_R2 | #REF! | A | 1.71e-06 | pound per million British Thermal Unit (lb/MMBtu) | Yes |  | 4078 | W4 | W4 Metals 2008 | W4 Port | 6 | 23 | Lead (Pb) | 2 | 2008-07-11 10:07 | 2008-07-11 12:16 |  |  |  | 15.8 | 4.7 | 14.6 | 178.1 | 29 | 2.196 | microgram per dry standard cubic meter (μg/dscm) | FALSE |  |  |  | 0.01 | pound per hour (lb/hr) | FALSE | [6 empty] | 1.71e-06 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100
| Yes | A | 1_Pb_T2_R3 | Weston | 4078 | W4 | Subbituminous | 100% |  |  | Part II Submittal | Pb | M29 | 0.916 | μg/dscm | No |  |  | 2.2046e-09 | lbs/μg | 0.028317 |  |  |  | cm/cf |  | 15.2 | 4.7 | 14.6 |  |  |  | 7.1e-07 | lb/MMBtu |  |  | 9820 | 0 | 1840 | 5.7184e-11 | 7.2446e-07 | 2.037% | 7.2068e-07 | 1.504% | 7.1e-07 | 9.0045 | 6.3932e-06 | original database export===> | 1_Pb_T2_R3 | 0 | A | 7.1e-07 | pound per million British Thermal Unit (lb/MMBtu) | Yes |  | 4078 | W4 | W4 Metals 2008 | W4 Port | 6 | 23 | Lead (Pb) | 3 | 2008-07-11 12:25 | 2008-07-11 14:35 |  |  |  | 15.2 | 4.7 | 14.6 | 178.6 | 29 | 0.916 | microgram per dry standard cubic meter (μg/dscm) | FALSE |  |  |  | 0 | pound per hour (lb/hr) | FALSE | [6 empty] | 7.1e-07 | pound per million British Thermal Unit (lb/MMBtu) | FALSE |  |  | coal - subbituminous | 100
|  |  |  | Weston |  | W4 | [6 empty] | M27 | [23 empty] | #N/A | #N/A | #N/A | [6 empty] | 9.0045 |  | original database export===> | Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | configuration_id | submittal_id | Compound | RunDate | Method | RunNumber | RunStartTime | RunEndTime | NetTravPts | Mass_TOOL | mass | units | Vmstd | Cd | Vwstd | PercH20 | PercCO2 | PercO2 | Fd | 19-1 | 19-5 | Fc | 19-6 | 19-9 | Fw | FuelType | lb/mmBtuO2 | CountOfComments | AvgOfStackTemp | AvgOfDryGasInlet | AvgOfDryGasOutlet | AvgOfOrificePresDesired | AvgOfOrificePresActual | AvgOfProbeTemp | AvgOfFilterTemp | AvgOfImpingTemp | CountOfNotes | M29 Isokinetic (+/- 10%) | OTM27 includes all fractions? | QA Comment | Questions for EPA
|  |  |  | Weston |  | W4 | [6 empty] | M28 | [23 empty] | #N/A | #N/A | #N/A | [6 empty] | 9.0045 |  | original database export===> | [20 empty] | DSCF | lb/dscf
| Yes | A | 1_Pb_T1_R1 | Weston | 4078 | W4 | Subbituminous |  |  |  | ERT | Pb | M29 | 6.8903e-12 | lb/dscf | [10 empty] | 9423 | 15.69 | 5.55 | 13.75 |  |  |  | 8.8482e-08 | lb/MMBtu |  |  | 9820 | 0 | 1840 | 6.8903e-12 | 9.2127e-08 | 4.119% | 9.2205e-08 | 4.207% | 8.8482e-08 | 9.0045 | 7.9674e-07 | original database export===> | 1_Pb_T1_R1 | 8.8403e-08 | A | 8.8482e-08 | lb/mmBtuO2 | Yes |  | 4078 | W4 | 1611 | Lead | 2010-05-11 | Method 29 | M5/29-1 | 08:30 | 15:52 | 48 | 0.00055 | 0.55 | ug | 175.820 | 6.8903e-12 | 32.72 | 15.69 | 13.75 | 5.55 | 9423 | 8.8403e-08 | 7.4532e-08 | 0 | 0 | 0 | 0 |  | 8.8482e-08 | 52 | 177.4792 | 68.5625 | 61.2083 | 1.7951 | 1.8208 | 237.125 | 249.7917 | 51.7292 | 52 | 101 |  |  |  |  | 8.965e-07
| Yes | A | 1_Pb_T1_R2 | Weston | 4078 | W4 | Subbituminous |  |  |  | ERT | Pb | M29 | 7.6247e-12 | lb/dscf | [10 empty] | 9430 | 15.73 | 6.1 | 13.4 |  |  |  | 1.0163e-07 | lb/MMBtu |  |  | 9820 | 0 | 1840 | 7.6247e-12 | 1.0573e-07 | 4.042% | 1.047e-07 | 3.021% | 1.0163e-07 | 9.0045 | 9.1509e-07 | original database export===> | 1_Pb_T1_R2 | 1.0154e-07 | A | 1.0163e-07 | lb/mmBtuO2 | Yes |  | 4078 | W4 | 1611 | Lead | 2010-05-12 | Method 29 | M5/29-2 | 08:00 | 13:30 | 48 | 0.000586 | 0.586 | ug | 169.286 | 7.6247e-12 | 31.59 | 15.73 | 13.4 | 6.1 | 9430 | 1.0154e-07 | 8.5564e-08 | 0 | 0 | 0 | 0 |  | 1.0163e-07 | 52 | 177.7292 | 68.4583 | 60.125 | 1.6702 | 1.6729 | 245.8958 | 250.3333 | 48.2083 | 52 | 100.3
| Yes | A | 1_Pb_T1_R3 | Weston | 4078 | W4 | Subbituminous |  |  |  | ERT | Pb | M29 | 8.2486e-12 | lb/dscf | [10 empty] | 9596 | 16.06 | 5.65 | 13.65 |  |  |  | 1.0858e-07 | lb/MMBtu |  |  | 9820 | 0 | 1840 | 8.2486e-12 | 1.1101e-07 | 2.242% | 1.1119e-07 | 2.407% | 1.0858e-07 | 9.0045 | 9.7768e-07 | original database export===> | 1_Pb_T1_R3 | 1.0848e-07 | A | 1.0858e-07 | lb/mmBtuO2 | Yes |  | 4078 | W4 | 1611 | Lead | 2010-05-13 | Method 29 | M5/29-3 | 07:55 | 13:15 | 48 | 0.000644 | 0.644 | ug | 171.969 | 8.2486e-12 | 32.90 | 16.06 | 13.65 | 5.65 | 9596 | 1.0848e-07 | 9.1057e-08 | 0 | 0 | 0 | 0 |  | 1.0858e-07 | 52 | 178.2292 | 72.3125 | 65.0625 | 1.7331 | 1.7375 | 249.875 | 250.0417 | 48.625 | 52 | 100.8
Conversions
1 | ppm SO2= | 1.66e-07 | lb/scf
1 | ppm Hg= | 5.1979e-07 | lb/scf
1000 | mg= | 1 | g
1000000 | ug= | 1 | g
454 | g= | 1 | lb
1 | m^3= | 35.3145 | ft^3
200.59 | Hg molecular weight
64.06 | SO2 molecular weight
Table 19-2 | Fd | Fw | Fc
Fuel Type | dscf/MMBtu | wscf/MMBtu | scf/MMBtu
Coal
Anthracite | 10100 | 10540 | 1970
Bituminous | 9780 | 10640 | 1800
Lignite | 9860 | 11950 | 1910
Oil | 9190 | 10320 | 1420
Subbituminous | 9820 |  | 1840
Note on I16: chancy: Not in ERT assumed this b/c subbit was in Part II

## ERT
Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | configuration_id | submittal_id | Compound | RunDate | Method | RunNumber | RunStartTime | RunEndTime | NetTravPts | Mass_TOOL | mass | units | Vmstd | Cd | Vwstd | PercH20 | PercCO2 | PercO2 | Fd | 19-1 | 19-5 | Fc | 19-6 | 19-9 | Fw | FuelType | lb/mmBtuO2 | CountOfComments | AvgOfStackTemp | AvgOfDryGasInlet | AvgOfDryGasOutlet | AvgOfOrificePresDesired | AvgOfOrificePresActual | AvgOfProbeTemp | AvgOfFilterTemp | AvgOfImpingTemp | CountOfNotes | M29 Isokinetic (+/- 10%) | OTM27 includes all fractions? | QA Comment | Questions for EPA
[20 empty] | DSCF | lb/dscf
1_Pb_T1_R1 | 8.8403e-08 | A | 8.8482e-08 | lb/mmBtuO2 | Yes |  | 4078 | W4 | 1611 | Lead | 2010-05-11 | Method 29 | M5/29-1 | 08:30 | 15:52 | 48 | 0.00055 | 0.55 | ug | 175.820 | 6.8903e-12 | 32.72 | 15.69 | 13.75 | 5.55 | 9423 | 8.8403e-08 | 7.4532e-08 | 0 | 0 | 0 | 0 |  | 8.8482e-08 | 52 | 177.4792 | 68.5625 | 61.2083 | 1.7951 | 1.8208 | 237.125 | 249.7917 | 51.7292 | 52 | 101
1_Pb_T1_R2 | 1.0154e-07 | A | 1.0163e-07 | lb/mmBtuO2 | Yes |  | 4078 | W4 | 1611 | Lead | 2010-05-12 | Method 29 | M5/29-2 | 08:00 | 13:30 | 48 | 0.000586 | 0.586 | ug | 169.286 | 7.6247e-12 | 31.59 | 15.73 | 13.4 | 6.1 | 9430 | 1.0154e-07 | 8.5564e-08 | 0 | 0 | 0 | 0 |  | 1.0163e-07 | 52 | 177.7292 | 68.4583 | 60.125 | 1.6702 | 1.6729 | 245.8958 | 250.3333 | 48.2083 | 52 | 100.3
1_Pb_T1_R3 | 1.0848e-07 | A | 1.0858e-07 | lb/mmBtuO2 | Yes |  | 4078 | W4 | 1611 | Lead | 2010-05-13 | Method 29 | M5/29-3 | 07:55 | 13:15 | 48 | 0.000644 | 0.644 | ug | 171.969 | 8.2486e-12 | 32.90 | 16.06 | 13.65 | 5.65 | 9596 | 1.0848e-07 | 9.1057e-08 | 0 | 0 | 0 | 0 |  | 1.0858e-07 | 52 | 178.2292 | 72.3125 | 65.0625 | 1.7331 | 1.7375 | 249.875 | 250.0417 | 48.625 | 52 | 100.8
[35 empty] | Header tab comments | [8 empty] | Point tab notes
Conversions Used
[7 empty] | 1000 | mg= | 1 | g
[7 empty] | 1000000 | ug= | 1 | g
[7 empty] | 454 | g= | 1 | lb

## 4078_PartII
Key | RTI Calculated QA lb/MMBtu | Run Grade | Submitted Value | Submitted Value UOM | Use ? | Comment | facility_id | configuration_id | report_id | sampling_port_id | order | pollutant_id | pollutant_name | run_id | start_datetime | end_datetime | unit_load | fuel_flow_rate | fuel_heating_value | fg_moisture_content | fg_oxygen_content | fg_CO2_content | fg_temperature | test_method | conc | conc_units | conc_ND | conc_MDL | conc2 | conc2_units | emission_rate | emission_rate_units | emission_rate_ND | emission_rate_MDL | Calculated conc lb/dscf | 19-1 lb/MMBtu | %Diff 19-1 | 19-6 lb/MMBtu | %Diff 19-6 | emission_factor | emission_factor_units | emission_factor_ND | emission_factor_MDL | run_pollutant_comment | Fuel1 | Fuel1%Btu | Fuel2 | Fuel2%Btu | QA Comment
1_Pb_T2_R1 | 2.2468e-06 | A | 2.22e-06 | pound per million British Thermal Unit (lb/MMBtu) | Yes |  | 4078 | W4 | W4 Metals 2008 | W4 Port | 6 | 23 | Lead (Pb) | 1 | 2008-07-11 07:40 | 2008-07-11 09:50 |  |  |  | 15.6 | 4.7 | 16.6 | 176.3 | 29 | 2.855 | microgram per dry standard cubic meter (μg/dscm) | FALSE |  |  |  | 0.01 | pound per hour (lb/hr) | FALSE | [6 empty] | 2.22e-06 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
1_Pb_T2_R2 | 1.7282e-06 | A | 1.71e-06 | pound per million British Thermal Unit (lb/MMBtu) | Yes |  | 4078 | W4 | W4 Metals 2008 | W4 Port | 6 | 23 | Lead (Pb) | 2 | 2008-07-11 10:07 | 2008-07-11 12:16 |  |  |  | 15.8 | 4.7 | 14.6 | 178.1 | 29 | 2.196 | microgram per dry standard cubic meter (μg/dscm) | FALSE |  |  |  | 0.01 | pound per hour (lb/hr) | FALSE | [6 empty] | 1.71e-06 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
1_Pb_T2_R3 | 7.2087e-07 | A | 7.1e-07 | pound per million British Thermal Unit (lb/MMBtu) | Yes |  | 4078 | W4 | W4 Metals 2008 | W4 Port | 6 | 23 | Lead (Pb) | 3 | 2008-07-11 12:25 | 2008-07-11 14:35 |  |  |  | 15.2 | 4.7 | 14.6 | 178.6 | 29 | 0.916 | microgram per dry standard cubic meter (μg/dscm) | FALSE |  |  |  | 0 | pound per hour (lb/hr) | FALSE | [6 empty] | 7.1e-07 | pound per million British Thermal Unit (lb/MMBtu) | FALSE
[7 empty] | 4078 | W4 | W4 Metals 2008 | W4 Port |  |  | Lead (Pb) | 1 | 2008-07-11 07:40 | 2008-07-11 09:50 |  |  |  | 15.6 | 4.7 | 16.6 | 176.3 | 29 | 2.855 | microgram per dry standard cubic meter (μg/dscm) | FALSE | [7 empty] | 1.7807e-10 | 2.2468e-06 | -1.208% | 1.9309e-06 | 13.02% | 2.22 | pound per trillion British Thermal Unit (lb/1012Btu) | FALSE |  |  | coal - subbituminous | 100 |  |  | lb/10^12Btu conversion
[7 empty] | 4078 | W4 | W4 Metals 2008 | W4 Port |  |  | Lead (Pb) | 2 | 2008-07-11 10:07 | 2008-07-11 12:16 |  |  |  | 15.8 | 4.7 | 14.6 | 178.1 | 29 | 2.196 | microgram per dry standard cubic meter (μg/dscm) | FALSE | [7 empty] | 1.3697e-10 | 1.7282e-06 | -1.064% | 1.6887e-06 | 1.248% | 1.71 | pound per trillion British Thermal Unit (lb/1012Btu) | FALSE |  |  | coal - subbituminous | 100 |  |  | lb/10^12Btu conversion
[7 empty] | 4078 | W4 | W4 Metals 2008 | W4 Port |  |  | Lead (Pb) | 3 | 2008-07-11 12:25 | 2008-07-11 14:35 |  |  |  | 15.2 | 4.7 | 14.6 | 178.6 | 29 | 0.916 | microgram per dry standard cubic meter (μg/dscm) | FALSE | [7 empty] | 5.7133e-11 | 7.2087e-07 | -1.531% | 7.0438e-07 | 0.7917% | 0.71 | pound per trillion British Thermal Unit (lb/1012Btu) | FALSE |  |  | coal - subbituminous | 100 |  |  | lb/10^12Btu conversion
Data from eICR. No test report provided.
Conversions
[7 empty] | 1 | ppm SO2= | 1.66e-07 | lb/scf
[7 empty] | 1 | ppm Hg= | 5.1979e-07 | lb/scf
[7 empty] | 1000 | mg= | 1 | g
[7 empty] | 1000000 | ug= | 1 | g
[7 empty] | 454 | g= | 1 | lb
[7 empty] | 1 | m^3= | 35.3145 | ft^3
[7 empty] | 200.59 | Hg molecular weight
[7 empty] | 64.06 | SO2 molecular weight
[7 empty] | Table 19-2 | Fd | Fw | Fc
[7 empty] | Fuel Type | dscf/MMBtu | wscf/MMBtu | scf/MMBtu
Coal
[7 empty] | Anthracite | 10100 | 10540 | 1970
[7 empty] | Bituminous | 9780 | 40640 | 1800
[7 empty] | Lignite | 9860 | 11950 | 1910
[7 empty] | Oil | 9190 | 10320 | 1420