## Summary_IGCC
Summary of UPLs using emission averages - IGCC Units | [16 empty] | Summary of UPLs using emission averages - IGCC Units
| Existing | [7 empty] | New | [8 empty] | Existing | [7 empty] | New
Pollutant | Mean (lb/MMBtu) | UPL (lb/MMBtu) | Number of units in the floor | Floor value |  |  |  | Is Floor = 3 x BDL? | Mean (lb/MMBtu) | UPL (lb/MMBtu) | Number of units in the floor | [6 empty] | Mean (lb/MMBtu) | UPL (lb/MMBtu) | Number of units in the floor | Floor number (lb/MMBtu) | Floor number (lb/TBtu) |  |  | Is Floor = 3 x BDL? | Mean (lb/MMBtu) | UPL (lb/MMBtu) | Number of units in the floor
Mercury | 9.1481e-07 | 2.4877e-06 | 2 | 2.4877 | 2.5 | 2.5 | lb/TBtu |  | 4.0167e-07 | 3.2407e-06 | 1 | [5 empty] | Antimony (Sb) | 1.1454e-07 | 4.2298e-07 | 2 | 1.3235e-06 | 1.4 | 1.4 | lb/TBtu | 3 x BDL | 5.265e-08 | 1.6733e-06 | 1
Total Metals | 2.3539e-05 | 5.0551e-05 | 2 | 5.0551e-05 | 6e-05 | 6e-05 | lb/MMBtu | No | 2.0188e-05 | 3.5405e-05 | 1 | [5 empty] | Arsenic (As) | 6.3633e-07 | 1.4137e-06 | 2 | 1.4137e-06 | 1.5 | 1.5 | lb/TBtu | No | 3.72e-07 | 1.3008e-06 | 1
Filterable PM | 0.010772 | 0.035195 | 2 | 0.035195 | 0.04 | 0.04 | lb/MMBtu | No | 0.001544 | 0.0074967 | 1 | [5 empty] | Beryllium (Be) | 1.1236e-08 | 2.5025e-08 | 2 | 9.6255e-08 | 0.1 | 0.1 | lb/TBtu | 3 x BDL | 6.03e-09 | 1.5059e-08 | 1
Acid gases -- HCl | 0.00018795 | 0.00044175 | 2 | 0.00044175 | 0.0005 | 0.0005 | lb/MMBtu | No | 9.2226e-05 | 0.00010888 | 1 | [5 empty] | Cadmium (Cd) | 5.9005e-08 | 1.4769e-07 | 2 | 1.4769e-07 | 0.15 | 0.15 | lb/TBtu | No | 3.3857e-08 | 1.5822e-07 | 1
[17 empty] | Chromium (Cr) | 1.2311e-06 | 2.8173e-06 | 2 | 2.8173e-06 | 2.9 | 2.9 | lb/TBtu | No | 6.8223e-07 | 3.1555e-06 | 1
[17 empty] | Cobalt (Co) | 1.3523e-07 | 1.1354e-06 | 2 | 1.1354e-06 | 1.2 | 1.2 | lb/TBtu | No | 9.0391e-08 | 3.1815e-07 | 1
[17 empty] | Lead (Pb) | 5.9758e-06 | 0.0001886 | 2 | 0.0001886 | 189 | 189 | lb/TBtu | No | 2.3467e-07 | 8.5869e-07 | 1
[17 empty] | Manganese (Mn) | 1.0094e-06 | 2.4143e-06 | 2 | 2.4143e-06 | 2.5 | 2.5 | lb/TBtu | No | 4.9209e-07 | 1.792e-06 | 1
[17 empty] | Nickel (Ni) | 2.0434e-06 | 4.9097e-06 | 2 | 6.4972e-06 | 6.5 | 6.5 | lb/TBtu | 3 x BDL | 1.42e-06 | 2.6865e-06 | 1
[17 empty] | Selenium (Se) | 1.2342e-05 | 2.1355e-05 | 2 | 2.1355e-05 | 22 | 22 | lb/TBtu | No | 1.0084e-05 | 2.995e-05 | 1
| Existing | [7 empty] | New
Pollutant | Mean (lb/MW) | UPL (lb/MW) | Number of units in the floor | Floor value |  |  |  | Is Floor = 3 x BDL? | Mean (lb/MW) | UPL (lb/MW) | Number of units in the floor | Floor value |  |  |  | Is Floor = 3 x BDL? |  | Existing | [7 empty] | New
Mercury | 9.0777e-06 | 2.4576e-05 | 2 | 2.4576e-05 | 0.03 | 0.03 | lb/GWh |  | 4.0666e-06 | 3.2809e-05 | 1 | 0.032809 | 0.04 | 0.04 | lb/GWh |  |  | Mean (lb/MW) | UPL (lb/MW) | Number of units in the floor | Floor number (lb/GWh) | Floor number (lb/GWh) |  |  |  | Mean (lb/MW) | UPL (lb/MW) | Number of units in the floor | Floor number (lb/GWh) | Floor number (lb/GWh)
Total Metals | 0.00023485 | 0.0004994 | 2 | 0.0004994 | 0.5 | 0.5 | lb/GWh | No | 0.00020439 | 0.00035845 | 1 | 0.35845 | 0.4 | 0.4 | lb/GWh | No | Antimony (Sb) | 1.1355e-06 | 4.1735e-06 | 2 | 0.013235 | 0.02 | 0.02 | lb/GWh | 3 x BDL | 5.3304e-07 | 1.6941e-05 | 1 | 0.016941 | 0.02 | 0.02 | lb/GWh | No
Filterable PM | 0.10886 | 0.35661 | 2 | 0.35661 | 0.4 | 0.4 | lb/MWh | No | 0.015233 | 0.073966 | 1 | 0.073966 | 0.08 | 0.08 | lb/MWh | No | Arsenic (As) | 6.3263e-06 | 1.3906e-05 | 2 | 0.013906 | 0.02 | 0.02 | lb/GWh | No | 3.7662e-06 | 1.3169e-05 | 1 | 0.013169 | 0.02 | 0.02 | lb/GWh | No
Acid gases -- HCl | 0.0018909 | 0.004491 | 2 | 0.004491 | 0.005 | 0.005 | lb/MWh | No | 0.00090994 | 0.0010743 | 1 | 0.0010743 | 0.002 | 0.002 | lb/MWh | No | Beryllium (Be) | 1.1164e-07 | 2.458e-07 | 2 | 0.00096255 | 0.001 | 0.001 | lb/GWh | 3 x BDL | 6.1049e-08 | 1.5247e-07 | 1 | 0.00096255 | 0.001 | 0.001 | lb/GWh | 3 x BDL
[17 empty] | Cadmium (Cd) | 5.8654e-07 | 1.4564e-06 | 2 | 0.0014564 | 0.002 | 0.002 | lb/GWh | No | 3.4277e-07 | 1.6018e-06 | 1 | 0.0016018 | 0.002 | 0.002 | lb/GWh | No
[17 empty] | Chromium (Cr) | 1.2376e-05 | 2.8575e-05 | 2 | 0.028575 | 0.03 | 0.03 | lb/GWh | No | 6.7312e-06 | 3.1134e-05 | 1 | 0.031134 | 0.04 | 0.04 | lb/GWh | No
[17 empty] | Cobalt (Co) | 1.3574e-06 | 1.1257e-05 | 2 | 0.011257 | 0.02 | 0.02 | lb/GWh | No | 8.9184e-07 | 3.139e-06 | 1 | 0.0036096 | 0.004 | 0.004 | lb/GWh | 3 x BDL
[17 empty] | Lead (Pb) | 5.8991e-05 | 0.0017941 | 2 | 1.7941 | 1.8 | 1.8 | lb/GWh | No | 2.3758e-06 | 8.6936e-06 | 1 | 0.0086936 | 0.009 | 0.009 | lb/GWh | No
[17 empty] | Manganese (Mn) | 1.0156e-05 | 2.4517e-05 | 2 | 0.024517 | 0.03 | 0.03 | lb/GWh | No | 4.8551e-06 | 1.768e-05 | 1 | 0.01768 | 0.02 | 0.02 | lb/GWh | No
[17 empty] | Nickel (Ni) | 2.0345e-05 | 4.8367e-05 | 2 | 0.064972 | 0.07 | 0.07 | lb/GWh | 3 x BDL | 1.4376e-05 | 2.7198e-05 | 1 | 0.064972 | 0.07 | 0.07 | lb/GWh | 3 x BDL
[17 empty] | Selenium (Se) | 0.00012365 | 0.00021639 | 2 | 0.21639 | 0.3 | 0.3 | lb/GWh | No | 9.9489e-05 | 0.0002955 | 1 | 0.2955 | 0.3 | 0.3 | lb/GWh | No
Calculation of 3 x RDL (lb/MMBTU) based on conversion of 3 x RDL (ug/dscm)
SynGas
E = Cd*Fc*100/(%CO2d)
Fc(syngas) = | 2313 |  | 2285 is Teco |  | 2341 is Wabash
lb/scf = | 16020000000000 | ng/scm
lb/scf = | 16020000000 | ug/scm
Corrected for 4 dscm sample volume
3xRDL, 4dscm sample volume
Method 29 Metals |  |  | ug/dscm | lb/dscf | lb/MMBtu @ 9% CO2 | lb/MW @ 9% CO2, 10 MMBtu/MW
Sb |  |  | 0.825 | 5.1498e-11 | 1.3235e-06 | 1.3235e-05
As |  |  | 0.3 | 1.8727e-11 | 4.8127e-07 | 4.8127e-06
Be |  |  | 0.06 | 3.7453e-12 | 9.6255e-08 | 9.6255e-07
Cd |  |  | 0.0225 | 1.4045e-12 | 3.6096e-08 | 3.6096e-07
Cr |  |  | 0.225 | 1.4045e-11 | 3.6096e-07 | 3.6096e-06
Co |  |  | 0.225 | 1.4045e-11 | 3.6096e-07 | 3.6096e-06
Pb |  |  | 0.225 | 1.4045e-11 | 3.6096e-07 | 3.6096e-06
Mn |  |  | 0.225 | 1.4045e-11 | 3.6096e-07 | 3.6096e-06
Ni |  |  | 4.05 | 2.5281e-10 | 6.4972e-06 | 6.4972e-05
Se |  |  | 0.6 | 3.7453e-11 | 9.6255e-07 | 9.6255e-06
Total |  |  |  |  | 1.0841e-05 | 0.00010841
fPM |  |  | 750 | 4.6816e-08 | 0.0012032 | 0.012032
HCl | Method 26a |  | 45 | 2.809e-09 | 7.2191e-05 | 0.00072191
HF | Method 26a |  | 45 | 2.809e-09 | 7.2191e-05 | 0.00072191
Note on U11: Based on a log normal UPL calculation method.
Note on U12: Based on a log normal UPL calculation method.
Note on U24: Based on a log normal UPL calculation method.
Note on U25: Based on a log normal UPL calculation method.

## Hg_avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.25e-07 | 1.4402e-06
2 | 9.78e-07 | 1.6524e-06
3 | 1.02e-07 | 1.1913e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | UPL Pooled Variance=
5
This step is for QC only:
means | 4.0167e-07 | 1.428e-06
9.1481e-07
Mean =
Pooled Variance = |  | 4.3699e-13
m= number future runs = |  | 3
Term1 |  | 0.5
Term2 |  | 2.1849e-13
Squared root Term2 |  | 4.6743e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.4877e-06

## Hg_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.25e-07 | DLL
2 | 9.78e-07
3 | 1.02e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 | UPL Pooled Variance=
2
This step is for QC only:
means | 4.0167e-07
4.0167e-07
Mean =
Pooled Variance = |  | 2.4925e-13
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.6617e-13
Squared root Term2 |  | 4.0764e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.2407e-06

## Hg_avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.2655e-06 | 1.421e-05
2 | 9.9015e-06 | 1.6303e-05
3 | 1.0327e-06 | 1.1754e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | UPL Pooled Variance=
5
This step is for QC only:
means | 4.0666e-06 | 1.4089e-05
9.0777e-06
Mean =
Pooled Variance = |  | 4.2427e-11
m= number future runs = |  | 3
Term1 |  | 0.5
Term2 |  | 2.1214e-11
Squared root Term2 |  | 4.6058e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.4576e-05

## Hg_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.2655e-06 | DLL
2 | 9.9015e-06
3 | 1.0327e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 | UPL Pooled Variance=
2
This step is for QC only:
means | 4.0666e-06
4.0666e-06
Mean =
Pooled Variance = |  | 2.5548e-11
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.7032e-11
Squared root Term2 |  | 4.127e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.2809e-05

## Mercury_IGCC
primary_fuel | ORIS code | Plant Name | physical_state | Unit Number | Unit Type | Boiler_Type | Boiler_count | Total_Capacity_MWe | Total_max_heat_input | Unit_heat_rate | Fuel_types | Fuel_Conc_lb/MMBtu | Mercury - ERT | Mercury MW - ERT | Mercury - ETTS | Mercury MW - ETTS | Mercury - CEMS | Mercury - Part II | Mercury MW - Part II | Mercury - min | Mercury - min | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
[8 empty] | MW | MMBtu/hr | Mmbtu/MWh |  | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW
Petroleum coke syngas | 1010 | Wabash River | IN | PG7221FA | IGCC | IGCC | 1 | 292 | 1709.1 | 10.1242 | Petroleum coke syngas | 9.6706e-07 |  |  | 4.0167e-07 | 4.0666e-06 |  |  |  | 4.0167e-07 | 4.0666e-06
coal gas | 7242 | Polk | FL | IGCC1 | IGCC | IGCC | 1 | 260 | 2431 | 9.8665 | coal gas | 4.2325e-06 |  |  | 1.428e-06 | 1.4089e-05 |  |  |  | 1.2333e-06 | 1.4089e-05 | PM control | PM scrubber - Syngas PM scrubbing | 35339

## Met_avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.9304e-05 | 4.4865e-05
2 | 2.3194e-05 | 2.4148e-05
3 | 1.8066e-05 | 1.1654e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 2.0188e-05 | 2.6889e-05
2.3539e-05
Mean =
Pooled Variance = |  | 1.2888e-10 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 1.5954 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | 3.3589 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 6.4441e-11
Squared root Term2 |  | 8.0275e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 5.0551e-05 | lb/MMBtu
Total | 3xRDL, 4dscm sample volume | 1.0841e-05 | lb/MMBtu
| Floor Value | 5.0551e-05 | lb/MMBtu

## Met_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.9304e-05
2 | 2.3194e-05
3 | 1.8066e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 2.0188e-05
2.0188e-05
Mean =
Pooled Variance = |  | 7.1602e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 4.7735e-12
Squared root Term2 |  | 2.1848e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.5405e-05 | lb/MMBtu
Total | 3xRDL, 4dscm sample volume | 1.0841e-05 | lb/MMBtu
| Floor Value | 3.5405e-05 | lb/MMBtu

## Met_avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 0.00019544 | 0.00044266
2 | 0.00023483 | 0.00023826
3 | 0.00018291 | 0.00011499
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 0.00020439 | 0.0002653
0.00023485
Mean =
Pooled Variance = |  | 1.2363e-08 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 1.5389 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | 3.2813 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 6.1813e-09
Squared root Term2 |  | 7.8621e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.0004994 | lb/MW
Total | 3xRDL, 4dscm sample volume | 0.00010841 | lb/MW
| Floor Value | 0.0004994 | lb/MW

## Met_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 0.00019544
2 | 0.00023483
3 | 0.00018291
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 0.00020439
0.00020439
Mean =
Pooled Variance = |  | 7.3392e-10
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 4.8928e-10
Squared root Term2 |  | 2.212e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.00035845 | lb/MW
Total | 3xRDL, 4dscm sample volume | 0.00010841 | lb/MW
| Floor Value | 0.35845 | lb/GW

## Metallic_IGCC
primary_fuel | ORIS code | Plant Name | physical_state | Unit Number | Unit Type | Boiler_type | Boiler_count | Total_Capacity_MWe | Total_max_heat_input | Boiler_heat_rate | Fuel types | Antimony_Fuel_lb/MMBtu | Antimony - ERT | Antimony MW - ERT | Antimony - Part II | Antimony MW - Part II | Antimony - min | Antimony MW - min | Arsenic_Fuel_lb/MMBtu | Arsenic - ERT | Arsenic MW - ERT | Arsenic - Part II | Arsenic MW - Part II | Arsenic - min | Arsenic MW - min | Beryllium_Fuel_lb/MMBtu | Beryllium - ERT | Beryllium MW - ERT | Beryllium - Part II | Beryllium MW - Part II | Beryllium - min | Beryllium MW - min | Cadmium_Fuel_lb/MMBtu | Cadmium - ERT | Cadmium MW - ERT | Cadmium - Part II | Cadmium MW - Part II | Cadmium - min | Cadmium MW - min | Chromium_Fuel_lb/MMBtu | Chromium - ERT | Chromium MW - ERT | Chromium - Part II | Chromium MW - Part II | Chromium - min | Chromium MW - min | Cobalt_Fuel_lb/MMBtu | Cobalt - ERT | Cobalt MW - ERT | Cobalt - Part II | Cobalt MW - Part II | Cobalt - min | Cobalt MW - min | Lead_Fuel_lb/MMBtu | Lead - ERT | Lead MW - ERT | Lead - Part II | Lead MW - Part II | Lead - min | Lead MW - min | Manganese_Fuel_lb/MMBtu | Manganese - ERT | Manganese MW - ERT | Manganese - Part II | Manganese MW - Part II | Manganese - min | Manganese MW - min | Nickel_Fuel_lb/MMBtu | Nickel - ERT | Nickel MW - ERT | Nickel - Part II | Nickel MW - Part II | Nickel - min | Nickel MW - min | Selenium_Fuel_lb/MMBtu | Selenium - ERT | Selenium MW - ERT | Selenium - Part II | Selenium MW - Part II | Selenium - min | Selenium MW - min | Total Metals -ERT | Total Metals MW -ERT | Filterable Particulate_Method 29 - ERT | Filterable Particulate_Method 29 MW - ERT | Filterable Particulate_Method 5 - ERT | Filterable Particulate_Method 5 MW - ERT | Filterable Particulate_Method 5/OTM-28 - ERT | Filterable Particulate_Method 5/OTM-28 MW - ERT | Filterable Particulate_OTM - 27/28 - ERT | Filterable Particulate_OTM - 27/28 MW - ERT | Filterable PM2_5_OTM - 27 - ERT | Filterable PM2_5_OTM - 27 MW - ERT | Filterable PM2_5_OTM - 27/28 - ERT | Filterable PM2_5_OTM - 27/28 MW - ERT | PM2_5 Condensible Particulate_Method 202 - ERT | PM2_5 Condensible Particulate_Method 202 MW - ERT | PM2_5 Condensible Particulate_Method 5/OTM-28 - ERT | PM2_5 Condensible Particulate_Method 5/OTM-28 MW - ERT | PM2_5 Condensible Particulate_OTM - 27/28 - ERT | PM2_5 Condensible Particulate_OTM - 27/28 MW - ERT | PM2_5 Condensible Particulate_OTM - 28 - ERT | PM2_5 Condensible Particulate_OTM - 28 MW - ERT | Total Particulate_Method 5/OTM-28 - ERT | Total Particulate_Method 5/OTM-28 MW - ERT | Total Particulate_OTM - 27/28 - ERT | Total Particulate_OTM - 27/28 MW - ERT | Total Particulate_OTM - 28 - ERT | Total Particulate_OTM - 28 MW - ERT | PM (Condensable) - Part II | PM (Condensable) MW - Part II | PM (Filterable and Condensable) - Part II | PM (Filterable and Condensable) MW - Part II | PM (Filterable) - Part II | PM (Filterable) MW - Part II | PM10 (Condensable) - Part II | PM10 (Condensable) MW - Part II | PM10 (Filterable and Condensable) - Part II | PM10 (Filterable and Condensable) MW - Part II | PM10 (Filterable) - Part II | PM10 (Filterable) MW - Part II | PM2_5 (Filterable) - Part II | PM2_5 (Filterable) MW - Part II | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
[8 empty] | MW | MMBtu/hr | MMBtu/MWh |  | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW
Petroleum coke syngas | 1010 | Wabash River | IN | PG7221FA | IGCC | IGCC | 1 | 292 | 1709.1 | 10.1242 | Petroleum coke syngas | 0.00020234 | 5.265e-08 | 5.3304e-07 |  |  | 5.265e-08 | 5.3304e-07 | 0.00013489 | 3.72e-07 | 3.7662e-06 |  |  | 3.72e-07 | 3.7662e-06 | 6.7446e-05 | 6.03e-09 | 6.1049e-08 |  |  | 6.03e-09 | 6.1049e-08 | 6.7446e-05 | 3.3857e-08 | 3.4277e-07 |  |  | 3.3857e-08 | 3.4277e-07 | 0.00050298 | 1.78e-06 | 1.8021e-05 |  |  | 1.78e-06 | 1.8021e-05 | 1.9073e-05 | 1.8007e-07 | 1.823e-06 |  |  | 1.8007e-07 | 1.823e-06 | 6.7446e-05 | 2.3467e-07 | 2.3758e-06 |  |  | 2.3467e-07 | 2.3758e-06 | 0.00035122 | 1.5267e-06 | 1.5456e-05 |  |  | 1.5267e-06 | 1.5456e-05 | 0.0058676 | 1.42e-06 | 1.4376e-05 |  |  | 1.42e-06 | 1.4376e-05 | 0.00013489 | 1.46e-05 | 0.00014781 |  |  | 1.46e-05 | 0.00014781 | 2.0188e-05 | 0.00020439 | 0.02 | 0.20248
coal gas | 7242 | Polk | FL | IGCC1 | IGCC | IGCC | 1 | 260 | 2431 | 9.8665 | coal gas | 7.1134e-05 | 1.558e-07 | 1.5372e-06 |  |  | 1.558e-07 | 1.5372e-06 | 0.00014938 | 9.0067e-07 | 8.8864e-06 |  |  | 9.0067e-07 | 8.8864e-06 | 7.1134e-06 | 1.6443e-08 | 1.6223e-07 |  |  | 1.6443e-08 | 1.6223e-07 | 1.4227e-05 | 8.4154e-08 | 8.303e-07 |  |  | 8.4154e-08 | 8.303e-07 | 0.00051216 | 6.8223e-07 | 6.7312e-06 |  |  | 6.8223e-07 | 6.7312e-06 | 0.00018495 | 9.0391e-08 | 8.9184e-07 |  |  | 9.0391e-08 | 8.9184e-07 | 0.00014227 | 1.1717e-05 | 0.00011561 |  |  | 1.1717e-05 | 0.00011561 | 7.1134e-06 | 4.9209e-07 | 4.8551e-06 |  |  | 4.9209e-07 | 4.8551e-06 | 0.011076 | 2.6669e-06 | 2.6313e-05 |  |  | 2.6669e-06 | 2.6313e-05 | 7.1134e-05 | 1.0084e-05 | 9.9489e-05 |  |  | 1.0084e-05 | 9.9489e-05 | 2.6889e-05 | 0.0002653 | 0.001544 | 0.015233 | [38 empty] | PM control | PM scrubber - Syngas PM scrubbing | 1996-10-01

## Sb_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.32e-08 | 3.0836e-07
2 | 9.21e-08 | 8.3234e-08
3 |  | 7.5812e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 2 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 5 | [6 empty] | UPL Pooled Variance=
4
This step is for QC only:
means | 5.265e-08 | 1.558e-07
1.1454e-07
Mean =
Pooled Variance = |  | 1.2705e-14 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 1.7865 | #DIV/0!
|  |  |  | SE Skewness | 1.0954 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | 3.7719 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2.1909 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 5 | 0 | REsult: | normal
Term1 |  | 0.53333
Term2 |  | 6.7759e-15
Squared root Term2 |  | 8.2316e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.7469
UPL POOLED VARIANCE = |  | 4.2298e-07 | lb/MMBtu
Sb | 3xRDL, 4dscm sample volume | 1.3235e-06 | lb/MMBtu
| Floor Value | 1.3235e-06 | lb/MMBtu

## Sb_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.32e-08
2 | 9.21e-08
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Number of sources = |  | 1
n =Total # test runs = |  | 2 | [13 empty] | UPL Pooled Variance=
1
This step is for QC only:
means | 5.265e-08 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
5.265e-08
Mean =
Pooled Variance = |  | 3.1126e-15
m= number future runs = |  | 3
Term1 |  | 0.83333
Term2 |  | 2.5938e-15
Squared root Term2 |  | 5.093e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 31.8205
UPL POOLED VARIANCE = |  | 1.6733e-06 | lb/MMBtu
Sb | 3xRDL, 4dscm sample volume | 1.3235e-06 | lb/MMBtu
| Floor Value | 1.6733e-06 | lb/MMBtu

## Sb_Avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.3364e-07 | 3.0424e-06
2 | 9.3244e-07 | 8.2123e-07
3 |  | 7.48e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 2 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 5 | [6 empty] | UPL Pooled Variance=
4
This step is for QC only:
means | 5.3304e-07 | 1.5372e-06
1.1355e-06
Mean =
Pooled Variance = |  | 1.2326e-12 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 1.7753 | #DIV/0!
|  |  |  | SE Skewness | 1.0954 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | 3.736 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2.1909 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 5 | 0 | REsult: | normal
Term1 |  | 0.53333
Term2 |  | 6.5736e-13
Squared root Term2 |  | 8.1078e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.7469
UPL POOLED VARIANCE = |  | 4.1735e-06 | lb/MW
Sb | 3xRDL, 4dscm sample volume | 1.3235e-05 | lb/MW
| Floor Value | 0.013235 | lb/GW

## Sb_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.3364e-07
2 | 9.3244e-07
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 2
Total Number of sources = |  | 1
n =Total # test runs = |  | 2 |  | UPL Pooled Variance=
1
This step is for QC only:
means | 5.3304e-07
5.3304e-07
Mean =
Pooled Variance = |  | 3.1904e-13
m= number future runs = |  | 3
Term1 |  | 0.83333
Term2 |  | 2.6587e-13
Squared root Term2 |  | 5.1563e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 31.8205
UPL POOLED VARIANCE = |  | 1.6941e-05 | lb/MW
Sb | 3xRDL, 4dscm sample volume | 1.3235e-05 | lb/MW
| Floor Value | 0.016941 | lb/GW

## As_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.98e-07 | 9.1432e-07
2 | 3.96e-07 | 1.0683e-06
3 | 5.22e-07 | 7.1941e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 3.72e-07 | 9.0067e-07
6.3633e-07
Mean =
Pooled Variance = |  | 1.0674e-13 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.026223 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -1.2583 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 5.3372e-14
Squared root Term2 |  | 2.3102e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 1.4137e-06 | lb/MMBtu
As | 3xRDL, 4dscm sample volume | 4.8127e-07 | lb/MMBtu
| Floor Value | 1.4137e-06 | lb/MMBtu

## As_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.98e-07
2 | 3.96e-07
3 | 5.22e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 3.72e-07
3.72e-07
Mean =
Pooled Variance = |  | 2.6676e-14
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.7784e-14
Squared root Term2 |  | 1.3336e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.3008e-06 | lb/MMBtu
As | 3xRDL, 4dscm sample volume | 4.8127e-07 | lb/MMBtu
| Floor Value | 1.3008e-06 | lb/MMBtu

## As_Avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 2.0046e-06 | 9.0211e-06
2 | 4.0092e-06 | 1.054e-05
3 | 5.2849e-06 | 7.098e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 3.7662e-06 | 8.8864e-06
6.3263e-06
Mean =
Pooled Variance = |  | 1.0149e-11 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.005216 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -1.1718 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 5.0745e-12
Squared root Term2 |  | 2.2527e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 1.3906e-05 | lb/MW
As | 3xRDL, 4dscm sample volume | 4.8127e-06 | lb/MW
| Floor Value | 0.013906 | lb/GW

## As_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 2.0046e-06
2 | 4.0092e-06
3 | 5.2849e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 3.7662e-06
3.7662e-06
Mean =
Pooled Variance = |  | 2.7343e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.8229e-12
Squared root Term2 |  | 1.3501e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.3169e-05 | lb/MW
As | 3xRDL, 4dscm sample volume | 4.8127e-06 | lb/MW
| Floor Value | 0.013169 | lb/GW

## Be_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 4.39e-09 | 1.6814e-08
2 | 7.56e-09 | 1.6385e-08
3 | 6.14e-09 | 1.613e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 6.03e-09 | 1.6443e-08
1.1236e-08
Mean =
Pooled Variance = |  | 3.3584e-17 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | -0.11691 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -2.962 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 1.6792e-17
Squared root Term2 |  | 4.0978e-09
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.5025e-08 | lb/MMBtu
Be | 3xRDL, 4dscm sample volume | 9.6255e-08 | lb/MMBtu
| Floor Value | 9.6255e-08 | lb/MMBtu

## Be_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 4.39e-09
2 | 7.56e-09
3 | 6.14e-09
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 6.03e-09
6.03e-09
Mean =
Pooled Variance = |  | 2.5213e-18
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.6809e-18
Squared root Term2 |  | 1.2965e-09
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.5059e-08 | lb/MMBtu
Be | 3xRDL, 4dscm sample volume | 9.6255e-08 | lb/MMBtu
| Floor Value | 9.6255e-08 | lb/MMBtu

## Be_Avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 4.4445e-08 | 1.6589e-07
2 | 7.6539e-08 | 1.6166e-07
3 | 6.2163e-08 | 1.5915e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 6.1049e-08 | 1.6223e-07
1.1164e-07
Mean =
Pooled Variance = |  | 3.1794e-15 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | -0.12678 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -2.9322 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 1.5897e-15
Squared root Term2 |  | 3.9871e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.458e-07 | lb/MW
Be | 3xRDL, 4dscm sample volume | 9.6255e-07 | lb/MW
| Floor Value | 0.00096255 | lb/GW

## Be_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 4.4445e-08
2 | 7.6539e-08
3 | 6.2163e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 6.1049e-08
6.1049e-08
Mean =
Pooled Variance = |  | 2.5843e-16
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.7229e-16
Squared root Term2 |  | 1.3126e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.5247e-07 | lb/MW
Be | 3xRDL, 4dscm sample volume | 9.6255e-07 | lb/MW
| Floor Value | 0.00096255 | lb/GW

## Cd_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 4.39e-08 | 1.224e-07
2 | 4.89e-08 | 6.5539e-08
3 | 8.77e-09 | 6.4521e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 3.3857e-08 | 8.4154e-08
5.9005e-08
Mean =
Pooled Variance = |  | 1.3892e-15 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.71842 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | 1.9425 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 6.9462e-16
Squared root Term2 |  | 2.6356e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 1.4769e-07 | lb/MMBtu
Cd | 3xRDL, 4dscm sample volume | 3.6096e-08 | lb/MMBtu
| Floor Value | 1.4769e-07 | lb/MMBtu

## Cd_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 4.39e-08
2 | 4.89e-08
3 | 8.77e-09
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 3.3857e-08
3.3857e-08
Mean =
Pooled Variance = |  | 4.7826e-16
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.1884e-16
Squared root Term2 |  | 1.7856e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.5822e-07 | lb/MMBtu
Cd | 3xRDL, 4dscm sample volume | 3.6096e-08 | lb/MMBtu
| Floor Value | 1.5822e-07 | lb/MMBtu

## Cd_Avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 4.4445e-07 | 1.2077e-06
2 | 4.9508e-07 | 6.4663e-07
3 | 8.879e-08 | 6.3659e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 3.4277e-07 | 8.303e-07
5.8654e-07
Mean =
Pooled Variance = |  | 1.3365e-13 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.69406 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | 2.0086 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 6.6824e-14
Squared root Term2 |  | 2.585e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 1.4564e-06 | lb/MW
Cd | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MW
| Floor Value | 0.0014564 | lb/GW

## Cd_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 4.4445e-07
2 | 4.9508e-07
3 | 8.879e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 3.4277e-07
3.4277e-07
Mean =
Pooled Variance = |  | 4.9021e-14
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.2681e-14
Squared root Term2 |  | 1.8078e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.6018e-06 | lb/MW
Cd | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MW
| Floor Value | 0.0016018 | lb/GW

## Co_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 1.3653e-07 | 5.05e-07
2 | 7.0126e-08 | 8.9e-09
3 | 6.4521e-08 | 2.63e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [8 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 9.0391e-08 | 1.8007e-07
1.3523e-07
Mean =
Pooled Variance = |  | 3.4759e-14 |  |  | Distribution of Normal Tests | Distribution of Log Tests
[9 empty] | -15.8068 | -14.4987
|  |  |  | Skewness = | 2.1583 | 0.065988 |  |  | -16.473 | -18.5372
|  |  |  | SE Skewness | 1 | 1 |  |  | -16.5563 | -17.4537
|  |  |  | Skewness Test | non-normal | normal
|  |  |  | Kurtosis = | 4.8357 | 0.35311
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | 2
|  |  |  | Kurtosis Test | non-normal | normal
|  |  |  | Number of test runs = | 6 | 6 | REsult: | log normal
Term1 |  | 0.5
Term2 |  | 1.7379e-14
Squared root Term2 |  | 1.3183e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 5.7883e-07 | lb/MMBtu
| New UPL based on log normal distribution calculation | 1.1354e-06 | lb/MMBtu
Co | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 1.1354e-06 | lb/MMBtu

## Co_New_IGCC_MMBtu
Emissions (lb/MMBtu)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 1.3653e-07
2 | 7.0126e-08
3 | 6.4521e-08
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 9.0391e-08
9.0391e-08
Mean =
Pooled Variance = |  | 1.6042e-15
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.0694e-15
Squared root Term2 |  | 3.2702e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.1815e-07 | lb/MMBtu
Co | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 3.6096e-07 | lb/MMBtu

## Co_Avg_IGCC_MW
Emissions (lb/MW)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 1.347e-06 | 5.1127e-06
2 | 6.919e-07 | 9.0106e-08
3 | 6.3659e-07 | 2.6627e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [8 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 8.9184e-07 | 1.823e-06
|  | 1.3574e-06 | [6 empty] | -13.5176 | -12.1838
Mean = | [8 empty] | -14.1838 | -16.2223
[9 empty] | -14.2671 | -15.1388
Pooled Variance = |  | 3.5724e-12 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 2.1751 | 0.10371
|  |  |  | SE Skewness | 1 | 1
|  |  |  | Skewness Test | non-normal | normal
|  |  |  | Kurtosis = | 4.9034 | 0.41047
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | 2
|  |  |  | Kurtosis Test | non-normal | normal
|  |  |  | Number of test runs = | 6 | 6 | REsult: | log normal
Term1 |  | 0.5
Term2 |  | 1.7862e-12
Squared root Term2 |  | 1.3365e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 5.8546e-06 | lb/MW
| New UPL based on log normal distribution calculation | 1.1257e-05 | lb/MW
Co | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.011257 | lb/GW

## Co_New_IGCC_MW
Emissions (lb/MW)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 1.347e-06
2 | 6.919e-07
3 | 6.3659e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 8.9184e-07
8.9184e-07
Mean =
Pooled Variance = |  | 1.5616e-13
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.0411e-13
Squared root Term2 |  | 3.2266e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.139e-06 | lb/MW
Co | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.0036096 | lb/GW

## Cr_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 1.0135e-06 | 1.63e-06
2 | 8.4348e-07 | 1.82e-06
3 | 1.8969e-07 | 1.89e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 6.8223e-07 | 1.78e-06
1.2311e-06
Mean =
Pooled Variance = |  | 4.4444e-13 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | -0.65238 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -0.8097 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 2.2222e-13
Squared root Term2 |  | 4.714e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.8173e-06 | lb/MMBtu
Cr | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 2.8173e-06 | lb/MMBtu

## Cr_New_IGCC_MMBtu
Emissions (lb/MMBtu)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 1.0135e-06
2 | 8.4348e-07
3 | 1.8969e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 6.8223e-07
6.8223e-07
Mean =
Pooled Variance = |  | 1.8917e-13
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.2612e-13
Squared root Term2 |  | 3.5513e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.1555e-06 | lb/MMBtu
Cr | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 3.1555e-06 | lb/MMBtu

## Cr_Avg_IGCC_MW
Emissions (lb/MW)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 9.9998e-06 | 1.6503e-05
2 | 8.3222e-06 | 1.8426e-05
3 | 1.8716e-06 | 1.9135e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 6.7312e-06 | 1.8021e-05
1.2376e-05
Mean =
Pooled Variance = |  | 4.6347e-11 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | -0.60733 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -0.97261 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 2.3174e-11
Squared root Term2 |  | 4.8139e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.8575e-05 | lb/MW
Cr | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.028575 | lb/GW

## Cr_New_IGCC_MW
Emissions (lb/MW)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 9.9998e-06
2 | 8.3222e-06
3 | 1.8716e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 6.7312e-06
6.7312e-06
Mean =
Pooled Variance = |  | 1.8416e-11
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 1.2277e-11
Squared root Term2 |  | 3.5039e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 3.1134e-05 | lb/MW
Cr | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.031134 | lb/GW

## Pb_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 2.2e-07 | 2.8714e-05
2 | 1.33e-07 | 4.4858e-06
3 | 3.51e-07 | 1.9514e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [8 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 2.3467e-07 | 1.1717e-05
5.9758e-06
Mean =
Pooled Variance = |  | 1.2687e-10 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 2.3344 | 0.63483 |  |  | -15.3296 | -10.4581
|  |  |  | SE Skewness | 1 | 1 |  |  | -15.8329 | -12.3146
|  |  |  | Skewness Test | non-normal | normal |  |  | -14.8625 | -13.1469
|  |  |  | Kurtosis = | 5.5288 | -0.82395
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | 2
|  |  |  | Kurtosis Test | non-normal | normal
|  |  |  | Number of test runs = | 6 | 6 | REsult: | log normal
Term1 |  | 0.5
Term2 |  | 6.3434e-11
Squared root Term2 |  | 7.9645e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 3.2776e-05 | lb/MMBtu
| New UPL based on log normal distribution calculation | 0.0001886 | lb/MMBtu
Pb | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 0.0001886 | lb/MMBtu

## Pb_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 2.2e-07
2 | 1.33e-07
3 | 3.51e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 2.3467e-07
2.3467e-07
Mean =
Pooled Variance = |  | 1.2042e-14
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 8.0282e-15
Squared root Term2 |  | 8.96e-08
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 8.5869e-07 | lb/MMBtu
Pb | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 8.5869e-07 | lb/MMBtu

## Pb_Avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 2.2273e-06 | 0.0002833
2 | 1.3465e-06 | 4.4259e-05
3 | 3.5536e-06 | 1.9254e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [8 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 2.3758e-06 | 0.00011561
5.8991e-05
Mean =
Pooled Variance = |  | 1.2346e-08 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 2.3347 | 0.64216 |  |  | -13.0147 | -8.169
|  |  |  | SE Skewness | 1 | 1 |  |  | -13.518 | -10.0255
|  |  |  | Skewness Test | non-normal | normal |  |  | -12.5475 | -10.8578
|  |  |  | Kurtosis = | 5.5301 | -0.79452
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | 2
|  |  |  | Kurtosis Test | non-normal | normal
|  |  |  | Number of test runs = | 6 | 6 | REsult: | log normal
Term1 |  | 0.5
Term2 |  | 6.173e-09
Squared root Term2 |  | 7.8569e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.00032337 | lb/MW
| New UPL based on log normal distribution calculation | 0.0017941 | lb/MW
Pb | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 1.7941 | lb/GW

## Pb_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 2.2273e-06
2 | 1.3465e-06
3 | 3.5536e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 2.3758e-06
2.3758e-06
Mean =
Pooled Variance = |  | 1.2343e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 8.229e-13
Squared root Term2 |  | 9.0714e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 8.6936e-06 | lb/MW
Pb | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.0086936 | lb/GW

## Mn_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 7.1827e-07 | 1.67e-06
2 | 2.6117e-07 | 1.42e-06
3 | 4.9681e-07 | 1.49e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 4.9209e-07 | 1.5267e-06
1.0094e-06
Mean =
Pooled Variance = |  | 3.4866e-13 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | -0.15972 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -2.4389 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 1.7433e-13
Squared root Term2 |  | 4.1753e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.4143e-06 | lb/MMBtu
Mn | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 2.4143e-06 | lb/MMBtu

## Mn_New_IGCC_MMBtu
Emissions (lb/MMBtu)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 7.1827e-07
2 | 2.6117e-07
3 | 4.9681e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 4.9209e-07
4.9209e-07
Mean =
Pooled Variance = |  | 5.2252e-14
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.4835e-14
Squared root Term2 |  | 1.8664e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.792e-06 | lb/MMBtu
Mn | 3xRDL, 4dscm sample volume | 3.6096e-07 | lb/MMBtu
| Floor Value | 1.792e-06 | lb/MMBtu

## Mn_Avg_IGCC_MW
Emissions (lb/MW)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 7.0868e-06 | 1.6907e-05
2 | 2.5768e-06 | 1.4376e-05
3 | 4.9018e-06 | 1.5085e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 4.8551e-06 | 1.5456e-05
1.0156e-05
Mean =
Pooled Variance = |  | 3.6432e-11 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | -0.14531 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -2.4867 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 1.8216e-11
Squared root Term2 |  | 4.268e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.4517e-05 | lb/MW
Mn | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.024517 | lb/GW

## Mn_New_IGCC_MW
Emissions (lb/MW)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 7.0868e-06
2 | 2.5768e-06
3 | 4.9018e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 4.8551e-06
4.8551e-06
Mean =
Pooled Variance = |  | 5.0866e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.3911e-12
Squared root Term2 |  | 1.8415e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 1.768e-05 | lb/MW
Mn | 3xRDL, 4dscm sample volume | 3.6096e-06 | lb/MW
| Floor Value | 0.01768 | lb/GW

## Ni_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.62e-06 | 3.8079e-06
2 | 1.46e-06 | 3.2946e-06
3 | 1.18e-06 | 8.9813e-07
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 1.42e-06 | 2.6669e-06
2.0434e-06
Mean =
Pooled Variance = |  | 1.4512e-12 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.86346 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -1.4075 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 7.2558e-13
Squared root Term2 |  | 8.5181e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 4.9097e-06 | lb/MMBtu
Ni | 3xRDL, 4dscm sample volume | 6.4972e-06 | lb/MMBtu
| Floor Value | 6.4972e-06 | lb/MMBtu

## Ni_New_IGCC_MMBtu
Emissions (lb/MMBtu)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.62e-06
2 | 1.46e-06
3 | 1.18e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 1.42e-06
1.42e-06
Mean =
Pooled Variance = |  | 4.96e-14
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.3067e-14
Squared root Term2 |  | 1.8184e-07
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 2.6865e-06 | lb/MMBtu
Ni | 3xRDL, 4dscm sample volume | 6.4972e-06 | lb/MMBtu
| Floor Value | 6.4972e-06 | lb/MMBtu

## Ni_Avg_IGCC_MW
Emissions (lb/MW)
| 1010 | 7242
ORIS/Facility/Unit | Wabash River | Polk
Runs | PG7221FA | IGCC1
1 | 1.6401e-05 | 3.7571e-05
2 | 1.4781e-05 | 3.2506e-05
3 | 1.1947e-05 | 8.8614e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 1.4376e-05 | 2.6313e-05
2.0345e-05
Mean =
Pooled Variance = |  | 1.3871e-10 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.83933 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -1.3931 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 6.9354e-11
Squared root Term2 |  | 8.3279e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 4.8367e-05 | lb/MW
Ni | 3xRDL, 4dscm sample volume | 6.4972e-05 | lb/MW
| Floor Value | 0.064972 | lb/GW

## Ni_New_IGCC_MW
Emissions (lb/MW)
1010
ORIS/Facility/Unit | Wabash River
Runs | PG7221FA
1 | 1.6401e-05
2 | 1.4781e-05
3 | 1.1947e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 1.4376e-05
1.4376e-05
Mean =
Pooled Variance = |  | 5.084e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 3.3893e-12
Squared root Term2 |  | 1.841e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 2.7198e-05 | lb/MW
Ni | 3xRDL, 4dscm sample volume | 6.4972e-05 | lb/MW
| Floor Value | 0.064972 | lb/GW

## Se_Avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 9.1129e-06 | 1.34e-05
2 | 1.396e-05 | 1.79e-05
3 | 7.178e-06 | 1.25e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 1.0084e-05 | 1.46e-05
1.2342e-05
Mean =
Pooled Variance = |  | 1.4349e-11 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.031932 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -0.19102 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 7.1747e-12
Squared root Term2 |  | 2.6786e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 2.1355e-05 | lb/MMBtu
Se | 3xRDL, 4dscm sample volume | 9.6255e-07 | lb/MMBtu
| Floor Value | 2.1355e-05 | lb/MMBtu

## Se_New_IGCC_MMBtu
Emissions (lb/MMBtu)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 9.1129e-06
2 | 1.396e-05
3 | 7.178e-06
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 1.0084e-05
1.0084e-05
Mean =
Pooled Variance = |  | 1.2205e-11
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 8.1364e-12
Squared root Term2 |  | 2.8524e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 2.995e-05 | lb/MMBtu
Se | 3xRDL, 4dscm sample volume | 9.6255e-07 | lb/MMBtu
| Floor Value | 2.995e-05 | lb/MMBtu

## Se_Avg_IGCC_MW
Emissions (lb/MW)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 8.9912e-05 | 0.00013566
2 | 0.00013773 | 0.00018122
3 | 7.0821e-05 | 0.00012655
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 9.9489e-05 | 0.00014781
0.00012365
Mean =
Pooled Variance = |  | 1.519e-09 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.048257 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -0.14227 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 7.595e-10
Squared root Term2 |  | 2.7559e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.00021639 | lb/MW
Se | 3xRDL, 4dscm sample volume | 9.6255e-06 | lb/MW
| Floor Value | 0.21639 | lb/GW

## Se_New_IGCC_MW
Emissions (lb/MW)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 8.9912e-05
2 | 0.00013773
3 | 7.0821e-05
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 9.9489e-05
9.9489e-05
Mean =
Pooled Variance = |  | 1.1881e-09
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 7.9206e-10
Squared root Term2 |  | 2.8144e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.0002955 | lb/MW
Se | 3xRDL, 4dscm sample volume | 9.6255e-06 | lb/MW
| Floor Value | 0.2955 | lb/GW

## PM_avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 0.0019504 | 0.0188
2 | 0.0023266 | 0.0182
3 | 0.00035487 | 0.023
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 0.001544 | 0.02
0.010772
Mean =
Pooled Variance = |  | 0.00010536 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.093301 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -2.9411 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 5.2681e-05
Squared root Term2 |  | 0.0072582
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.035195 | lb/MMBtu
fPM | 3xRDL, 4dscm sample volume | 0.0012032 | lb/MMBtu
| Floor Value | 0.035195 | lb/MMBtu

## PM_New_IGCC_MMBtu
Emissions (lb/MMBtu)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 0.0019504
2 | 0.0023266
3 | 0.00035487
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 0.001544
0.001544
Mean =
Pooled Variance = |  | 1.0958e-06
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 7.3056e-07
Squared root Term2 |  | 0.00085473
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.0074967 | lb/MMBtu
fPM | 3xRDL, 4dscm sample volume | 0.0012032 | lb/MMBtu
| Floor Value | 0.0074967 | lb/MMBtu

## PM_avg_IGCC_MW
Emissions (lb/MW)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 0.019243 | 0.19034
2 | 0.022956 | 0.18426
3 | 0.0035013 | 0.23286
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 0.015233 | 0.20249
0.10886
Mean =
Pooled Variance = |  | 0.010842 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.093807 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -2.9452 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 0.005421
Squared root Term2 |  | 0.073628
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.35661 | lb/MW
fPM | 3xRDL, 4dscm sample volume | 0.012032 | lb/MW
| Floor Value | 0.35661 | lb/MW

## PM_New_IGCC_MW
Emissions (lb/MW)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 0.019243
2 | 0.022956
3 | 0.0035013
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 0.015233
0.015233
Mean =
Pooled Variance = |  | 0.00010668
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 7.1118e-05
Squared root Term2 |  | 0.0084331
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.073966 | lb/MW
fPM | 3xRDL, 4dscm sample volume | 0.012032 | lb/MW
| Floor Value | 0.073966 | lb/MW

## PM_IGCC
primary_fuel | ORIS code | Plant Name | physical_state | Unit Number | Unit Type | Boiler_type | Boiler_count | Total_Capacity_MWe | Total_max_heat_input | Boiler_heat_rate | Fuel types | Antimony_Fuel_lb/MMBtu | Antimony - ERT | Antimony MW - ERT | Antimony - Part II | Antimony MW - Part II | Antimony - min | Antimony MW - min | Arsenic_Fuel_lb/MMBtu | Arsenic - ERT | Arsenic MW - ERT | Arsenic - Part II | Arsenic MW - Part II | Arsenic - min | Arsenic MW - min | Beryllium_Fuel_lb/MMBtu | Beryllium - ERT | Beryllium MW - ERT | Beryllium - Part II | Beryllium MW - Part II | Beryllium - min | Beryllium MW - min | Cadmium_Fuel_lb/MMBtu | Cadmium - ERT | Cadmium MW - ERT | Cadmium - Part II | Cadmium MW - Part II | Cadmium - min | Cadmium MW - min | Chromium_Fuel_lb/MMBtu | Chromium - ERT | Chromium MW - ERT | Chromium - Part II | Chromium MW - Part II | Chromium - min | Chromium MW - min | Cobalt_Fuel_lb/MMBtu | Cobalt - ERT | Cobalt MW - ERT | Cobalt - Part II | Cobalt MW - Part II | Cobalt - min | Cobalt MW - min | Lead_Fuel_lb/MMBtu | Lead - ERT | Lead MW - ERT | Lead - Part II | Lead MW - Part II | Lead - min | Lead MW - min | Manganese_Fuel_lb/MMBtu | Manganese - ERT | Manganese MW - ERT | Manganese - Part II | Manganese MW - Part II | Manganese - min | Manganese MW - min | Nickel_Fuel_lb/MMBtu | Nickel - ERT | Nickel MW - ERT | Nickel - Part II | Nickel MW - Part II | Nickel - min | Nickel MW - min | Selenium_Fuel_lb/MMBtu | Selenium - ERT | Selenium MW - ERT | Selenium - Part II | Selenium MW - Part II | Selenium - min | Selenium MW - min | Total Metals -ERT | Total Metals MW -ERT | Filterable Particulate_Method 29 - ERT | Filterable Particulate_Method 29 MW - ERT | Filterable Particulate_Method 5 - ERT | Filterable Particulate_Method 5 MW - ERT | Filterable Particulate_Method 5/OTM-28 - ERT | Filterable Particulate_Method 5/OTM-28 MW - ERT | Filterable Particulate_OTM - 27/28 - ERT | Filterable Particulate_OTM - 27/28 MW - ERT | Filterable PM2_5_OTM - 27 - ERT | Filterable PM2_5_OTM - 27 MW - ERT | Filterable PM2_5_OTM - 27/28 - ERT | Filterable PM2_5_OTM - 27/28 MW - ERT | PM2_5 Condensible Particulate_Method 202 - ERT | PM2_5 Condensible Particulate_Method 202 MW - ERT | PM2_5 Condensible Particulate_Method 5/OTM-28 - ERT | PM2_5 Condensible Particulate_Method 5/OTM-28 MW - ERT | PM2_5 Condensible Particulate_OTM - 27/28 - ERT | PM2_5 Condensible Particulate_OTM - 27/28 MW - ERT | PM2_5 Condensible Particulate_OTM - 28 - ERT | PM2_5 Condensible Particulate_OTM - 28 MW - ERT | Total Particulate_Method 5/OTM-28 - ERT | Total Particulate_Method 5/OTM-28 MW - ERT | Total Particulate_OTM - 27/28 - ERT | Total Particulate_OTM - 27/28 MW - ERT | Total Particulate_OTM - 28 - ERT | Total Particulate_OTM - 28 MW - ERT | PM (Condensable) - Part II | PM (Condensable) MW - Part II | PM (Filterable and Condensable) - Part II | PM (Filterable and Condensable) MW - Part II | PM (Filterable) - Part II | PM (Filterable) MW - Part II | PM10 (Condensable) - Part II | PM10 (Condensable) MW - Part II | PM10 (Filterable and Condensable) - Part II | PM10 (Filterable and Condensable) MW - Part II | PM10 (Filterable) - Part II | PM10 (Filterable) MW - Part II | PM2_5 (Filterable) - Part II | PM2_5 (Filterable) MW - Part II | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
[8 empty] | MW | MMBtu/hr | MMBtu/MWh |  | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW
Petroleum coke syngas | 1010 | Wabash River | IN | PG7221FA | IGCC | IGCC | 1 | 292 | 1709.1 | 10.1242 | Petroleum coke syngas | 0.00020234 | 5.265e-08 | 5.3304e-07 |  |  | 5.265e-08 | 5.3304e-07 | 0.00013489 | 3.72e-07 | 3.7662e-06 |  |  | 3.72e-07 | 3.7662e-06 | 6.7446e-05 | 6.03e-09 | 6.1049e-08 |  |  | 6.03e-09 | 6.1049e-08 | 6.7446e-05 | 3.3857e-08 | 3.4277e-07 |  |  | 3.3857e-08 | 3.4277e-07 | 0.00050298 | 1.78e-06 | 1.8021e-05 |  |  | 1.78e-06 | 1.8021e-05 | 1.9073e-05 | 1.8007e-07 | 1.823e-06 |  |  | 1.8007e-07 | 1.823e-06 | 6.7446e-05 | 2.3467e-07 | 2.3758e-06 |  |  | 2.3467e-07 | 2.3758e-06 | 0.00035122 | 1.5267e-06 | 1.5456e-05 |  |  | 1.5267e-06 | 1.5456e-05 | 0.0058676 | 1.42e-06 | 1.4376e-05 |  |  | 1.42e-06 | 1.4376e-05 | 0.00013489 | 1.46e-05 | 0.00014781 |  |  | 1.46e-05 | 0.00014781 | 2.0188e-05 | 0.00020439 | 0.02 | 0.20248
coal gas | 7242 | Polk | FL | IGCC1 | IGCC | IGCC | 1 | 260 | 2431 | 9.8665 | coal gas | 7.1134e-05 | 1.558e-07 | 1.5372e-06 |  |  | 1.558e-07 | 1.5372e-06 | 0.00014938 | 9.0067e-07 | 8.8864e-06 |  |  | 9.0067e-07 | 8.8864e-06 | 7.1134e-06 | 1.6443e-08 | 1.6223e-07 |  |  | 1.6443e-08 | 1.6223e-07 | 1.4227e-05 | 8.4154e-08 | 8.303e-07 |  |  | 8.4154e-08 | 8.303e-07 | 0.00051216 | 6.8223e-07 | 6.7312e-06 |  |  | 6.8223e-07 | 6.7312e-06 | 0.00018495 | 9.0391e-08 | 8.9184e-07 |  |  | 9.0391e-08 | 8.9184e-07 | 0.00014227 | 1.1717e-05 | 0.00011561 |  |  | 1.1717e-05 | 0.00011561 | 7.1134e-06 | 4.9209e-07 | 4.8551e-06 |  |  | 4.9209e-07 | 4.8551e-06 | 0.011076 | 2.6669e-06 | 2.6313e-05 |  |  | 2.6669e-06 | 2.6313e-05 | 7.1134e-05 | 1.0084e-05 | 9.9489e-05 |  |  | 1.0084e-05 | 9.9489e-05 | 2.6889e-05 | 0.0002653 | 0.001544 | 0.015233 | [38 empty] | PM control | PM scrubber - Syngas PM scrubbing | 1996-10-01

## Acid_Gas_avg_IGCC_MMBtu
Emissions (lb/MMBtu)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 8.966e-05 | 0.000294
2 | 9.1598e-05 | 0.000308
3 | 9.5418e-05 | 0.000249
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 9.2226e-05 | 0.00028367
0.00018795
Mean =
Pooled Variance = |  | 1.1378e-08 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.12723 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -3.001 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 5.6892e-09
Squared root Term2 |  | 7.5427e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.00044175 | lb/MMBtu
HCl | 3xRDL, 4dscm sample volume | 7.2191e-05 | lb/MMBtu
| Floor Value | 0.00044175 | lb/MMBtu

## Acid_Gas_New_IGCC_MMBtu
Emissions (lb/MMBtu)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 8.966e-05 | BDL
2 | 9.1598e-05 | BDL
3 | 9.5418e-05 | BDL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 9.2226e-05
9.2226e-05
Mean =
Pooled Variance = |  | 8.5822e-12
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 5.7215e-12
Squared root Term2 |  | 2.392e-06
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.00010888 | lb/MMBtu
HCl | 3xRDL, 4dscm sample volume | 7.2191e-05 | lb/MMBtu
| Floor Value | 0.00010888 | lb/MMBtu

## Acid_Gas_avg_IGCC_MW
Emissions (lb/MW)
| 7242 | 1010
ORIS/Facility/Unit | Polk | Wabash River
Runs | IGCC1 | PG7221FA
1 | 0.00088463 | 0.0029765
2 | 0.00090375 | 0.0031183
3 | 0.00094144 | 0.0025209
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3 | 3
Total Number of sources = |  | 2
n =Total # test runs = |  | 6 | [6 empty] | UPL Pooled Variance=
5
This step is for QC only:
means | 0.00090994 | 0.0028719
0.0018909
Mean =
Pooled Variance = |  | 1.1941e-06 |  |  | Distribution of Normal Tests | Distribution of Log Tests
|  |  |  | Skewness = | 0.12445 | #DIV/0!
|  |  |  | SE Skewness | 1 | #DIV/0!
|  |  |  | Skewness Test | normal | #DIV/0!
|  |  |  | Kurtosis = | -3.0082 | #DIV/0!
m= number future runs = |  | 3 |  | SE Kurtosis | 2 | #DIV/0!
|  |  |  | Kurtosis Test | normal | #DIV/0!
|  |  |  | Number of test runs = | 6 | 0 | REsult: | normal
Term1 |  | 0.5
Term2 |  | 5.9705e-07
Squared root Term2 |  | 0.00077269
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 3.3649
UPL POOLED VARIANCE = |  | 0.004491 | lb/MW
HCl | 3xRDL, 4dscm sample volume | 0.00072191 | lb/MW
| Floor Value | 0.004491 | lb/MW

## Acid_Gas_New_IGCC_MW
Emissions (lb/MW)
7242
ORIS/Facility/Unit | Polk
Runs | IGCC1
1 | 0.00088463 | BDL
2 | 0.00090375 | BDL
3 | 0.00094144 | BDL
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
ni = number test runs = | 3
Total Number of sources = |  | 1
n =Total # test runs = |  | 3 |  | UPL Pooled Variance=
2
This step is for QC only:
means | 0.00090994
0.00090994
Mean =
Pooled Variance = |  | 8.3546e-10
m= number future runs = |  | 3
Term1 |  | 0.66667
Term2 |  | 5.5697e-10
Squared root Term2 |  | 2.36e-05
NOTE: the pvalue for the t-statistic is calculated as: 2*alpha, where 1-alpha is desired confidence, so if 99% confidence is desired then alpha=0.01 and 2*alpha=2*(0.01)
t-statistic | = quantile t-distribution with df degrees of freedom at .99 confidence level = | 6.9646
UPL POOLED VARIANCE = |  | 0.0010743 | lb/MW
HCl | 3xRDL, 4dscm sample volume | 0.00072191 | lb/MW
| Floor Value | 0.0010743 | lb/MW

## Acid_Gas_IGCC
primary_fuel | ORIS code | Plant Name | physical_state | Unit Number | Unit Type | Boiler_type | Boiler_count | Total_Capacity_MWe | Total_max_heat_input | Unit_heat_rate | Fuel types | Fuel_Cl_lb/MMBtu | Fuel_F_lb/MMBtu | Chlorine - ERT | Chlorine MW - ERT | Chlorine - ETTS | Chlorine MW - ETTS | Chlorine - Part II | Chlorine MW - Part II | Chlorine - min | Chlorine MW - min | HCN - ERT | HCN MW - ERT | HCN - ETTS | HCN MW - ETTS | HCN - Part II | HCN MW - Part II | HCN - min | HCN MW - min | Hydrogen Chloride - ERT | Hydrogen Chloride MW - ERT | Hydrogen Chloride - ETTS | Hydrogen Chloride MW - ETTS | Hydrogen Chloride - Part II | Hydrogen Chloride MW - Part II | Hydrogen Chloride - min | Hydrogen Chloride MW - min | Hydrogen Fluoride - ERT | Hydrogen Fluoride MW - ERT | Hydrogen Fluoride - ETTS | Hydrogen Fluoride MW - ETTS | Hydrogen Fluoride - Part II | Hydrogen Fluoride MW - Part II | Hydrogen Fluoride - min | Hydrogen Fluoride MW - min | Sulfur Dioxide - CEMS | Sulfur Dioxide MW - CEMS | Sulfur Dioxide - ERT | Sulfur Dioxide MW - ERT | Sulfur Dioxide - ETTS | Sulfur Dioxide MW - ETTS | Sulfur Dioxide - Part II | Sulfur Dioxide MW - Part II | Sulfur Dioxide - min | Sulfur Dioxide MW - min | control_group_1 | control_type_1 | install_date_1 | control_group_2 | control_type_2 | install_date_2 | control_group_3 | control_type_3 | install_date_3 | control_group_4 | control_type_4 | install_date_4 | control_group_5 | control_type_5 | install_date_5 | control_group_6 | control_type_6 | install_date_6 | control_group_7 | control_type_7 | install_date_7 | control_group_8 | control_type_8 | install_date_8 | control_group_9 | control_type_9 | install_date_9 | control_group_10 | control_type_10 | install_date_10 | control_group_11 | control_type_11 | install_date_11 | control_group_12 | control_type_12 | install_date_12
[8 empty] | MW | MMBtu/hr | Mmbtu/MWh |  | lb/MMBtu | lb/MMBtu | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW | lb/MMBtu | lb/MW
Petroleum coke syngas | 1010 | Wabash River | IN | PG7221FA | IGCC | IGCC | 1 | 292 | 1709.1 | 10.1242 | Petroleum coke syngas | 0.015795 | 0.00067736 | [16 empty] | 0.00028367 | 0.0028719 |  |  |  |  | 0.00028367 | 0.0028719
coal gas | 7242 | Polk | FL | IGCC1 | IGCC | IGCC | 1 | 260 | 2431 | 9.8665 | coal gas | 0.016361 | 0.0071134 | [16 empty] | 9.2226e-05 | 0.00090994 |  |  |  |  | 9.2226e-05 | 0.00090994 | [18 empty] | PM control | PM scrubber - Syngas PM scrubbing | 1996-10-01