## Equations
Size | acfm
25MW | 76400
50MW | 152800
70MW | 213920
150 MW | 458400
370 MW | 1130720
700 MW | 2139200
Costing equations
| Capital cost, 1999$ | Annual cost, 1999 $/y | Energy usage, kWh/y | Solid waste generation, tons/y | [17 empty] | fraction of unit operated at 70 % instead of 80 %
[5 empty] | MW | Capital, $ | MW | Annual, $/y | MW | Energy, KWh | MW | Solid waste, tons/yr-MW | MW | Capital, $ | MW | Annual, $/y | MW | Energy, KWh | MW | Solid waste, tons/yr-MW |  | capital |  | annual |  | power |  | solid waste
[5 empty] | 25 | 195087.3871 | 25 | 30656.5807 | 25 | 24688.6667 | 25 | 0.16254 | 25 | 291844.8179 | 25 | 44081.1007 | 25 | 28872.6667 | 25 | 0.16254 |  | 0.66846 | 1 | 0.69546 | 1 | 0.85509 | 1 | 1
[5 empty] | 50 | 112539.9034 | 50 | 18455.2104 | 50 | 24689 | 50 | 0.16254 | 50 | 166618.2598 | 50 | 26105.3504 | 50 | 28873 | 50 | 0.16254 |  | 0.67544 | 1 | 0.70695 | 1 | 0.85509 | 1 | 1
<500 MW | -162853Ln(x) + 813007 | -23373Ln(x) + 118878 | 28873 | 0.163 | 70 | 87525.26 | 70 | 14765.336 | 70 | 24689.0476 | 70 | 0.16254 | 70 | 127391.8191 | 70 | 20479.3535 | 70 | 28873.0952 | 70 | 0.16254 |  | 0.68706 | 1 | 0.72099 | 1 | 0.85509 | 1 | 1
150 MW | -24890Ln(x) + 204138 | -3538.9Ln(x) + 31394 | 28873 | 0.163 | 150 | 52287.3574 | 150 | 9594.2516 | 150 | 24689 | 150 | 0.16254 | 150 | 80601.1509 | 150 | 13829.125 | 150 | 28872.8889 | 150 | 0.16254 |  | 0.64872 | 1 | 0.69377 | 1 | 0.85509 | 1 | 1
370 MW |  |  |  |  | 370 | 35383.0274 | 370 | 7133.548 | 370 | 24689.009 | 370 | 0.16254 | 370 | 54110.8551 | 370 | 10063.2939 | 370 | 28872.973 | 370 | 0.16254 |  | 0.6539 | 1 | 0.70887 | 1 | 0.85509 | 1 | 1
700 MW |  |  |  |  | 700 | 27732.1787 | 700 | 6026.5796 | 700 | 24688.9524 | 700 | 0.16254 | 700 | 42749.2563 | 700 | 8447.1039 | 700 | 28872.9286 | 700 | 0.16254 |  | 0.64872 | 1 | 0.71345 | 1 | 0.85509 | 1 | 1
[21 empty] | ave | 0.66371 |  | 0.70658 | 1 | 0.85509 | 1 | 1

## ESP oil 700
ELECTROSTATIC PRECIPITATORS
Case | Oil - 700 MW | [5 empty] | 700
You supply data for boxed cells, see OAQPS Control Cost Manual
SIZING PROCEDURE |  |  | Flat Plate Design
| ESP Type |  |  | 2 | (Flat Plate =2, Plate-Wire=1)
| Design Efficiency (E) |  |  | 0.8
| Penetration (p) |  |  | 0.2
| Temperature (Tk) |  |  | 413
| Resistivity (ohm-cm) |  |  | 2000000000
| MMD(i) |  |  | 3.5
| Sneakage (Sn) |  |  | 0.1
| Rapping Reentrainment(RR) |  |  | 0.124
| MMD(p) |  |  | 2
| MMD(r) |  |  | 3
| Loss Factor (LF) |  |  | 0.2116
| E(bd) |  |  | 318193.5206 | (V/m)
| n (eta) |  |  | 2.3077e-05 | (Kg/md)
| e(0) |  |  | 8.845e-12 | (F/m)
| E(avg) |  |  | 252534.5402
| Number of Sections (n) |  |  | 2
| Average Section Penetration (Ps) |  |  | 0.44721
| Collection Penetration (Pc) |  |  | 0.29885
| Particle Size Change Factor (D) |  |  | 0.44721
| MMD(rp) |  |  | 0.52491
| Computed MMD(n) |  | 1 | 3.5
|  |  | 2 | 2.9436
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Computed SCA |  | 1 | 12.7061
|  |  | 2 | 15.1079
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Total SCA |  |  | 27.814
| Total ESCA |  |  | 141.2949
EXHAUST VOLUME (acfm) |  |  | 2139200 | acfm | Annual Dust Loading
Total Collection Area (sq. ft.) |  |  | 302258.0285 | sq. ft. | 0.1 | grains/cu. ft.
Annual Hours of Operations |  |  | 7446
COSTING PROCEDURE
Prices include: ESP casing, pyramidal hoppers, rigid electrodes and
internal collecting plates, transformer-rectifier sets and microprocessor controls,
rappers and stub-supports. (Options include inlet/outler nozzles and
diffusion plates, hopper auxiliaries and level detectors, weather enclosure
and stair access, structural supports, and 3 in. of fiberglass insulation
encased in a metal skin. Costs also include auxiliary equipment.)
"Your year" dollars are based on the Chemical Engineering cost index value you
specify below. The base year value (mid 1987) is 320, which should be entered if
you do not have a cost index value. In this case you should not use "your year"
values for direct annual costs and should not enter 1 in the second line of the box
below.
"CRF" is a capital recovery factor calculated as described in Chapter 2 of the
OAQPS Control Cost Manual and based on interest rate and equipment lifetime.
Supply the following data to be used in the costing procedure:
Chemical Engineering cost index value for
| your year (enter base year value of 320 if no other value) |  |  |  |  | 394.3
| If using your year dollar values for direct annual costs, enter 1 |  |  |  |  | 1
| Operating labor hourly cost without overheads ($12/hr base year) |  |  |  |  | 17.26
| Cost of electricity ($0.06/kWh for base year) |  |  |  |  | 0.06
| Tipping fee for waste disposal ($20/ton for base year) |  |  |  |  | 50
| Fractional interest rate for capital (0.07 for base year) |  |  |  |  | 0.07
| Equipment lifetime (20 years for base case) |  |  |  |  | 20
| Additional auxiliary costs, base year (1987) |  |  |  |  | 0
| Retrofit factor (1.2 to 1.5 typical, use 1 for new installation) |  |  |  |  | 1.4
Capital Cost Factors for ESPs
Direct Costs in base year dollars
Purchased Equipment Costs
| ESP + auxiliary equipment |  |  |  | 6303659.4
| Auxiliary equipment |  |  |  | 2801626.4
| ESP |  |  |  | 3502033 |  | 11.5862 | $/ft2 plate area, 1987 $, ESP only
| Instrumentation (0.1 x EC) |  |  |  | 630366 |  | 5.0029 | $/kW, 1987 $, ESP only
| Sales taxes (0.03 x EC) |  |  |  | 189110
| Freight (0.05 x EC) |  |  |  | 315183
|  | Purchased equipment cost, PEC |  |  | 7438318.4
Direct installation costs in base year dollars
| Foundations & supports (0.04 x PEC) |  |  |  | 297533
| Handling & erection ().5 x PEC) |  |  |  | 3719159
| Electrical (0.08 x PEC) |  |  |  | 595065
| Piping (0.01 x PEC) |  |  |  | 74383
| Insulation for ductwork (0.02 x PEC) |  |  |  | 148766
| Painting (0.02 x PEC) |  |  |  | 148766
|  | Direct installation costs |  |  | 4983672
Site preparation
Buildings
|  | Total Direct Costs, DC |  |  | 7013388
Indirect Costs (installation, in base year dollars)
| Engineering (0.2 x PEC) |  |  |  | 1487664
| Construction and field expenses (0.2 x PEC) |  |  |  | 1487664
| Contractor fees (0.1 x PEC) |  |  |  | 743832
| Start-up (0.01 x PEC) |  |  |  | 74383
| Performance test (0.01 x PEC |  |  |  | 74383
| Model study (0.02 x PEC) |  |  |  | 148766
| Contingencies (0.03 x PEC) |  |  |  | 223150
|  | Total Indirect Costs, IC |  |  | 4239842
| Total Capital Investment (TCI= (DC + IC) x retrofit) |  |  |  | 15754522
| TCI in your year dollars |  |  |  |  | 19412525.0769 | 9.0747 | $/acfm
[7 empty] | 27.7322 | $/kW
Annual Costs For ESP Systems | [6 empty] | 27732.1787 | $/MW
Direct Annual Costs, DC
Operating labor
| Operator (3 hrs/day x labor cost ) |  |  |  | 16064.745
| Supervisor (15 % of operator) |  |  |  | 2410
| Coordinator (1/3 of operator) |  |  |  | 5355
Operating materials
Maintenance
| Labor (based on collector area) |  |  |  | 30726
| Materials (1% of PEC) |  |  |  | 74383
Utilities
| Electricity - fan |  |  |  | 774965 | 24688.9524 | kWh/y-MW
(0.000181 x flue x pres. drp. x hrs x power cost)
| Electricity - operating |  |  |  | 261971
(0.00194 x col. area x hrs x power cost)
| Waste disposal |  | 2 | mile haul | 348499 | 0.16254 | tons/y-MW
(tipping fee + $0.50/ton-mi)
|  | Total DC, | your year dollars |  | 1514373.745
Indirect Annual Costs, IC
| Overhead (60% of labor & maint. materials) |  |  |  | 95326
| Administrative charges (0.02 x TCI) |  |  |  | 388251
| Property tax (0.01 x TCI) |  |  |  | 194125
| Insurance (0.01 x TCI) |  |  |  | 194125
| Capital recovery (CRF x TCI)* |  |  |  | 1832405
|  | Total IC , | your year dollars |  | 2704232
| Total Annual Cost, |  | your year dollars |  | 4218605.745 |  | 9.2029 | $/acfm
[7 empty] | 6.0266 | $/kW
[7 empty] | 6026.5796 | $/MW
0.5 | 0.75 | 0.9 | 0.95 | 0.99 | 0.995 | 0.999
308802 | 378309 | 416839 | 517794 | 673798 | 589425 | 680192

## ESP oil 370
ELECTROSTATIC PRECIPITATORS
Case | Oil - 370 MW | [5 empty] | 370
You supply data for boxed cells, see OAQPS Control Cost Manual
SIZING PROCEDURE |  |  | Flat Plate Design
| ESP Type |  |  | 2 | (Flat Plate =2, Plate-Wire=1)
| Design Efficiency (E) |  |  | 0.8
| Penetration (p) |  |  | 0.2
| Temperature (Tk) |  |  | 413
| Resistivity (ohm-cm) |  |  | 2000000000
| MMD(i) |  |  | 3.5
| Sneakage (Sn) |  |  | 0.1
| Rapping Reentrainment(RR) |  |  | 0.124
| MMD(p) |  |  | 2
| MMD(r) |  |  | 3
| Loss Factor (LF) |  |  | 0.2116
| E(bd) |  |  | 318193.5206 | (V/m)
| n (eta) |  |  | 2.3077e-05 | (Kg/md)
| e(0) |  |  | 8.845e-12 | (F/m)
| E(avg) |  |  | 252534.5402
| Number of Sections (n) |  |  | 2
| Average Section Penetration (Ps) |  |  | 0.44721
| Collection Penetration (Pc) |  |  | 0.29885
| Particle Size Change Factor (D) |  |  | 0.44721
| MMD(rp) |  |  | 0.52491
| Computed MMD(n) |  | 1 | 3.5
|  |  | 2 | 2.9436
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Computed SCA |  | 1 | 12.7061
|  |  | 2 | 15.1079
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Total SCA |  |  | 27.814
| Total ESCA |  |  | 141.2949
EXHAUST VOLUME (acfm) |  |  | 1130720 | acfm | Annual Dust Loading
Total Collection Area (sq. ft.) |  |  | 159764.9579 | sq. ft. | 0.1 | grains/cu. ft.
Annual Hours of Operations |  |  | 7446
COSTING PROCEDURE
Prices include: ESP casing, pyramidal hoppers, rigid electrodes and
internal collecting plates, transformer-rectifier sets and microprocessor controls,
rappers and stub-supports. (Options include inlet/outler nozzles and
diffusion plates, hopper auxiliaries and level detectors, weather enclosure
and stair access, structural supports, and 3 in. of fiberglass insulation
encased in a metal skin. Costs also include auxiliary equipment.)
"Your year" dollars are based on the Chemical Engineering cost index value you
specify below. The base year value (mid 1987) is 320, which should be entered if
you do not have a cost index value. In this case you should not use "your year"
values for direct annual costs and should not enter 1 in the second line of the box
below.
"CRF" is a capital recovery factor calculated as described in Chapter 2 of the
OAQPS Control Cost Manual and based on interest rate and equipment lifetime.
Supply the following data to be used in the costing procedure:
Chemical Engineering cost index value for
| your year (enter base year value of 320 if no other value) |  |  |  |  | 394.3
| If using your year dollar values for direct annual costs, enter 1 |  |  |  |  | 1
| Operating labor hourly cost without overheads ($12/hr base year) |  |  |  |  | 17.26
| Cost of electricity ($0.06/kWh for base year) |  |  |  |  | 0.06
| Tipping fee for waste disposal ($20/ton for base year) |  |  |  |  | 50
| Fractional interest rate for capital (0.07 for base year) |  |  |  |  | 0.07
| Equipment lifetime (20 years for base case) |  |  |  |  | 20
| Additional auxiliary costs, base year (1987) |  |  |  |  | 0
| Retrofit factor (1.2 to 1.5 typical, use 1 for new installation) |  |  |  |  | 1.4
Capital Cost Factors for ESPs
Direct Costs in base year dollars
Purchased Equipment Costs
| ESP + auxiliary equipment |  |  |  | 3799488.6
| Auxiliary equipment |  |  |  | 1688661.6
| ESP |  |  |  | 2110827 |  | 13.2121 | $/ft2 plate area, 1987 $, ESP only
| Instrumentation (0.1 x EC) |  |  |  | 379949 |  | 5.7049 | $/kW, 1987 $, ESP only
| Sales taxes (0.03 x EC) |  |  |  | 113985
| Freight (0.05 x EC) |  |  |  | 189974
|  | Purchased equipment cost, PEC |  |  | 4483396.6
Direct installation costs in base year dollars
| Foundations & supports (0.04 x PEC) |  |  |  | 179336
| Handling & erection ().5 x PEC) |  |  |  | 2241698
| Electrical (0.08 x PEC) |  |  |  | 358672
| Piping (0.01 x PEC) |  |  |  | 44834
| Insulation for ductwork (0.02 x PEC) |  |  |  | 89668
| Painting (0.02 x PEC) |  |  |  | 89668
|  | Direct installation costs |  |  | 3003876
Site preparation
Buildings
|  | Total Direct Costs, DC |  |  | 5033592
Indirect Costs (installation, in base year dollars)
| Engineering (0.2 x PEC) |  |  |  | 896679
| Construction and field expenses (0.2 x PEC) |  |  |  | 896679
| Contractor fees (0.1 x PEC) |  |  |  | 448340
| Start-up (0.01 x PEC) |  |  |  | 44834
| Performance test (0.01 x PEC |  |  |  | 44834
| Model study (0.02 x PEC) |  |  |  | 89668
| Contingencies (0.03 x PEC) |  |  |  | 134502
|  | Total Indirect Costs, IC |  |  | 2555536
| Total Capital Investment (TCI= (DC + IC) x retrofit) |  |  |  | 10624779.2
| TCI in your year dollars |  |  |  |  | 13091720.1205 | 11.5782 | $/acfm
[7 empty] | 35.383 | $/kW
Annual Costs For ESP Systems | [6 empty] | 35383.0274 | $/MW
Direct Annual Costs, DC
Operating labor
| Operator (3 hrs/day x labor cost ) |  |  |  | 16064.745
| Supervisor (15 % of operator) |  |  |  | 2410
| Coordinator (1/3 of operator) |  |  |  | 5355
Operating materials
Maintenance
| Labor (based on collector area) |  |  |  | 16241
| Materials (1% of PEC) |  |  |  | 44834
Utilities
| Electricity - fan |  |  |  | 409625 | 24689.009 | kWh/y-MW
(0.000181 x flue x pres. drp. x hrs x power cost)
| Electricity - operating |  |  |  | 138471
(0.00194 x col. area x hrs x power cost)
| Waste disposal |  | 2 | mile haul | 184207 | 0.16254 | tons/y-MW
(tipping fee + $0.50/ton-mi)
|  | Total DC, | your year dollars |  | 817207.745
Indirect Annual Costs, IC
| Overhead (60% of labor & maint. materials) |  |  |  | 62771
| Administrative charges (0.02 x TCI) |  |  |  | 261834
| Property tax (0.01 x TCI) |  |  |  | 130917
| Insurance (0.01 x TCI) |  |  |  | 130917
| Capital recovery (CRF x TCI)* |  |  |  | 1235766
|  | Total IC , | your year dollars |  | 1822205
| Total Annual Cost, |  | your year dollars |  | 2639412.745 |  | 5.7579 | $/acfm
[7 empty] | 7.1335 | $/kW
[7 empty] | 7133.548 | $/MW
0.5 | 0.75 | 0.9 | 0.95 | 0.99 | 0.995 | 0.999
308802 | 378309 | 416839 | 517794 | 673798 | 589425 | 680192

## ESP oil 150
ELECTROSTATIC PRECIPITATORS
Case | Oil - 150 MW | [5 empty] | 150
You supply data for boxed cells, see OAQPS Control Cost Manual
SIZING PROCEDURE |  |  | Flat Plate Design
| ESP Type |  |  | 2 | (Flat Plate =2, Plate-Wire=1)
| Design Efficiency (E) |  |  | 0.8
| Penetration (p) |  |  | 0.2
| Temperature (Tk) |  |  | 413
| Resistivity (ohm-cm) |  |  | 2000000000
| MMD(i) |  |  | 3.5
| Sneakage (Sn) |  |  | 0.1
| Rapping Reentrainment(RR) |  |  | 0.124
| MMD(p) |  |  | 2
| MMD(r) |  |  | 3
| Loss Factor (LF) |  |  | 0.2116
| E(bd) |  |  | 318193.5206 | (V/m)
| n (eta) |  |  | 2.3077e-05 | (Kg/md)
| e(0) |  |  | 8.845e-12 | (F/m)
| E(avg) |  |  | 252534.5402
| Number of Sections (n) |  |  | 2
| Average Section Penetration (Ps) |  |  | 0.44721
| Collection Penetration (Pc) |  |  | 0.29885
| Particle Size Change Factor (D) |  |  | 0.44721
| MMD(rp) |  |  | 0.52491
| Computed MMD(n) |  | 1 | 3.5
|  |  | 2 | 2.9436
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Computed SCA |  | 1 | 12.7061
|  |  | 2 | 15.1079
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Total SCA |  |  | 27.814
| Total ESCA |  |  | 141.2949
EXHAUST VOLUME (acfm) |  |  | 458400 | acfm | Annual Dust Loading
Total Collection Area (sq. ft.) |  |  | 64769.5775 | sq. ft. | 0.1 | grains/cu. ft.
Annual Hours of Operations |  |  | 7446
COSTING PROCEDURE
Prices include: ESP casing, pyramidal hoppers, rigid electrodes and
internal collecting plates, transformer-rectifier sets and microprocessor controls,
rappers and stub-supports. (Options include inlet/outler nozzles and
diffusion plates, hopper auxiliaries and level detectors, weather enclosure
and stair access, structural supports, and 3 in. of fiberglass insulation
encased in a metal skin. Costs also include auxiliary equipment.)
"Your year" dollars are based on the Chemical Engineering cost index value you
specify below. The base year value (mid 1987) is 320, which should be entered if
you do not have a cost index value. In this case you should not use "your year"
values for direct annual costs and should not enter 1 in the second line of the box
below.
"CRF" is a capital recovery factor calculated as described in Chapter 2 of the
OAQPS Control Cost Manual and based on interest rate and equipment lifetime.
Supply the following data to be used in the costing procedure:
Chemical Engineering cost index value for
| your year (enter base year value of 320 if no other value) |  |  |  |  | 394.3
| If using your year dollar values for direct annual costs, enter 1 |  |  |  |  | 1
| Operating labor hourly cost without overheads ($12/hr base year) |  |  |  |  | 17.26
| Cost of electricity ($0.06/kWh for base year) |  |  |  |  | 0.06
| Tipping fee for waste disposal ($20/ton for base year) |  |  |  |  | 50
| Fractional interest rate for capital (0.07 for base year) |  |  |  |  | 0.07
| Equipment lifetime (20 years for base case) |  |  |  |  | 20
| Additional auxiliary costs, base year (1987) |  |  |  |  | 0
| Retrofit factor (1.2 to 1.5 typical, use 1 for new installation) |  |  |  |  | 1.4
Capital Cost Factors for ESPs
Direct Costs in base year dollars
Purchased Equipment Costs
| ESP + auxiliary equipment |  |  |  | 1720098
| Auxiliary equipment |  |  |  | 764488
| ESP |  |  |  | 955610 |  | 14.754 | $/ft2 plate area, 1987 $, ESP only
| Instrumentation (0.1 x EC) |  |  |  | 172010 |  | 6.3707 | $/kW, 1987 $, ESP only
| Sales taxes (0.03 x EC) |  |  |  | 51603
| Freight (0.05 x EC) |  |  |  | 86005
|  | Purchased equipment cost, PEC |  |  | 2029716
Direct installation costs in base year dollars
| Foundations & supports (0.04 x PEC) |  |  |  | 81189
| Handling & erection ().5 x PEC) |  |  |  | 1014858
| Electrical (0.08 x PEC) |  |  |  | 162377
| Piping (0.01 x PEC) |  |  |  | 20297
| Insulation for ductwork (0.02 x PEC) |  |  |  | 40594
| Painting (0.02 x PEC) |  |  |  | 40594
|  | Direct installation costs |  |  | 1359909
Site preparation
Buildings
|  | Total Direct Costs, DC |  |  | 3389625
Indirect Costs (installation, in base year dollars)
| Engineering (0.2 x PEC) |  |  |  | 405943
| Construction and field expenses (0.2 x PEC) |  |  |  | 405943
| Contractor fees (0.1 x PEC) |  |  |  | 202972
| Start-up (0.01 x PEC) |  |  |  | 20297
| Performance test (0.01 x PEC |  |  |  | 20297
| Model study (0.02 x PEC) |  |  |  | 40594
| Contingencies (0.03 x PEC) |  |  |  | 60891
|  | Total Indirect Costs, IC |  |  | 1156937
| Total Capital Investment (TCI= (DC + IC) x retrofit) |  |  |  | 6365186.8
| TCI in your year dollars |  |  |  |  | 7843103.6101 | 17.1097 | $/acfm
[7 empty] | 52.2874 | $/kW
Annual Costs For ESP Systems | [6 empty] | 52287.3574 | $/MW
Direct Annual Costs, DC
Operating labor
| Operator (3 hrs/day x labor cost ) |  |  |  | 16064.745
| Supervisor (15 % of operator) |  |  |  | 2410
| Coordinator (1/3 of operator) |  |  |  | 5355
Operating materials
Maintenance
| Labor (based on collector area) |  |  |  | 6584
| Materials (1% of PEC) |  |  |  | 20297
Utilities
| Electricity - fan |  |  |  | 166064 | 24689 | kWh/y-MW
(0.000181 x flue x pres. drp. x hrs x power cost)
| Electricity - operating |  |  |  | 56137
(0.00194 x col. area x hrs x power cost)
| Waste disposal |  | 2 | mile haul | 74678 | 0.16254 | tons/y-MW
(tipping fee + $0.50/ton-mi)
|  | Total DC, | your year dollars |  | 347589.745
Indirect Annual Costs, IC
| Overhead (60% of labor & maint. materials) |  |  |  | 37491
| Administrative charges (0.02 x TCI) |  |  |  | 156862
| Property tax (0.01 x TCI) |  |  |  | 78431
| Insurance (0.01 x TCI) |  |  |  | 78431
| Capital recovery (CRF x TCI)* |  |  |  | 740333
|  | Total IC , | your year dollars |  | 1091548
| Total Annual Cost, |  | your year dollars |  | 1439137.745 |  | 3.1395 | $/acfm
[7 empty] | 9.5943 | $/kW
[7 empty] | 9594.2516 | $/MW
0.5 | 0.75 | 0.9 | 0.95 | 0.99 | 0.995 | 0.999
308802 | 378309 | 416839 | 517794 | 673798 | 589425 | 680192

## ESP oil 70
ELECTROSTATIC PRECIPITATORS
Case | Oil - 70 MW | [5 empty] | 70
You supply data for boxed cells, see OAQPS Control Cost Manual
SIZING PROCEDURE |  |  | Flat Plate Design
| ESP Type |  |  | 2 | (Flat Plate =2, Plate-Wire=1)
| Design Efficiency (E) |  |  | 0.8
| Penetration (p) |  |  | 0.2
| Temperature (Tk) |  |  | 413
| Resistivity (ohm-cm) |  |  | 2000000000
| MMD(i) |  |  | 3.5
| Sneakage (Sn) |  |  | 0.1
| Rapping Reentrainment(RR) |  |  | 0.124
| MMD(p) |  |  | 2
| MMD(r) |  |  | 3
| Loss Factor (LF) |  |  | 0.2116
| E(bd) |  |  | 318193.5206 | (V/m)
| n (eta) |  |  | 2.3077e-05 | (Kg/md)
| e(0) |  |  | 8.845e-12 | (F/m)
| E(avg) |  |  | 252534.5402
| Number of Sections (n) |  |  | 2
| Average Section Penetration (Ps) |  |  | 0.44721
| Collection Penetration (Pc) |  |  | 0.29885
| Particle Size Change Factor (D) |  |  | 0.44721
| MMD(rp) |  |  | 0.52491
| Computed MMD(n) |  | 1 | 3.5
|  |  | 2 | 2.9436
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Computed SCA |  | 1 | 12.7061
|  |  | 2 | 15.1079
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Total SCA |  |  | 27.814
| Total ESCA |  |  | 141.2949
EXHAUST VOLUME (acfm) |  |  | 213920 | acfm | Annual Dust Loading
Total Collection Area (sq. ft.) |  |  | 30225.8028 | sq. ft. | 0.1 | grains/cu. ft.
Annual Hours of Operations |  |  | 7446
COSTING PROCEDURE
Prices include: ESP casing, pyramidal hoppers, rigid electrodes and
internal collecting plates, transformer-rectifier sets and microprocessor controls,
rappers and stub-supports. (Options include inlet/outler nozzles and
diffusion plates, hopper auxiliaries and level detectors, weather enclosure
and stair access, structural supports, and 3 in. of fiberglass insulation
encased in a metal skin. Costs also include auxiliary equipment.)
"Your year" dollars are based on the Chemical Engineering cost index value you
specify below. The base year value (mid 1987) is 320, which should be entered if
you do not have a cost index value. In this case you should not use "your year"
values for direct annual costs and should not enter 1 in the second line of the box
below.
"CRF" is a capital recovery factor calculated as described in Chapter 2 of the
OAQPS Control Cost Manual and based on interest rate and equipment lifetime.
Supply the following data to be used in the costing procedure:
Chemical Engineering cost index value for
| your year (enter base year value of 320 if no other value) |  |  |  |  | 394.3
| If using your year dollar values for direct annual costs, enter 1 |  |  |  |  | 1
| Operating labor hourly cost without overheads ($12/hr base year) |  |  |  |  | 17.26
| Cost of electricity ($0.06/kWh for base year) |  |  |  |  | 0.06
| Tipping fee for waste disposal ($20/ton for base year) |  |  |  |  | 50
| Fractional interest rate for capital (0.07 for base year) |  |  |  |  | 0.07
| Equipment lifetime (20 years for base case) |  |  |  |  | 20
| Additional auxiliary costs, base year (1987) |  |  |  |  | 0
| Retrofit factor (1.2 to 1.5 typical, use 1 for new installation) |  |  |  |  | 1.4
Capital Cost Factors for ESPs
Direct Costs in base year dollars
Purchased Equipment Costs
| ESP + auxiliary equipment |  |  |  | 1040121
| Auxiliary equipment |  |  |  | 462276
| ESP |  |  |  | 577845 |  | 19.1176 | $/ft2 plate area, 1987 $, ESP only
| Instrumentation (0.1 x EC) |  |  |  | 104012 |  | 8.2549 | $/kW, 1987 $, ESP only
| Sales taxes (0.03 x EC) |  |  |  | 31204
| Freight (0.05 x EC) |  |  |  | 52006
|  | Purchased equipment cost, PEC |  |  | 1227343
Direct installation costs in base year dollars
| Foundations & supports (0.04 x PEC) |  |  |  | 49094
| Handling & erection ().5 x PEC) |  |  |  | 613672
| Electrical (0.08 x PEC) |  |  |  | 98187
| Piping (0.01 x PEC) |  |  |  | 12273
| Insulation for ductwork (0.02 x PEC) |  |  |  | 24547
| Painting (0.02 x PEC) |  |  |  | 24547
|  | Direct installation costs |  |  | 822320
Site preparation
Buildings
|  | Total Direct Costs, DC |  |  | 2852036
Indirect Costs (installation, in base year dollars)
| Engineering (0.2 x PEC) |  |  |  | 245469
| Construction and field expenses (0.2 x PEC) |  |  |  | 245469
| Contractor fees (0.1 x PEC) |  |  |  | 122734
| Start-up (0.01 x PEC) |  |  |  | 12273
| Performance test (0.01 x PEC |  |  |  | 12273
| Model study (0.02 x PEC) |  |  |  | 24547
| Contingencies (0.03 x PEC) |  |  |  | 36820
|  | Total Indirect Costs, IC |  |  | 699585
| Total Capital Investment (TCI= (DC + IC) x retrofit) |  |  |  | 4972269.4
| TCI in your year dollars |  |  |  |  | 6126768.2013 | 28.6405 | $/acfm
[7 empty] | 87.5253 | $/kW
Annual Costs For ESP Systems | [6 empty] | 87525.26 | $/MW
Direct Annual Costs, DC
Operating labor
| Operator (3 hrs/day x labor cost ) |  |  |  | 16064.745
| Supervisor (15 % of operator) |  |  |  | 2410
| Coordinator (1/3 of operator) |  |  |  | 5355
Operating materials
Maintenance
| Labor (based on collector area) |  |  |  | 5082.7734
| Materials (1% of PEC) |  |  |  | 12273
Utilities
| Electricity - fan |  |  |  | 77497 | 24689.0476 | kWh/y-MW
(0.000181 x flue x pres. drp. x hrs x power cost)
| Electricity - operating |  |  |  | 26197
(0.00194 x col. area x hrs x power cost)
| Waste disposal |  | 2 | mile haul | 34850 | 0.16254 | tons/y-MW
(tipping fee + $0.50/ton-mi)
|  | Total DC, | your year dollars |  | 179729.5184
Indirect Annual Costs, IC
| Overhead (60% of labor & maint. materials) |  |  |  | 30449
| Administrative charges (0.02 x TCI) |  |  |  | 122535
| Property tax (0.01 x TCI) |  |  |  | 61268
| Insurance (0.01 x TCI) |  |  |  | 61268
| Capital recovery (CRF x TCI)* |  |  |  | 578324
|  | Total IC , | your year dollars |  | 853844
| Total Annual Cost, |  | your year dollars |  | 1033573.5184 |  | 2.2547 | $/acfm
[7 empty] | 14.7653 | $/kW
[7 empty] | 14765.336 | $/MW
0.5 | 0.75 | 0.9 | 0.95 | 0.99 | 0.995 | 0.999
308802 | 378309 | 416839 | 517794 | 673798 | 589425 | 680192

## ESP oil 50
ELECTROSTATIC PRECIPITATORS
Case | Oil - 50 MW | [5 empty] | 50
You supply data for boxed cells, see OAQPS Control Cost Manual
SIZING PROCEDURE |  |  | Flat Plate Design
| ESP Type |  |  | 2 | (Flat Plate =2, Plate-Wire=1)
| Design Efficiency (E) |  |  | 0.8
| Penetration (p) |  |  | 0.2
| Temperature (Tk) |  |  | 413
| Resistivity (ohm-cm) |  |  | 2000000000
| MMD(i) |  |  | 3.5
| Sneakage (Sn) |  |  | 0.1
| Rapping Reentrainment(RR) |  |  | 0.124
| MMD(p) |  |  | 2
| MMD(r) |  |  | 3
| Loss Factor (LF) |  |  | 0.2116
| E(bd) |  |  | 318193.5206 | (V/m)
| n (eta) |  |  | 2.3077e-05 | (Kg/md)
| e(0) |  |  | 8.845e-12 | (F/m)
| E(avg) |  |  | 252534.5402
| Number of Sections (n) |  |  | 2
| Average Section Penetration (Ps) |  |  | 0.44721
| Collection Penetration (Pc) |  |  | 0.29885
| Particle Size Change Factor (D) |  |  | 0.44721
| MMD(rp) |  |  | 0.52491
| Computed MMD(n) |  | 1 | 3.5
|  |  | 2 | 2.9436
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Computed SCA |  | 1 | 12.7061
|  |  | 2 | 15.1079
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Total SCA |  |  | 27.814
| Total ESCA |  |  | 141.2949
EXHAUST VOLUME (acfm) |  |  | 152800 | acfm | Annual Dust Loading
Total Collection Area (sq. ft.) |  |  | 21589.8592 | sq. ft. | 0.1 | grains/cu. ft.
Annual Hours of Operations |  |  | 7446
COSTING PROCEDURE
Prices include: ESP casing, pyramidal hoppers, rigid electrodes and
internal collecting plates, transformer-rectifier sets and microprocessor controls,
rappers and stub-supports. (Options include inlet/outler nozzles and
diffusion plates, hopper auxiliaries and level detectors, weather enclosure
and stair access, structural supports, and 3 in. of fiberglass insulation
encased in a metal skin. Costs also include auxiliary equipment.)
"Your year" dollars are based on the Chemical Engineering cost index value you
specify below. The base year value (mid 1987) is 320, which should be entered if
you do not have a cost index value. In this case you should not use "your year"
values for direct annual costs and should not enter 1 in the second line of the box
below.
"CRF" is a capital recovery factor calculated as described in Chapter 2 of the
OAQPS Control Cost Manual and based on interest rate and equipment lifetime.
Supply the following data to be used in the costing procedure:
Chemical Engineering cost index value for
| your year (enter base year value of 320 if no other value) |  |  |  |  | 394.3
| If using your year dollar values for direct annual costs, enter 1 |  |  |  |  | 1
| Operating labor hourly cost without overheads ($12/hr base year) |  |  |  |  | 17.26
| Cost of electricity ($0.06/kWh for base year) |  |  |  |  | 0.06
| Tipping fee for waste disposal ($20/ton for base year) |  |  |  |  | 50
| Fractional interest rate for capital (0.07 for base year) |  |  |  |  | 0.07
| Equipment lifetime (20 years for base case) |  |  |  |  | 20
| Additional auxiliary costs, base year (1987) |  |  |  |  | 0
| Retrofit factor (1.2 to 1.5 typical, use 1 for new installation) |  |  |  |  | 1.4
Capital Cost Factors for ESPs
Direct Costs in base year dollars
Purchased Equipment Costs
| ESP + auxiliary equipment |  |  |  | 842121
| Auxiliary equipment |  |  |  | 374276
| ESP |  |  |  | 467845 |  | 21.6697 | $/ft2 plate area, 1987 $, ESP only
| Instrumentation (0.1 x EC) |  |  |  | 84212 |  | 9.3569 | $/kW, 1987 $, ESP only
| Sales taxes (0.03 x EC) |  |  |  | 25264
| Freight (0.05 x EC) |  |  |  | 42106
|  | Purchased equipment cost, PEC |  |  | 993703
Direct installation costs in base year dollars
| Foundations & supports (0.04 x PEC) |  |  |  | 39748
| Handling & erection ().5 x PEC) |  |  |  | 496852
| Electrical (0.08 x PEC) |  |  |  | 79496
| Piping (0.01 x PEC) |  |  |  | 9937
| Insulation for ductwork (0.02 x PEC) |  |  |  | 19874
| Painting (0.02 x PEC) |  |  |  | 19874
|  | Direct installation costs |  |  | 665781
Site preparation
Buildings
|  | Total Direct Costs, DC |  |  | 2695497
Indirect Costs (installation, in base year dollars)
| Engineering (0.2 x PEC) |  |  |  | 198741
| Construction and field expenses (0.2 x PEC) |  |  |  | 198741
| Contractor fees (0.1 x PEC) |  |  |  | 99370
| Start-up (0.01 x PEC) |  |  |  | 9937
| Performance test (0.01 x PEC |  |  |  | 9937
| Model study (0.02 x PEC) |  |  |  | 19874
| Contingencies (0.03 x PEC) |  |  |  | 29811
|  | Total Indirect Costs, IC |  |  | 566411
| Total Capital Investment (TCI= (DC + IC) x retrofit) |  |  |  | 4566671.2
| TCI in your year dollars |  |  |  |  | 5626995.1692 | 36.8259 | $/acfm
[7 empty] | 112.5399 | $/kW
Annual Costs For ESP Systems | [6 empty] | 112539.9034 | $/MW
Direct Annual Costs, DC
Operating labor
| Operator (3 hrs/day x labor cost ) |  |  |  | 16064.745
| Supervisor (15 % of operator) |  |  |  | 2410
| Coordinator (1/3 of operator) |  |  |  | 5355
Operating materials
Maintenance
| Labor (based on collector area) |  |  |  | 5082.7734
| Materials (1% of PEC) |  |  |  | 9937
Utilities
| Electricity - fan |  |  |  | 55355 | 24689 | kWh/y-MW
(0.000181 x flue x pres. drp. x hrs x power cost)
| Electricity - operating |  |  |  | 18712
(0.00194 x col. area x hrs x power cost)
| Waste disposal |  | 2 | mile haul | 24893 | 0.16254 | tons/y-MW
(tipping fee + $0.50/ton-mi)
|  | Total DC, | your year dollars |  | 137809.5184
Indirect Annual Costs, IC
| Overhead (60% of labor & maint. materials) |  |  |  | 28722
| Administrative charges (0.02 x TCI) |  |  |  | 112540
| Property tax (0.01 x TCI) |  |  |  | 56270
| Insurance (0.01 x TCI) |  |  |  | 56270
| Capital recovery (CRF x TCI)* |  |  |  | 531149
|  | Total IC , | your year dollars |  | 784951
| Total Annual Cost, |  | your year dollars |  | 922760.5184 |  | 2.013 | $/acfm
[7 empty] | 18.4552 | $/kW
[7 empty] | 18455.2104 | $/MW
0.5 | 0.75 | 0.9 | 0.95 | 0.99 | 0.995 | 0.999
308802 | 378309 | 416839 | 517794 | 673798 | 589425 | 680192

## ESP 25
ELECTROSTATIC PRECIPITATORS
Case | Oil - 25 MW | [5 empty] | 25
You supply data for boxed cells, see OAQPS Control Cost Manual
SIZING PROCEDURE |  |  | Flat Plate Design
| ESP Type |  |  | 2 | (Flat Plate =2, Plate-Wire=1)
| Design Efficiency (E) |  |  | 0.8
| Penetration (p) |  |  | 0.2
| Temperature (Tk) |  |  | 413
| Resistivity (ohm-cm) |  |  | 2000000000
| MMD(i) |  |  | 3.5
| Sneakage (Sn) |  |  | 0.1
| Rapping Reentrainment(RR) |  |  | 0.124
| MMD(p) |  |  | 2
| MMD(r) |  |  | 3
| Loss Factor (LF) |  |  | 0.2116
| E(bd) |  |  | 318193.5206 | (V/m)
| n (eta) |  |  | 2.3077e-05 | (Kg/md)
| e(0) |  |  | 8.845e-12 | (F/m)
| E(avg) |  |  | 252534.5402
| Number of Sections (n) |  |  | 2
| Average Section Penetration (Ps) |  |  | 0.44721
| Collection Penetration (Pc) |  |  | 0.29885
| Particle Size Change Factor (D) |  |  | 0.44721
| MMD(rp) |  |  | 0.52491
| Computed MMD(n) |  | 1 | 3.5
|  |  | 2 | 2.9436
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Computed SCA |  | 1 | 12.7061
|  |  | 2 | 15.1079
|  |  | 3 | 0
|  |  | 4 | 0
|  |  | 5 | 0
|  |  | 6 | 0
|  |  | 7 | 0
| Total SCA |  |  | 27.814
| Total ESCA |  |  | 141.2949
EXHAUST VOLUME (acfm) |  |  | 76400 | acfm | Annual Dust Loading
Total Collection Area (sq. ft.) |  |  | 10794.9296 | sq. ft. | 0.1 | grains/cu. ft.
Annual Hours of Operations |  |  | 7446
COSTING PROCEDURE
Prices include: ESP casing, pyramidal hoppers, rigid electrodes and
internal collecting plates, transformer-rectifier sets and microprocessor controls,
rappers and stub-supports. (Options include inlet/outler nozzles and
diffusion plates, hopper auxiliaries and level detectors, weather enclosure
and stair access, structural supports, and 3 in. of fiberglass insulation
encased in a metal skin. Costs also include auxiliary equipment.)
"Your year" dollars are based on the Chemical Engineering cost index value you
specify below. The base year value (mid 1987) is 320, which should be entered if
you do not have a cost index value. In this case you should not use "your year"
values for direct annual costs and should not enter 1 in the second line of the box
below.
"CRF" is a capital recovery factor calculated as described in Chapter 2 of the
OAQPS Control Cost Manual and based on interest rate and equipment lifetime.
Supply the following data to be used in the costing procedure:
Chemical Engineering cost index value for
| your year (enter base year value of 320 if no other value) |  |  |  |  | 394.3
| If using your year dollar values for direct annual costs, enter 1 |  |  |  |  | 1
| Operating labor hourly cost without overheads ($12/hr base year) |  |  |  |  | 17.26
| Cost of electricity ($0.06/kWh for base year) |  |  |  |  | 0.06
| Tipping fee for waste disposal ($20/ton for base year) |  |  |  |  | 50
| Fractional interest rate for capital (0.07 for base year) |  |  |  |  | 0.07
| Equipment lifetime (20 years for base case) |  |  |  |  | 20
| Additional auxiliary costs, base year (1987) |  |  |  |  | 0
| Retrofit factor (1.2 to 1.5 typical, use 1 for new installation) |  |  |  |  | 1.4
Capital Cost Factors for ESPs
Direct Costs in base year dollars
Purchased Equipment Costs
| ESP + auxiliary equipment |  |  |  | 545063.4
| Auxiliary equipment |  |  |  | 242250.4
| ESP |  |  |  | 302813 |  | 28.0514 | $/ft2 plate area, 1987 $, ESP only
| Instrumentation (0.1 x EC) |  |  |  | 54506 |  | 12.1125 | $/kW, 1987 $, ESP only
| Sales taxes (0.03 x EC) |  |  |  | 16352
| Freight (0.05 x EC) |  |  |  | 27253
|  | Purchased equipment cost, PEC |  |  | 643174.4
Direct installation costs in base year dollars
| Foundations & supports (0.04 x PEC) |  |  |  | 25727
| Handling & erection ().5 x PEC) |  |  |  | 321587
| Electrical (0.08 x PEC) |  |  |  | 51454
| Piping (0.01 x PEC) |  |  |  | 6432
| Insulation for ductwork (0.02 x PEC) |  |  |  | 12863
| Painting (0.02 x PEC) |  |  |  | 12863
|  | Direct installation costs |  |  | 430926
Site preparation
Buildings
|  | Total Direct Costs, DC |  |  | 2460642
Indirect Costs (installation, in base year dollars)
| Engineering (0.2 x PEC) |  |  |  | 128635
| Construction and field expenses (0.2 x PEC) |  |  |  | 128635
| Contractor fees (0.1 x PEC) |  |  |  | 64317
| Start-up (0.01 x PEC) |  |  |  | 6432
| Performance test (0.01 x PEC |  |  |  | 6432
| Model study (0.02 x PEC) |  |  |  | 12863
| Contingencies (0.03 x PEC) |  |  |  | 19295
|  | Total Indirect Costs, IC |  |  | 366609
| Total Capital Investment (TCI= (DC + IC) x retrofit) |  |  |  | 3958151.4
| TCI in your year dollars |  |  |  |  | 4877184.6782 | 63.8375 | $/acfm
[7 empty] | 195.0874 | $/kW
Annual Costs For ESP Systems | [6 empty] | 195087.3871 | $/MW
Direct Annual Costs, DC
Operating labor
| Operator (3 hrs/day x labor cost ) |  |  |  | 16064.745
| Supervisor (15 % of operator) |  |  |  | 2410
| Coordinator (1/3 of operator) |  |  |  | 5355
Operating materials
Maintenance
| Labor (based on collector area) |  |  |  | 5082.7734
| Materials (1% of PEC) |  |  |  | 6432
Utilities
| Electricity - fan |  |  |  | 27677 | 24688.6667 | kWh/y-MW
(0.000181 x flue x pres. drp. x hrs x power cost)
| Electricity - operating |  |  |  | 9356
(0.00194 x col. area x hrs x power cost)
| Waste disposal |  | 2 | mile haul | 12446 | 0.16254 | tons/y-MW
(tipping fee + $0.50/ton-mi)
|  | Total DC, | your year dollars |  | 84823.5184
Indirect Annual Costs, IC
| Overhead (60% of labor & maint. materials) |  |  |  | 26131
| Administrative charges (0.02 x TCI) |  |  |  | 97544
| Property tax (0.01 x TCI) |  |  |  | 48772
| Insurance (0.01 x TCI) |  |  |  | 48772
| Capital recovery (CRF x TCI)* |  |  |  | 460372
|  | Total IC , | your year dollars |  | 681591
| Total Annual Cost, |  | your year dollars |  | 766414.5184 |  | 1.6719 | $/acfm
[7 empty] | 30.6566 | $/kW
[7 empty] | 30656.5807 | $/MW
0.5 | 0.75 | 0.9 | 0.95 | 0.99 | 0.995 | 0.999
308802 | 378309 | 416839 | 517794 | 673798 | 589425 | 680192